## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2026-10-22
This version is 1 day old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2026-08-14
This version is 69 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 8.7365 | 13.3735 | 22.5897 | 3.9418 | 2.8885 | 13.3735 | 0 | 0 | #REF!
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 7.9995 | 17.3935 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | #REF!
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0.895 | 3.1134 | 3.1134 | 3.1134 | 0.895 | 3.2626 | 1.1073 | #REF!
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 0 | 7.5018 | 28.7346 | 19.2944 | 14.1387 | 7.5018 | 0 | 0 | #REF!
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 2.9456 | 7.0826 | 32.0759 | 6.4875 | 4.7335 | 7.0826 | 4.8939 | 0.33304 | #REF!
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 2.3615 | 7.1115 | 20.8769 | 20.8769 | 15.6143 | 7.1115 | 15.7536 | 7.6053 | #REF!
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 4.3107 | 10.6979 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | #REF!
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 6.9544 | 9.9544 | 20.7499 | 9.3284 | 6.8063 | 9.9544 | 0 | 0 | #REF!
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0 | 3.0396 | 11.2179 | 1.9575 | 1.4344 | 3.0396 | 1.4344 | 0 | #REF!
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 0 | 7.5018 | 18.3256 | 18.3256 | 14.1387 | 7.5018 | 0 | 0 | #REF!
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 0 | 22.6759 | 8.9959 | 6.5636 | 0 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.3735 | 1.3735 | 5.1702 | 1.9575 | 1.4344 | 1.3735 | 1.4344 | 0 | #REF!
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 6.1763 | 9.7702 | 28.9714 | 8.6696 | 6.3256 | 9.7702 | 6.5315 | 13.4847 | #REF!
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 5.3687 | 9.5057 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9845 | 11.7345 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 0 | 0 | 31.2952 | 10.2073 | 7.4475 | 0 | 1.3561 | 10.6051 | #REF!
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 3.9666 | 10.9466 | 8.6709 | 6.4889 | 4.6637 | 8.6709 | 6.4697 | 8.428 | #REF!
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.9707 | 1.6707 | 3.2047 | 3.2047 | 3.2047 | 1.6707 | 3.9789 | 1.6295 | #REF!
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 4.3343 | 6.3343 | 7 | 1.9575 | 1.4344 | 6.3343 | 0 | 0 | #REF!
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 8.005 | 15.7965 | 31.1828 | 5.134 | 3.6899 | 15.7965 | 3.7461 | 0 | #REF!
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 4.1504 | 7.6504 | 22.4723 | 12.8463 | 9.373 | 7.6504 | 9.6723 | 7.1892 | #REF!
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 5.142 | 9.7702 | 29.737 | 10.0051 | 7.1909 | 9.7702 | 7.6584 | 8.6278 | #REF!
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 6.4239 | 10.5609 | 11.2179 | 1.9575 | 1.4344 | 10.5609 | 1.4344 | 10.2623 | #REF!
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 6.7684 | 11.2179 | 1.9575 | 1.4344 | 6.7684 | 1.4344 | 9.8525 | #REF!
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.6459 | 18.1459 | 20.2251 | 9.7311 | 7.1308 | 18.1459 | 8.0292 | 18.3194 | #REF!
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 0 | 4.3598 | 11.2179 | 1.9575 | 1.4344 | 4.3598 | 1.4344 | 10.2441 | #REF!
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 4.3877 | 8.8877 | 28.7162 | 10.1228 | 7.2755 | 8.8877 | 7.2768 | 0 | #REF!
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 8.0653 | 10.2659 | 23.8473 | 13.6535 | 9.9619 | 10.2659 | 9.5768 | 4.6017 | #REF!
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.7206 | 9.7206 | 11.048 | 1.9575 | 1.4344 | 9.7206 | 1.4344 | 9.8921 | #REF!
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0 | 5.4997 | 6.9596 | 6.9596 | 6.9596 | 5.4997 | 0 | 0 | #REF!
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 5.7916 | 10.4286 | 11.2179 | 1.9575 | 1.4344 | 10.4286 | 1.4344 | 10.1499 | #REF!
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 2.2397 | 6.3767 | 11.2179 | 1.9575 | 1.4344 | 6.3767 | 1.4344 | 6.4123 | #REF!
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 6.9123 | 11.5493 | 30.7308 | 9.6014 | 7.0054 | 11.5493 | 6.1854 | 10.7604 | #REF!
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 10.133 | 14.77 | 29.8365 | 13.1304 | 9.5803 | 14.77 | 9.7958 | 15.68 | #REF!
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 12.7091 | 20.4591 | 34.9848 | 8.7441 | 6.3799 | 20.4591 | 6.7082 | 17.439 | #REF!
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 1.3537 | 1.3537 | 11.2179 | 1.9575 | 1.4344 | 1.3537 | 1.4344 | 0 | #REF!
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.2042 | 8.3266 | 8.3266 | 8.3266 | 4.2042 | 8.4802 | 3.8465 | #REF!
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | #REF!
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.1464 | 10.1464 | 19.9085 | 19.9085 | 19.2175 | 10.1464 | 19.2177 | 9.8578 | #REF!
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 2.8551 | 7.4921 | 28.3593 | 6.4337 | 4.6241 | 7.4921 | 3.7567 | 5.6289 | #REF!
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 12.8871 | 33.3871 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | #REF!
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 0 | 2.9697 | 31.0828 | 12.151 | 8.7332 | 2.9697 | 8.9022 | 10.8219 | #REF!
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 0 | 4.3656 | 11.2179 | 1.9575 | 1.4344 | 4.3656 | 1.4344 | 0 | #REF!
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 10.4355 | 21.0755 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 5.6182 | 9.1182 | 23.1379 | 12.5677 | 9.0327 | 9.1182 | 9.1136 | 8.37 | #REF!
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 0 | 5.2476 | 30.7835 | 13.2682 | 9.6808 | 5.2476 | 9.8568 | 6.6125 | #REF!
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 7.2225 | 11.8595 | 29.9689 | 12.7761 | 9.3218 | 11.8595 | 9.4256 | 12.706 | #REF!
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 10.5228 | 15.4228 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | #REF!
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | #REF!
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 13.3719 | 17.8719 | 28.5363 | 13.7162 | 9.8581 | 17.8719 | 9.8081 | 10.2615 | #REF!
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 11.3425 | 16.5202 | 21.3275 | 4.8448 | 3.5349 | 16.5202 | 3.8058 | 9.6649 | #REF!
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 11.3308 | 15.4678 | 29.1718 | 11.0453 | 8.059 | 15.4678 | 6.7909 | 5.3989 | #REF!
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 3.1242 | 11.4212 | 17.663 | 17.663 | 16.8626 | 11.4212 | 17.1739 | 8.8706 | #REF!
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 0 | 0 | 9.4697 | 1.5591 | 1.1206 | 0 | 0.7451 | 5.0572 | #REF!
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 0 | 0 | 15.4871 | 8.8339 | 6.3491 | 0 | 4.4683 | 2.8737 | #REF!
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 8.7468 | 12.8838 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.2958 | #REF!
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 10.4706 | 27 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.8954 | #REF!
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 9.2979 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | #REF!
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 5.1538 | 28.1639 | 0.34776 | 0.056402 | 0.041153 | 0.34776 | 0.16545 | 1.3982 | #REF!
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 15.3591 | 17.6961 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 2.666 | 5.166 | 7.534 | 1.8098 | 1.3262 | 5.166 | 8.424 | 5.5206 | #REF!
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 14.3669 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 6.3457 | 10.9827 | 20.6926 | 3.356 | 2.4487 | 10.9827 | 2.09 | 9.5109 | #REF!
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.3899 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 9.5316 | 14.7216 | 31.2088 | 16.4445 | 11.9984 | 14.7216 | 12.1148 | 12.9781 | #REF!
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 3.662 | 13.019 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | #REF!
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 3.243 | 3.243 | 25.1766 | 4.0833 | 2.9793 | 3.243 | 1.3649 | 0 | #REF!
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 1.8222 | 7.1422 | 11.2179 | 1.9575 | 1.4344 | 7.1422 | 1.4344 | 8.4761 | #REF!
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 1.0981 | 11.9981 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 7.121 | 14.521 | 30.2519 | 9.7311 | 7.1308 | 14.521 | 7.3076 | 14.6753 | #REF!
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 0 | 2.7549 | 21.3975 | 10.7823 | 7.8671 | 2.7549 | 8.0328 | 8.3048 | #REF!
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 4.2119 | 8.8489 | 31.0275 | 12.913 | 9.2808 | 8.8489 | 9.2691 | 12.9036 | #REF!
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.1036 | 2.1036 | 22.1641 | 15.1705 | 11.0688 | 2.1036 | 11.1639 | 2.7039 | #REF!
CHELFORD | 11 | Moss Nook | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.6 | 7.9995 | 17.3935 | 11.2179 | 1.9575 | 1.4344 | 11.2179
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 0.69607 | 6.2517 | 25.839 | 9.5485 | 6.9668 | 6.2517 | 5.9831 | 2.9543 | #REF!
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 8.0071 | 13.0635 | 18.5639 | 18.5639 | 17.1186 | 13.0635 | 17.154 | 12.6129 | #REF!
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 0 | 0 | 24.2238 | 13.297 | 9.5568 | 0 | 5.1053 | 5.0492 | #REF!
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 5.4598 | 11.4598 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 9.12 | #REF!
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 5.8561 | 12.6561 | 13.9117 | 13.9117 | 13.9117 | 12.6561 | 7.0436 | 11.2916 | #REF!
CIRCLE SQ | 6.6 | Longsight | LONGSIGHT | BREDBURY | 384365 | 397285 | 630 | 7.2 | 0 | 17.034 | 24.2035 | 11.3226 | 8.2613 | 17.034
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 4.375 | 9.012 | 30.8503 | 12.6536 | 9.2324 | 9.012 | 2.9125 | 3.9899 | #REF!
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0 | 0 | 8.1667 | 1.9575 | 1.4344 | 0 | 1.5151 | 3.7068 | #REF!
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.3975 | 19.0775 | 25.3708 | 10.7509 | 7.8441 | 19.0775 | 7.0436 | 19.3058 | #REF!
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 6.1573 | 9.6573 | 11.2179 | 1.9575 | 1.4344 | 9.6573 | 1.4344 | 7.8631 | #REF!
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 9.0006 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 4.7605 | #REF!
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 10.5739 | 19.5967 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 5.0521 | 15.477 | 43.2277 | 8.5659 | 6.2499 | 15.477 | 1.845 | 13.1837 | #REF!
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 0.83759 | 4.6591 | 4.6591 | 4.6591 | 0.83759 | 4.8516 | 1.4303 | #REF!
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 3.5778 | 5.2148 | 22.6752 | 5.0049 | 3.6517 | 5.2148 | 2.296 | 3.1319 | #REF!
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 5.7689 | 10.0689 | 11.2179 | 1.9575 | 1.4344 | 10.0689 | 1.4344 | 8.1583 | #REF!
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.2644 | 9.4044 | 11.2179 | 1.9575 | 1.4344 | 9.4044 | 1.4344 | 9.0804 | #REF!
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 12.0031 | 3.3493 | 7.9863 | 32.1918 | 7.0239 | 5.0482 | 7.9863 | 0.088852 | 0 | #REF!
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 0 | 13.617 | 9.4523 | 6.9266 | 0 | 0 | 0 | #REF!
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 11.2083 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 3.9666 | 11.4466 | 29.413 | 15.5148 | 11.1508 | 11.4466 | 11.6712 | 8.928 | #REF!
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 4.6651 | 14.5112 | 30.1444 | 12.3588 | 9.0173 | 14.5112 | 9.1618 | 11.3246 | #REF!
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.3261 | 14.9631 | 2.3872 | 0.41655 | 0.30525 | 2.3872 | 1.4344 | 11.2179 | #REF!
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 6.1929 | 10.8299 | 2.3872 | 0.41655 | 0.30525 | 2.3872 | 1.4344 | 11.2179 | #REF!
DICKINSON ST T11 & T12 | 6.6 | Bloom St | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 4.6651 | 14.0154 | 36.9183 | 12.5067 | 9.1253 | 14.0154
DICKINSON ST T13 | 6.6 | Stuart Street | STUART ST | STALYBRIDGE | 384109 | 397722 | 800 | 9.1452 | 9.9138 | 23.9138 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 9.5067 | 5.4068 | #REF!
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 8.2941 | 12.9311 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 11.2179 | #REF!
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 8.1058 | 14.7658 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 7.6553 | 12.2953 | 2.3872 | 0.41655 | 0.30525 | 2.3872 | 1.4344 | 9.4097 | #REF!
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 10.4739 | 16.4763 | 22.3734 | 3.7208 | 2.7148 | 16.4763 | 2.6715 | 15.6217 | #REF!
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 3.911 | 10.411 | 11.2179 | 1.9575 | 1.4344 | 10.411 | 1.4344 | 7.2779 | #REF!
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 13.0758 | 14.4758 | 6.9885 | 1.1506 | 0.82696 | 6.9885 | 0.99981 | 8.4492 | #REF!
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 1.8043 | 6.4413 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0 | 2.435 | 2.435 | 2.435 | 0 | 2.8786 | 0 | #REF!
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 0.75343 | 3.2534 | 10.3718 | 1.8098 | 1.3262 | 3.2534 | 12.6319 | 4.995 | #REF!
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 4.5011 | 15.5011 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | #REF!
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 2.1389 | 5.6389 | 22.5897 | 3.9418 | 2.8885 | 5.6389 | 0 | 0 | #REF!
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 3.243 | 3.243 | 28.4034 | 8.3924 | 6.1498 | 3.243 | 1.3649 | 0 | #REF!
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 1.4325 | 6.0695 | 11.048 | 1.9575 | 1.4344 | 6.0695 | 1.4344 | 11.2006 | #REF!
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 10.9049 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 2.9228 | 15.2228 | 18.6096 | 3.9418 | 2.8885 | 15.2228 | 0 | 0 | #REF!
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 3.1942 | 14.1542 | 29.298 | 15.8024 | 11.3575 | 14.1542 | 11.2192 | 5.6473 | #REF!
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 5.4199 | 10.839 | 10.839 | 10.839 | 5.4199 | 11.0501 | 4.4257 | #REF!
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 6.0103 | 12.5103 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 13.0988 | 17.7358 | 29.2281 | 12.1931 | 8.8964 | 17.7358 | 8.6697 | 0 | #REF!
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 2.6867 | 2.6867 | 13.8416 | 12.5615 | 9.2049 | 2.6867 | 9.0987 | 0.2593 | #REF!
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 2.6936 | 13.1936 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | #REF!
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 0 | 8.7256 | 30.601 | 13.6882 | 9.9873 | 8.7256 | 8.9257 | 9.6892 | #REF!
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0.39487 | 2.5949 | 7.5878 | 7.5878 | 7.5878 | 2.5949 | 7.4769 | 2.881 | #REF!
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 8.8403 | 21.324 | 10.3607 | 1.7058 | 1.226 | 10.3607 | 1.4212 | 12.0107 | #REF!
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.359 | 12.996 | 30.683 | 5.4452 | 3.9902 | 12.996 | 5.4751 | 12.055 | #REF!
GOLBORNE T11 & T12 | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 10.1109 | 15.6109 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | #REF!
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 6.8353 | 6.8353 | 24.3991 | 8.8877 | 6.3878 | 6.8353 | 7.0494 | 5.6473 | #REF!
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.9582 | 15.0582 | 25.0372 | 5.8467 | 4.2659 | 15.0582 | 5.885 | 14.3872 | #REF!
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 5.5458 | 11.5458 | 20.9969 | 20.9969 | 19.1965 | 11.5458 | 19.5311 | 10.7263 | #REF!
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 10.6819 | 18.8019 | 17.7841 | 3.4403 | 2.5101 | 17.7841 | 1.1085 | 9.368 | #REF!
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 7.3126 | 11.9496 | 31.6854 | 15.6977 | 11.2823 | 11.9496 | 11.1508 | 10.8283 | #REF!
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 6.8088 | 11.4458 | 31.5238 | 9.048 | 6.503 | 11.4458 | 5.6166 | 0.45951 | #REF!
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 0 | 5.9689 | 19.3178 | 19.3178 | 17.7364 | 5.9689 | 4.1968 | 3.8848 | #REF!
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 0 | 7.72 | 31.2798 | 9.1919 | 6.7066 | 7.72 | 5.7981 | 10.2071 | #REF!
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 13.5087 | 18.0087 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 10.2659 | 10.2659 | 61.8488 | 10.156 | 7.4101 | 10.2659 | 6.8407 | 4.6017 | #REF!
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 8.9927 | 13.6327 | 22.5897 | 3.9418 | 2.8885 | 13.6327 | 0 | 0 | #REF!
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 10.5967 | 17.3237 | 7.6713 | 1.263 | 0.90776 | 7.6713 | 0.83754 | 7.0779 | #REF!
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 1.2411 | 1.2411 | 21.5498 | 10.5769 | 7.7172 | 1.2411 | 0 | 0 | #REF!
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 7.0938 | 11.7308 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | #REF!
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 0 | 0 | 10.8309 | 10.8309 | 10.8309 | 0 | 5.1053 | 5.1053 | #REF!
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 7.8904 | 12.5274 | 29.3567 | 12.312 | 8.9832 | 12.5274 | 9.5452 | 9.9239 | #REF!
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 11.3825 | 16.0225 | 30.0164 | 12.487 | 9.1108 | 16.0225 | 9.1946 | 15.552 | #REF!
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 1.1494 | 5.4494 | 11.2179 | 1.9575 | 1.4344 | 5.4494 | 1.4344 | 7.187 | #REF!
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 0 | 0 | 14.7253 | 4.9178 | 3.5345 | 0 | 3.4214 | 6.4802 | #REF!
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.1866 | 6.6866 | 13.1381 | 13.1381 | 13.1381 | 6.6866 | 13.0026 | 6.7952 | #REF!
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 12.4311 | 16.9311 | 29.6601 | 16.634 | 11.9552 | 16.9311 | 12.0132 | 15.4515 | #REF!
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 1.764 | 10.3691 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | #REF!
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.5926 | 19.8126 | 3.168 | 0.52159 | 0.37488 | 3.168 | 0 | 0 | #REF!
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.5926 | 19.8126 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | #REF!
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 6.0872 | 9.5872 | 23.2195 | 9.7248 | 7.0955 | 9.5872 | 7.0425 | 7.7035 | #REF!
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 1.9021 | 1.9021 | 8.3721 | 1.9575 | 1.4344 | 1.9021 | 1.4344 | 2.695 | #REF!
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 8.6961 | 17.9061 | 29.0742 | 8.87 | 6.4718 | 17.9061 | 0 | 0 | #REF!
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 2.7589 | 2.7589 | 30.021 | 9.5821 | 6.9913 | 2.7589 | 7.1221 | 0 | #REF!
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0.8713 | 2.7589 | 24.0291 | 4.7126 | 3.4384 | 2.7589 | 3.0681 | 0 | #REF!
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.50207 | 8.5021 | 12.4038 | 12.4038 | 12.4038 | 8.5021 | 13.2972 | 8.3367 | #REF!
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 14.0292 | 18.1662 | 10.3718 | 1.8098 | 1.3262 | 10.3718 | 9.101 | 17.1039 | #REF!
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 10.0114 | 14.6484 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 5.3712 | 13.9204 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 1.3671 | 3.87 | 15.9213 | 2.5822 | 1.8841 | 3.87 | 1.2885 | 0 | #REF!
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 6.7989 | 14.2989 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | #REF!
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 6.7928 | 11.4298 | 23.2983 | 5.4152 | 3.892 | 11.4298 | 3.7037 | 4.126 | #REF!
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 7.345 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 1.134 | 6.5049 | 1.9575 | 1.4344 | 1.134 | 1.4344 | 0.95096 | #REF!
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 9.6314 | 15.7965 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | #REF!
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 3.243 | 3.243 | 27.1006 | 7.3421 | 5.357 | 3.243 | 1.3649 | 0 | #REF!
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.7595 | 10.8965 | 11.2179 | 1.9575 | 1.4344 | 10.8965 | 1.4344 | 11.2179 | #REF!
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 5.7002 | 9.2002 | 11.2179 | 1.9575 | 1.4344 | 9.2002 | 1.4344 | 6.5258 | #REF!
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 4.6943 | 8.1943 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 10.2795 | 15.5784 | 26.3039 | 23.0042 | 16.5336 | 15.5784 | 17.2503 | 13.3736 | #REF!
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.4363 | 11.0733 | 31.2051 | 5.4452 | 3.9902 | 11.0733 | 5.4751 | 11.4433 | #REF!
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 4.8839 | 17.1839 | 29.3443 | 13.5659 | 9.8981 | 17.1839 | 7.0436 | 17.6125 | #REF!
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 9.8997 | 18.8949 | 22.5897 | 3.9418 | 2.8885 | 18.8949 | 0 | 0 | #REF!
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 0 | 7.5018 | 12.4695 | 12.4695 | 12.4695 | 7.5018 | 0 | 0 | #REF!
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 4.63 | 8.77 | 11.2179 | 1.9575 | 1.4344 | 8.77 | 1.4344 | 4.4053 | #REF!
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 3.5728 | 7.7098 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 14.0411 | 18.1781 | 29.0556 | 13.3568 | 9.7455 | 18.1781 | 7.0436 | 16.5205 | #REF!
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 0 | 6.4926 | 28.4174 | 9.0664 | 6.5162 | 6.4926 | 0 | 0 | #REF!
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 5.5291 | 8.0291 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | #REF!
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 22.62 | 29.8572 | 47.0319 | 8.093 | 5.8166 | 29.8572 | 1.6009 | 0 | #REF!
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.74632 | 2.2463 | 3.1382 | 3.1382 | 3.1382 | 2.2463 | 3.1954 | 2.3112 | #REF!
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 0 | 7.2449 | 13.3001 | 13.3001 | 13.3001 | 7.2449 | 0 | 0 | #REF!
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.4668 | 5.9668 | 2.5787 | 2.5787 | 2.5787 | 2.5787 | 2.8987 | 2.8987 | #REF!
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 9.264 | 11.764 | 18.838 | 18.838 | 18.838 | 11.764 | 19.5904 | 10.2783 | #REF!
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 4.2347 | 15.4847 | 26.8074 | 24.4297 | 17.5581 | 15.4847 | 18.6543 | 13.2545 | #REF!
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 5.7135 | 8.0635 | 21.2353 | 11.3794 | 8.1786 | 8.0635 | 8.0695 | 0 | #REF!
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 1.2164 | 12.0145 | 30.9806 | 13.1326 | 9.5819 | 12.0145 | 9.0797 | 10.8837 | #REF!
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 2.1317 | 29.3481 | 6.9389 | 5.0628 | 2.1317 | 4.9077 | 0 | #REF!
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 1.2164 | 13.56 | 22.7737 | 9.9501 | 7.2598 | 13.56 | 7.0795 | 15.6051 | #REF!
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | #REF!
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 3.243 | 3.243 | 31.2857 | 8.3924 | 6.1498 | 3.243 | 1.3649 | 0 | #REF!
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 10.3172 | 14.9572 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 3.3864 | 11.3864 | 19.4357 | 19.4357 | 19.4357 | 11.3864 | 19.6186 | 0 | #REF!
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 0 | 5.1726 | 24.6755 | 14.0779 | 10.2716 | 5.1726 | 10.1941 | 6.1719 | #REF!
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 14.174 | 22.3127 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | #REF!
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 6.1777 | 7 | 1.9575 | 1.4344 | 6.1777 | 1.4344 | 4.4466 | #REF!
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 5.7529 | 8.0391 | 15.691 | 15.691 | 15.691 | 8.0391 | 16.5605 | 4.0762 | #REF!
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 3.997 | 7.497 | 24.3866 | 10.0536 | 7.3354 | 7.497 | 6.9929 | 0 | #REF!
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 7.0567 | 11.6937 | 29.2493 | 7.6215 | 5.5608 | 11.6937 | 5.7031 | 10.4658 | #REF!
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 0 | 5.6457 | 27.811 | 5.3596 | 3.9105 | 5.6457 | 2.8907 | 9.1882 | #REF!
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 5.5095 | 11.5095 | 36.618 | 6.0289 | 4.3331 | 11.5095 | 0.088852 | 0 | #REF!
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 8.4199 | 17.449 | 22.5897 | 3.9418 | 2.8885 | 17.449 | 0 | 0 | #REF!
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 2.8394 | 5.0764 | 11.2179 | 1.9575 | 1.4344 | 5.0764 | 1.4344 | 10.6576 | #REF!
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 0.32011 | 32.9592 | 10.2207 | 7.4573 | 0.32011 | 7.4513 | 1.5496 | #REF!
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0 | 0 | 6.0932 | 6.0932 | 6.0932 | 0 | 7.1061 | 0 | #REF!
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 8.127 | 14.133 | 24.787 | 8.7259 | 6.3666 | 14.133 | 6.5522 | 14.5624 | #REF!
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 7.9839 | 18.3879 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | #REF!
MEDIPARK | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 380478 | 387812 | 630 | 12.0028 | 24.7276 | 33.8649 | 38.7798 | 10.3204 | 7.4175 | 33.8649
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 0 | 3.5398 | 6.5282 | 6.5282 | 6.5282 | 3.5398 | 0 | 0 | #REF!
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 1.2411 | 1.2411 | 21.5498 | 13.0627 | 9.5309 | 1.2411 | 0 | 0 | #REF!
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 3.243 | 3.243 | 26.2459 | 4.3212 | 3.1057 | 3.243 | 1.3649 | 0 | #REF!
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 9.5852 | 12.2893 | 10.3718 | 1.8098 | 1.3262 | 10.3718 | 18.0835 | 11.4916 | #REF!
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 12.3835 | 17.0235 | 29.2996 | 10.5844 | 7.7227 | 17.0235 | 7.4802 | 14.0754 | #REF!
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 0 | 7.5018 | 13.2598 | 2.1831 | 1.5691 | 7.5018 | 0 | 0 | #REF!
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 4.0341 | 13.5341 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | #REF!
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 4.5488 | 8.0488 | 11.2179 | 1.9575 | 1.4344 | 8.0488 | 1.4344 | 5.0297 | #REF!
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 3.6963 | 7.1963 | 11.2179 | 1.9575 | 1.4344 | 7.1963 | 1.4344 | 8.9507 | #REF!
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 6.7947 | 11.5919 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | #REF!
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 4.2263 | 7.2452 | 22.3017 | 8.743 | 6.3792 | 7.2452 | 5.8695 | 0 | #REF!
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 6.1119 | 7 | 1.9575 | 1.4344 | 6.1119 | 1.4344 | 3.7702 | #REF!
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 9.6156 | 22.1773 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | #REF!
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.9905 | 7.3045 | 27.2809 | 12.8162 | 9.2113 | 7.3045 | 9.1199 | 4.5253 | #REF!
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 2.0451 | 33.5948 | 10.3389 | 7.5435 | 2.0451 | 7.5673 | 1.6732 | #REF!
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 10.2039 | 14.8409 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 0.98298 | 5.6199 | 11.2179 | 1.9575 | 1.4344 | 5.6199 | 1.4344 | 8.7054 | #REF!
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.3515 | 13.9715 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 4.9303 | 9.0703 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 3.243 | 3.243 | 29.7533 | 8.3924 | 6.1498 | 3.243 | 1.3649 | 0 | #REF!
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0 | 1.4763 | 3.2149 | 3.2149 | 3.2149 | 1.4763 | 3.8322 | 2.0546 | #REF!
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0.42271 | 7.4227 | 14.6189 | 14.6189 | 14.6189 | 7.4227 | 15.0523 | 7.0631 | #REF!
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.3694 | 14.3694 | 18.4853 | 5.4452 | 3.9902 | 14.3694 | 1.511 | 1.511 | #REF!
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 1.0946 | 1.0946 | 12.0002 | 8.3924 | 6.1498 | 1.0946 | 1.3649 | 0 | #REF!
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 5.6196 | 9.7566 | 26.6116 | 9.4523 | 6.9266 | 9.7566 | 0 | 0 | #REF!
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 1.2943 | 5.2943 | 26.8074 | 6.4363 | 4.6259 | 5.2943 | 3.841 | 8.6565 | #REF!
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 1.1214 | 5.8714 | 19.7335 | 19.7335 | 19.3352 | 5.8714 | 14.4183 | 10.2752 | #REF!
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.2283 | 23.5559 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 9.6773 | 14.6235 | 6.4828 | 1.0673 | 0.76712 | 6.4828 | 0.56343 | 4.7615 | #REF!
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 7.6283 | 11.1283 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 9.31 | #REF!
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 2.5901 | 7.5301 | 11.2179 | 1.9575 | 1.4344 | 7.5301 | 1.4344 | 10.0382 | #REF!
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 2.7589 | 2.7589 | 28.9822 | 12.4548 | 9.0874 | 2.7589 | 9.1327 | 0 | #REF!
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 1.3949 | 5.7146 | 2.3872 | 0.41655 | 0.30525 | 2.3872 | 1.4344 | 5.886 | #REF!
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 10.4513 | #REF!
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 15.9341 | 22.9341 | 6.6984 | 1.1028 | 0.79263 | 6.6984 | 0.84345 | 7.1279 | #REF!
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 1.879 | 11.679 | 19.6263 | 19.6263 | 19.6263 | 11.679 | 19.6031 | 8.983 | #REF!
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 7.8385 | 11.9755 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 2.2304 | 11.2304 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 4.6651 | 10.0228 | 30.2834 | 8.2684 | 6.0328 | 10.0228 | 6.0414 | 15.0117 | #REF!
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 10.4513 | #REF!
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 6.2477 | 11.0449 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.4344 | 7 | #REF!
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 2.7589 | 2.7589 | 28.596 | 9.154 | 6.679 | 2.7589 | 6.7371 | 0 | #REF!
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 7.0012 | 8.9812 | 11.2179 | 1.9575 | 1.4344 | 8.9812 | 1.4344 | 6.9765 | #REF!
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 6.8566 | 10.3566 | 22.8897 | 13.0124 | 9.3523 | 10.3566 | 9.4181 | 10.8112 | #REF!
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 11.9288 | 16.4288 | 29.788 | 12.5615 | 9.2049 | 16.4288 | 9.0987 | 15.8281 | #REF!
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 0 | 0 | 2.6918 | 0.43658 | 0.31854 | 0 | 1.4344 | 0 | #REF!
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 10.6034 | 15.2404 | 30.2892 | 11.506 | 8.3951 | 15.2404 | 8.77 | 17.138 | #REF!
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 5.667 | 10.304 | 31.4025 | 7.988 | 5.8283 | 10.304 | 5.8553 | 6.3816 | #REF!
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 5.3191 | 12.8791 | 29.4223 | 12.7923 | 9.3336 | 12.8791 | 8.8549 | 17.2513 | #REF!
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.9582 | 15.0582 | 25.0372 | 10.5854 | 7.7234 | 15.0582 | 9.5083 | 14.3872 | #REF!
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 1.0239 | 4.6759 | 11.2179 | 1.9575 | 1.4344 | 4.6759 | 1.4344 | 0 | #REF!
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 3.1607 | 15.8607 | 34.5907 | 12.6684 | 9.2432 | 15.8607 | 8.8192 | 17.3639 | #REF!
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.8013 | 15.4383 | 30.5998 | 15.6377 | 11.4097 | 15.4383 | 11.7382 | 14.2835 | #REF!
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 2.7589 | 2.7589 | 29.8741 | 9.8191 | 7.1643 | 2.7589 | 7.0914 | 0 | #REF!
RIBBLESDALE T13 & T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 2.279 | 5.029 | 22.7667 | 16.2946 | 11.7113 | 5.029 | 11.8923 | 1.683 | #REF!
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 12.0652 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 4.6708 | 8.868 | 1.4601 | 1.0494 | 4.6708 | 1.2626 | 4.1747 | #REF!
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 22.3348 | 35.3348 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | #REF!
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 5.4339 | 12.9092 | 22.5897 | 3.9418 | 2.8885 | 12.9092 | 0 | 0 | #REF!
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 1.0842 | 2.7589 | 22.5098 | 10.7476 | 7.7245 | 2.7589 | 7.5834 | 0 | #REF!
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 1.2521 | 4.7521 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 5.3712 | 14.6613 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 6.1763 | 9.7702 | 30.1984 | 8.5 | 6.2018 | 9.7702 | 6.5677 | 14.7385 | #REF!
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 2.1265 | 2.1265 | 11.7228 | 11.7228 | 11.7228 | 2.1265 | 12.01 | 1.3941 | #REF!
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 20.2086 | 27.0007 | 27.5016 | 18.0756 | 12.9913 | 27.0007
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 10.9888 | 15.4888 | 29.7534 | 9.7311 | 7.1308 | 15.4888 | 7.2924 | 14.3266 | #REF!
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 0 | 0 | 6.2775 | 1.9575 | 1.4344 | 0 | 1.4344 | 3.6656 | #REF!
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0.89005 | 1.89 | 1.9632 | 1.9575 | 1.4344 | 1.89 | 1.4344 | 1.1732 | #REF!
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 0 | 7.5018 | 18.5214 | 18.5214 | 14.1387 | 7.5018 | 0 | 0 | #REF!
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 0.69685 | 0.69685 | 4.6434 | 4.6434 | 4.6434 | 0.69685 | 4.9054 | 1.1883 | #REF!
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.17672 | 7.6767 | 13.8784 | 13.8784 | 13.8784 | 7.6767 | 13.3716 | 7.6618 | #REF!
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 1.6645 | 8.0145 | 31.424 | 26.373 | 18.9548 | 8.0145 | 18.9995 | 5.2353 | #REF!
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 3.8711 | 10.2793 | 31.7373 | 10.7618 | 7.8521 | 10.2793 | 8.0106 | 5.397 | #REF!
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 2.7268 | 5.5268 | 12.5332 | 12.5332 | 12.5332 | 5.5268 | 12.2325 | 7.0318 | #REF!
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 5.3712 | 15.8789 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 12.5613 | 19.0613 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | #REF!
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 19.1502 | 41.3893 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.3976 | 7.809 | #REF!
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 10.2795 | 15.5784 | 26.8074 | 24.1381 | 17.3485 | 15.5784 | 17.7881 | 13.3736 | #REF!
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 4.4657 | 6.4657 | 10.3718 | 1.8098 | 1.3262 | 6.4657 | 12.7115 | 7.3459 | #REF!
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 8.4931 | 13.1586 | 2.3872 | 0.41655 | 0.30525 | 2.3872 | 1.4344 | 11.2179 | #REF!
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 1.3537 | 1.3537 | 11.2179 | 1.9575 | 1.4344 | 1.3537 | 1.4344 | 0 | #REF!
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.9314 | 20.396 | 21.6604 | 11.269 | 8.0992 | 20.396 | 0 | 0 | #REF!
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 1.3537 | 1.3537 | 11.2179 | 1.9575 | 1.4344 | 1.3537 | 1.4344 | 0 | #REF!
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 8.5516 | 8.5516 | 11.2179 | 1.9575 | 1.4344 | 8.5516 | 1.4344 | 5.2215 | #REF!
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 5.77 | 7.52 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | #REF!
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 8.1507 | 11.6507 | 22.546 | 12.657 | 9.2349 | 11.6507 | 4.1691 | 9.6296 | #REF!
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 4.9065 | 18.6865 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | #REF!
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | #REF!
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 5.5194 | 10.1194 | 18.3714 | 2.9796 | 2.174 | 10.1194 | 2.1114 | 6.2955 | #REF!
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 10.853 | 14.353 | 21.6604 | 9.5898 | 6.997 | 14.353 | 0 | 0 | #REF!
ST JOHNS | 6.6 | Frederick Road | FREDERICK RD | KEARSLEY | 383100 | 398078 | 600 | 6.8589 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 8.1268 | 10.2659 | 29.5137 | 10.8866 | 7.9432 | 10.2659 | 7.7148 | 4.6017 | #REF!
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 6.9189 | 10.4189 | 11.2179 | 1.9575 | 1.4344 | 10.4189 | 1.4344 | 10.0664 | #REF!
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 14.4111 | 19.0481 | 21.6604 | 12.7962 | 9.3364 | 19.0481 | 0 | 0 | #REF!
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 9.0999 | 11.5999 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | #REF!
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 0 | 0 | 18.5035 | 7.0267 | 5.0502 | 0 | 1.9914 | 1.9914 | #REF!
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 11.7843 | 15.9213 | 20.1283 | 3.355 | 2.4479 | 15.9213 | 2.4384 | 6.5078 | #REF!
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 2.5383 | 9.5383 | 11.2179 | 1.9575 | 1.4344 | 9.5383 | 1.4344 | 0 | #REF!
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 7.7257 | 24.7257 | 26.0311 | 4.2858 | 3.0803 | 24.7257 | 2.782 | 23.5098 | #REF!
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 13.5651 | 18.7298 | 30.0295 | 14.9599 | 10.752 | 18.7298 | 10.853 | 18.1986 | #REF!
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 8.5077 | 13.1447 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 10.3338 | 14.4708 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | #REF!
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 0 | 0 | 16.3222 | 4.9849 | 3.5827 | 0 | 0.31765 | 2.6844 | #REF!
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 4.587 | 15.287 | 29.6379 | 10.0925 | 7.3637 | 15.287 | 7.3789 | 14.5981 | #REF!
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 9.6156 | 34.8156 | 11.2179 | 1.9575 | 1.4344 | 11.2179
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 9.2154 | 12.3524 | 10.1713 | 1.6746 | 1.2036 | 10.1713 | 0.31765 | 2.6844 | #REF!
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 3.243 | 3.243 | 32.1284 | 8.3924 | 6.1498 | 3.243 | 1.3649 | 0 | #REF!
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 0 | 6.9376 | 22.6463 | 8.0198 | 5.8515 | 6.9376 | 5.7122 | 14.3365 | #REF!
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 3.7038 | 8.9538 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | #REF!
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 9.3598 | 13.4968 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.4618 | #REF!
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 4.9299 | 7.9299 | 15.2785 | 9.8549 | 7.0829 | 7.9299 | 7.6223 | 7.75 | #REF!
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 7.5901 | 12.2271 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.7198 | #REF!
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 1.2164 | 8.3747 | 23.2036 | 11.4185 | 8.2067 | 8.3747 | 8.1328 | 6.6945 | #REF!
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 9.1264 | 13.7634 | 29.3832 | 7.5785 | 5.5295 | 13.7634 | 5.7691 | 14.4783 | #REF!
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 0 | 27.5312 | 8.0249 | 5.8552 | 0 | 4.6312 | 4.9475 | #REF!
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 8.1091 | 11.6091 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.9371 | #REF!
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 8.8246 | 13.7173 | 30.2557 | 7.9584 | 5.8066 | 13.7173 | 5.5739 | 0 | #REF!
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 1.2411 | 1.2411 | 21.5498 | 12.8932 | 9.4072 | 1.2411 | 0 | 0 | #REF!
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 10.2659 | 10.2659 | 29.3523 | 13.3337 | 9.7286 | 10.2659 | 9.344 | 4.6017 | #REF!
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 0 | 0 | 29.5191 | 12.4599 | 8.9552 | 0 | 1.3561 | 10.6051 | #REF!
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | #REF!
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 10.2659 | 10.2659 | 29.7248 | 12.9846 | 9.4739 | 10.2659 | 8.8768 | 4.6017 | #REF!
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 9.9541 | 14.5911 | 30.401 | 13.1314 | 9.581 | 14.5911 | 10.1945 | 7.7239 | #REF!
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7274 | 10.7274 | 11.048 | 1.9575 | 1.4344 | 10.7274 | 1.4344 | 8.6933 | #REF!
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 5.0572 | #REF!
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 1.1922 | 5.8292 | 10.8238 | 1.7821 | 1.2808 | 5.8292 | 0.088852 | 0 | #REF!
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 4.3499 | 6.8499 | 7 | 1.9575 | 1.4344 | 6.8499 | 1.4344 | 7 | #REF!
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 9.67 | 14.307 | 26.4684 | 7.9304 | 5.6997 | 14.307 | 5.5392 | 11.0853 | #REF!
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 4.0762 | 13.2132 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 10.576 | #REF!
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 0 | 6.8336 | 21.9765 | 18.3746 | 13.2062 | 6.8336 | 0 | 0 | #REF!
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.4304 | 8.9304 | 23.4528 | 14.5556 | 10.4614 | 8.9304 | 10.3146 | 9.0214 | #REF!
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 5.2154 | 6.7154 | 9.9558 | 4.0346 | 2.9438 | 6.7154 | 3.1391 | 5.9064 | #REF!
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0.93347 | 5.0705 | 6.6671 | 1.9575 | 1.4344 | 5.0705 | 1.4344 | 0.21045 | #REF!
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 9.682 | #REF!
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 2.8646 | 7.5011 | 25.3708 | 13.2683 | 9.6809 | 7.5011 | 9.2635 | 4.6017 | #REF!
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 4.4474 | 8.5844 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | #REF!
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 4.5599 | 8.0599 | 11.2179 | 1.9575 | 1.4344 | 8.0599 | 1.4344 | 5.768 | #REF!
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 0 | 7.5018 | 30.7106 | 19.2944 | 14.1387 | 7.5018 | 0 | 0 | #REF!
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 3.9632 | 7.4632 | 17.4779 | 6.9471 | 5.0688 | 7.4632 | 2.1791 | 7.5047 | #REF!
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.2457 | 5.7457 | 11.048 | 1.9575 | 1.4344 | 5.7457 | 1.4344 | 6.0832 | #REF!
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 1.3537 | 1.3537 | 11.2179 | 1.9575 | 1.4344 | 1.3537 | 0.31765 | 0 | #REF!
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.2743 | 8.7743 | 23.9427 | 14.0637 | 10.2613 | 8.7743 | 10.5673 | 8.8316 | #REF!
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 0 | 0 | 30.9563 | 13.948 | 10.0247 | 0 | 5.1053 | 5.1053 | #REF!
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.5151 | 2.7595 | #REF!
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 0.2042 | 3.7042 | 11.2179 | 1.9575 | 1.4344 | 3.7042 | 1.4344 | 0.86929 | #REF!
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 2.7589 | 2.7589 | 10.691 | 1.7602 | 1.2651 | 2.7589 | 1.0921 | 0 | #REF!
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 11.4735 | 15.4735 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 9.6965 | 14.3335 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | #REF!
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 0 | 12.8814 | 25.5181 | 12.2519 | 8.9393 | 12.8814 | 7.7377 | 8.7753 | #REF!
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 0 | 0 | 29.7842 | 15.3468 | 11.0301 | 0 | 5.1053 | 5.1053 | #REF!
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0 | 5.2766 | 12.7306 | 12.7306 | 12.7306 | 5.2766 | 0 | 0 | #REF!

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 20.9766 | 38.9766 | 141.226 | 47.0978 | 38.9766 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | #REF!
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 13.5651 | 25.5651 | 91.4745 | 27.6624 | 25.5651 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | #REF!
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 28.8271 | 46.8271 | 146.334 | 48.9712 | 46.8271 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | #REF!
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 15.7965 | 15.7965 | 124.0447 | 28.035 | 15.7965 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | #REF!
BARROW & SANDGATE | 33 | HARKER | 319709 | 470489 | 39.7309 | 66.3507 | 53.0463 | 9.6235 | 53.0463 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | #REF!
BARTON | 33 | CARRINGTON | 376758 | 397174 | 25.3322 | 44.1754 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | #REF!
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 29.8572 | 29.8572 | 56.2947 | 23.9633 | 29.8572 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | #REF!
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 32.3782 | 32.3782 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | #REF!
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 32.1545 | 32.1545 | 75.5717 | 44.8659 | 32.1545 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | #REF!
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 38.2123 | 39.0523 | 125.598 | 34.973 | 39.0523 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | #REF!
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 4.6651 | 46.4651 | 149.3756 | 48.6765 | 46.4651 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | #REF!
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 15.7874 | 43.7874 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | #REF!
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 66.4662 | 69.2862 | 53.7128 | 22.7571 | 53.7128 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | #REF!
BURY | 33 | KEARSLEY | 380272 | 411184 | 27.4893 | 27.4893 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | #REF!
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 0 | 0 | 89.0157 | 45.4916 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | #REF!
CARLISLE | 33 | HARKER | 338655 | 556583 | 24.0256 | 45.2256 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | #REF!
CARLISLE NORTH | 11 | HARKER | 338547 | 560280 | 1.344 | 18.7624 | 5.0385 | 1.4491 | 5.0385
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 11.0613 | 32.0613 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | #REF!
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 26.3331 | 26.3331 | 88.4573 | 37.1173 | 26.3331 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | #REF!
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 3.243 | 3.243 | 45.7488 | 8.2996 | 3.243 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | #REF!
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 35.9586 | 35.9586 | 2.2707 | 0.41195 | 2.2707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | #REF!
EGREMONT | 33 | HARKER | 301070 | 513074 | 50.3313 | 50.3313 | 9.8659 | 1.7898 | 9.8659 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | #REF!
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 0 | 6.7308 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | #REF!
GOLBORNE | 33 | BOLD | 360607 | 397690 | 24.6032 | 42.6032 | 51.5268 | 9.3478 | 42.6032 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | #REF!
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 10.2659 | 10.2659 | 109.8684 | 38.7942 | 10.2659 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | #REF!
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 46.3565 | 64.3565 | 131.6766 | 36.9341 | 64.3565 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | #REF!
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 28.9619 | 90.9619 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | #REF!
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 35.1425 | 48.9425 | 68.4546 | 21.7717 | 48.9425 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | #REF!
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 26.6904 | 26.6904 | 29.6829 | 5.385 | 26.6904 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | #REF!
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 37.4717 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | #REF!
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 0 | 7.5018 | 60.2511 | 19.081 | 7.5018 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | #REF!
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 0 | 0 | 10.6707 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | #REF!
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 22.4247 | 37.3887 | 128.4578 | 33.7646 | 37.3887 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | #REF!
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 0 | 17.034 | 148.9806 | 39.05 | 17.034 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | #REF!
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 9.8997 | 59.8997 | 21.4878 | 3.8982 | 21.4878 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | #REF!
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 21.1809 | 21.1809 | 21.6604 | 21.6604 | 21.1809 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | #REF!
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 1.3537 | 1.3537 | 10.6707 | 1.9358 | 1.3537 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | #REF!
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 9.6156 | 34.8156 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | #REF!
NELSON | 33 | PADIHAM | 385989 | 438643 | 10.5739 | 31.9867 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | #REF!
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 20.3074 | 20.3074 | 47.4136 | 47.4136 | 20.3074 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | #REF!
ORRELL | 33 | KIRKBY | 352784 | 404565 | 1.2164 | 58.2164 | 135.7877 | 53.3438 | 58.2164 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | #REF!
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 22.6282 | 54.1282 | 140.353 | 30.7686 | 54.1282 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | #REF!
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 1.2411 | 1.2411 | 21.5498 | 21.5498 | 1.2411 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | #REF!
PENRITH & SHAP | 33 | HUTTON | 349996 | 530398 | 15.5784 | 15.5784 | 26.8074 | 26.8074 | 15.5784 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | #REF!
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 0 | 0 | 10.6707 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | #REF!
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 28.7179 | 46.7179 | 152.5583 | 32.6208 | 46.7179
RADCLIFFE | 11 | KEARSLEY | 377524 | 406160 | 0 | 0 | 44.3575 | 38.6588 | 0
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 76.0185 | 112.0185 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | #REF!
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 46.4434 | 58.4434 | 83.1391 | 22.2137 | 58.4434 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | #REF!
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 35.8304 | 48.6992 | 84.4355 | 45.6248 | 48.6992 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | #REF!
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 5.3712 | 71.784 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | #REF!
SALE | 33 | CARRINGTON | 378726 | 392892 | 6.1763 | 9.7702 | 78.0965 | 49.019 | 9.7702 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | #REF!
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 0 | 0 | 10.6707 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | #REF!
STAINBURN & SIDDICK | 33 | HARKER | 302535 | 529330 | 20.272 | 68.82 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | #REF!
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 11.0575 | 43.3085 | 134.3787 | 34.9951 | 43.3085 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | #REF!
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 59.0866 | 122.0866 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | #REF!
THORNTON | 33 | STANAH | 334559 | 443368 | 20.7713 | 32.7713 | 36.2039 | 12.4226 | 32.7713 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | #REF!
TRIMPELL | 11 | HEYSHAM | 341861 | 458979 | 9.4981 | 9.4981 | 5.0385 | 1.4491 | 5.0385
ULVERSTON | 33 | HARKER | 327495 | 477808 | 64.0376 | 64.0376 | 65.5616 | 27.8889 | 64.0376 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | #REF!
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 2.7589 | 2.7589 | 84.8416 | 15.7465 | 2.7589 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | #REF!
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 10.9664 | 47.4664 | 10.6231 | 1.9358 | 10.6231 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | #REF!
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 27.6464 | 27.6464 | 89.5308 | 24.4447 | 27.6464 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | #REF!
WIGAN | 33 | KIRKBY | 358343 | 404626 | 0 | 61.4555 | 138.5399 | 70.0881 | 61.4555 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | #REF!
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 0 | 0 | 67.654 | 18.8186 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | #REF!

## 6) GSP Demand Headroom Data (hidden)
GSP Headroom
Substation | GSP | Voltage (kV) | GSP Group | GSP Coordinates |  | Demand Headroom (MVA) |  | Battery Storage Headroom N-0 -(MW)
|  |  |  | Easting | Northing | Firm (non inverter based) | Non Firm (inverter based)
Bold GSP (132) | BOLD | 132 | BOLD | 353959 | 393258 | -139.0585 | -139.0585 | -99.1396 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en
Bredbury (132) | BREDBURY | 132 | BREDBURY | 391365 | 390944 | 130.6602 | 146.7402 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en
Carrington GSP (132) | CARRINGTON | 132 | CARRINGTON | 372952 | 393301 | -48.4123 | 104.5877 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en
Harker / Hutton GSP (132) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | 132 | HARKER / HUTTON | 338285 | 561159 | -654.416 | -654.416 | -1393.5411 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en
Heysham GSP (132) | HEYSHAM | 132 | HEYSHAM | 341889 | 460007 | 328.4761 | 328.4761 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en
Kearsley GSP (132) | KEARSLEY | 132 | KEARSLEY | 376283 | 404800 | -9.6464 | 127.5736 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en
Padiham (132) | PADIHAM | 132 | PADIHAM | 378522 | 433196 | -252.3064 | -252.3064 | -271.5158 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en
Penwortham East / Rochdale SGT 1 GSP (132) | PENWORTHAM EAST/ROCHDALE | 132 | PENWORTHAM EAST / ROCHDALE | 350213 | 428032 | 323.9712 | 342.7211 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en
Penwortham West / Stanah GSP (132) | PENWORTHAM WEST/STANAH | 132 | PENWORTHAM WEST / STANAH | 350200 | 428029 | 234.1023 | 234.1023 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en
Rochdale GSP (132) | ROCHDALE | 132 | ROCHDALE | 385789 | 413832 | 131.1469 | 131.1469 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en
South Manchester GSP (132) | SOUTH MANCHESTER | 132 | SOUTH MANCHESTER | 381823 | 391734 | 187.0908 | 187.0908 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en
Stalybridge GSP (132) | STALYBRIDGE | 132 | STALYBRIDGE | 397172 | 399496 | 77.1566 | 174.0566 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en
Washway Farm / Kirkby GSP (132) | Washway Farm GSP / Kirkby GSP GROUP | 132 | WASHWAY FARM / KIRKBY | 345822 | 407637 | -106.5126 | -106.5126 | -15.7832 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en
Whitegate GSP (132) | WHITEGATE | 132 | WHITEGATE | 389202 | 403745 | 175.4843 | 279.2843 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en

## 7)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Connected (MW) | Accepted (MW) | Materiality Headroom (MW) | TIA Threshold (MW) | Awaiting TIA (MW) | Transmission FL Headroom (kA) | Project Progression Update
BOLD* | BOLD | 45.1 | 40.36 | N/A | N/A | N/A | 0 | N/A
BREDBURY | BREDBURY | 80.7 | 296 | 0 | 5 | 0 | 3 | Connections Reform
CARRINGTON | CARRINGTON | 164 | 39 | 0 | 5 | 0 | 5.13 | Connections Reform
HARKER1 | HARKER | 765.4 | 774.89 | 0 | 1 | 338.6 | TBC | Connections Reform
HEYSHAM | HUTTON | 302.1 | 495.8 | 0 | 1 | 0 | 0 | Connections Reform
HUTTON1 | HEYSHAM | 47.9 | 471.1 | 0 | 1 | 55.65 | TBC | Connections Reform
KEARSLEY | KEARSLEY | 226 | 39.3 | 0 | 1 | 0 | 1.29 | Connections Reform
KIRKBY | KIRKBY | 22.3 | 144.99 | 0 | 5 | 0 | 3 | Connections Reform
MACCLESFIELD | MACCLESFIELD | 47.9 | 0 | 0 | 5 | 0 | 3 | Connections Reform
PADIHAM2 | PADIHAM | 81.7 | 270.7 | 0 | 5 | 120 | 2.9 | Connections Reform
PENWORTHAM3 | PENWORTHAM | 498.8 | 399.72 | 0 | 5 | 124.4 | 3 | Connections Reform
ROCHDALE | ROCHDALE | 277.8 | 28.4 | 0 | 5 | 70 | 1.92 | Connections Reform
SOUTH MANCHESTER | SOUTH MANCHESTER | 95.5 | 262.6 | 0 | 1 | 0 | 0 | Connections Reform
STALYBRIDGE4 | STALYBRIDGE | 149.8 | 112.2 | 0 | 1 | 9 | 0.591 | Connections Reform
STANAH | STANAH | 239.4 | 78.89 | 0 | 5 | 20 | 3.01 | Connections Reform
WASHWAY FARM5 | WASHWAY FARM | 107.1 | 89 | 0 | 5 | 99.8 | 3 | Connections Reform
WHITEGATE | WHITEGATE | 120.3 | 3.06 | 0 | 5 | 0 | 3.09 | Connections Reform
Disclaimer | Appendix G Process |  | Definition
Note that the capacities reported in the table above were true prior to the ongoing Connections Reform, hence only indicative. SP ENW will update the table after Connections Reform, likely in Q1 (2027). | The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of SP ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  | TIA: Transmission Impact Assessment 1: Triggering New GSP (LANCASHIRE CONNECTION NODE B) 2: Triggering New GSP MANCHESTER NORTH CONNECTION NODE A 3: Triggering New GSP LANCASHIRE CONNECTION NODE C 4: Triggering New GSP STALYBRIDGE B 5: Triggering New GSP MERSEYSIDE CONNECTION NODE B * The site connected to the SP Manweb network and Appendix G submisions are carried out by SP Manweb on ENWLs behalf.