## Introduction
Network Headroom Report 2022 Data Workbook
This workbook is an accompaniment to our 2022 Network Headroom Report. It contains detailed datasets and interactive tools which allow our customers to understand headroom availability by Primary and Bulk Supply point, from a Demand and Generation point of view out to 2051.The Data contained in this workbook is based on our 2021 DFES data and existing network. Please note the value of headroom is calculated from two reference points, Firm Capacity at sites now, and the anticipated Firm Capacity at sites at the end of RIIO-ED2 (2028) based on changes to firm capacity driven by anticipated investment outcomes. Results should only be used as an indication and will be updated upon the next refresh of the data in two years time.
Future forecasts under the DFES may differ over time as a consequence of government policy, a change in consumer habits, changes to generation portfolio through new connections etc. In addition, our proposed investments may change because of changing forecasts and agreed allowances as set by Ofgem as part of each Distribution Price Control period. It must be highlighted at this point that this exercise mainly focuses on the available demand and generation headroom at the substation level only. Within this analysis, the methodology has taken into account potential circuit limitations for radial circuits, since this is considered within the published firm capacity values. However, for highly interconnected ring networks, there is a possibility that the methodology would provide an overestimate of the available headroom, as this might be reduced by circuit limitations. To account for some of the upstream circuit limitations or interconnected networks, the headroom methodology considers any known upstream circuit constraints for substation groups. Potential voltage constraints, power quality limitation and upstream transmission constraints have not been considered within the analysis. The information presented within the NPD is accurate at the point of publication.
CONTENTS
Section | Tab | Description
INTERACTIVE DATA TOOLS | Local Authority Look Up | List of all Primaries, BSPs and GSPs with a link to the local authrity in which they are located.
| Demand Headroom Summary Table | Select specific Primary or BSP to return overview of Demand Headroom 2022-2051
| Generation Headroom Summary Table | Select specific Primary or BSP and technology type to return overview of Generation Headroom 2022-2051
GROUP,BSP AND PRIMARY SUBSTATION DATASETS | Primary Headroom | All Primary data showing demand headroom by Scenario
| BSP Headroom | All BSP data showing demand headroom by Scenario
| Gen Primary Headroom | All Primary data showing generation headroom by Scenario
| Gen BSP Headroom | All BSP data showing generation headroom by Scenario
Version
1.3
Published
May 2022

## User Guide
Network Headroom Report 2022 Data Workbook - User Guide
This workbook should be used in conjunction with the following documents - Network Development Report, Network Headroom Report and Network Development Methodology
To review demand headroom at any Primary or Bulk Supply Point on the ENWL network, the user can initially identify the location via "Tab 1 Local Authority Look Up" which highlights the local authority in which the specific site resides. Please note some sites cover more than one local authority. Next the user should move to "Tab 2 Demand Headroom Table", and using the drop down menu in cell D4 select the Primary Substation as required. This will then cause the look up to display results from all five scenarios out to 2051.The user should then progress to cell D22 and select the Bulk Supply Point indicated in cell D5 to get a picture and understanding of the BSP headroom availability. Alternatively should the user only be interested in BSP capacity then cell D22 can be used to simply select the required BSP location.
Capacity is quoted as either Firm or Non Firm. Firm capacity is defined at a two transformer site as the Long Term Emergency Rating of the remaining in service transformer for the loss of the other transfomer or the HV transfer capablity of a single transfomer site. Non firm is based on the 3 min Auto Switching rating of the transfomer or the HV transfer capablity of a single transformer site.
A similar process can then be followed using "Tab 3 Generation headroom table". The drop down menu in cell D4 allows the Primary Substation to be selected with the results from all scenarios out to 2051 displayed. Use of Cell D4 allows the selection of the specific technology type to be made, allowing for example either Synchronous or Battery Technology to be selected. The user should then progress to cell D24 and select the Bulk Supply Point indicated in cell D5 to get a picture and understanding of the BSP headroom availability. It is recommended to also match the technology type via cell D25. Alternatively should the user only be interested in BSP capacity then cell D24 can be used to simply select the appropriate BSP location along with the technology type selection in cell D25.
Negative values shown in red cells in the report workbook tabs indicate where there are shortfalls in the capacity of our existing network and show us where future network interventions may be required; this allows users to understand the influence of the various scenarios on available network headroom up to 2051. Negative values also show where interventions may be required to accommodate demand or generation forecast requirements, and these should not be interpreted as a barrier to specific requirements. Review of the Network Development Plan Document will likely show an investment route planned to alleviate any highlighted shortfall.

## 1 - Local Authority Look Up
Primary | Bulk Supply Point | Grid Supply Point | Local Authority | Combined Local Authority
Albion St | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Alderley & Chelford | Moss Nook | South Manchester GSP | Cheshire East | Greater Manchester
Alston | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Ambleside | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Ancoats North T11 & T12 | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Ancoats North T14 | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Annie Pit | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Ansdell | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Ardwick | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Arnside | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Arnside | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Ashton (Golborne) | Golborne | Bold | St. Helens | Merseyside
Ashton (Golborne) | Golborne | Bold | Wigan | Greater Manchester
Ashton (Ribble) | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Fylde | Lancashire
Ashton (Ribble) | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Ashton On Mersey | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Ashton Under Lyne T11 & T12 | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Ashton Under Lyne T11 & T12 | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Ashton Under Lyne T13 | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Ashwood Dale | Buxton | Stalybridge GSP | High Peak | Derbyshire
Askam & Dalton | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Askam & Dalton | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Askam & Dalton | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Askerton Castle | Spadeadam 11/33kV | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Aspatria | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Atherton Town Centre | Atherton | Kearsley 132 GSP | Bolton | Greater Manchester
Atherton Town Centre | Atherton | Kearsley 132 GSP | Wigan | Lancashire
Athletic St | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Avenham | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Baguley | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Manchester | Greater Manchester
Baguley | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Bamber Bridge | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Barbara St | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Barrow | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Barrow | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Barton Dock Rd | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Bedford | Atherton | Kearsley 132 GSP | Salford | Greater Manchester
Bedford | Atherton | Kearsley 132 GSP | Warrington | Warrington
Bedford | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Belgrave | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Belgrave | Greenhill | Whitegate GSP | Tameside | Greater Manchester
Benchill | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Bentham | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Craven | Cumbria
Bentham | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Bispham | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Bispham | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Blackbull | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Blackbull | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Wyre | Lancashire
Blackburn | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Blackburn | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Hyndburn | Lancashire
Blackburn Rd Clayton | Huncoat | Padiham GSP | Hyndburn | Lancashire
Blackburn Rd Clayton | Huncoat | Padiham GSP | Ribble Valley | Lancashire
Blackfriars | Frederick Rd | Kearsley 132 GSP | Manchester | Greater Manchester
Blackfriars | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Blackley | Red Bank | Whitegate GSP | Bury | Greater Manchester
Blackley | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Blackpool | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Bollington |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
Bolton By Bowland | Padiham | Padiham GSP | Ribble Valley | Lancashire
Bolton Le Sands | Lancaster | Heysham GSP | Lancaster | Lancashire
Botany Bay | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Bow Lane | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Bow Lane | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Bowaters | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Bowdon | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Cheshire East | Cheshire East
Bowdon | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Bradford | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Bradshawgate | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Bramhall | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Bridgewater | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Brinksway | Adswood | Bredbury GSP | Stockport | Greater Manchester
Broadheath | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Broadway | Lancaster | Heysham GSP | Lancaster | Lancashire
Buckshaw | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Buckshaw | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Burnley | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Burnley | Burnley | Rochdale SGTs 2 3 4 | Pendle | Lancashire
Burnley Centre | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Burnley North | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Burnley North | Burnley | Rochdale SGTs 2 3 4 | Pendle | Lancashire
Burrow Beck | Lancaster | Heysham GSP | Lancaster | Lancashire
Burrow Beck | Lancaster | Heysham GSP | Wyre | Lancashire
Burscough Bridge | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Bury Town Centre | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Campbell St |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Cannon St | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Capontree | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Carleton | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Carlisle North | Carlisle North | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Carr St |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Castleton | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Catterall Waterworks | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Wyre | Lancashire
Cecil St | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Central Manchester | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Chadderton | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Chamberhall | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Chamberhall | Bury | Kearsley 132 GSP | Rochdale | Greater Manchester
Chamberhall | Bury | Kearsley 132 GSP | Rossendale | Lancashire
Chapel Wharf | Frederick Rd | Kearsley 132 GSP | Manchester | Greater Manchester
Chapel Wharf | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Chassen Rd | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Chatsworth St | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Cheadle Heath | Adswood | Bredbury GSP | Stockport | Greater Manchester
Cheadle Hulme | Adswood | Bredbury GSP | Stockport | Greater Manchester
Cheetham Hill | Agecroft | Kearsley 132 GSP | Bury | Greater Manchester
Cheetham Hill | Agecroft | Kearsley 132 GSP | Manchester | Greater Manchester
Cheetham Hill | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Chester Rd T11 & T12 | Stretford | South Manchester GSP | Trafford | Greater Manchester
Chester Rd T13 | Stretford | South Manchester GSP | Trafford | Greater Manchester
Chorley South | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Chorlton | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Chorlton | West Didsbury | South Manchester GSP | Trafford | Greater Manchester
Church | Huncoat | Padiham GSP | Hyndburn | Lancashire
Circle Sq | Longsight | Bredbury GSP | Manchester | Greater Manchester
Clarendon Rd | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Clarendon Rd | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Hyndburn | Lancashire
Clarendon Rd | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Claughton | Lancaster | Heysham GSP | Lancaster | Lancashire
Cleveleys | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Cleveleys | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Clifton Junction |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Clover Hill | Nelson | Padiham GSP | Burnley | Lancashire
Clover Hill | Nelson | Padiham GSP | Pendle | Lancashire
Cog Lane | Huncoat | Padiham GSP | Burnley | Lancashire
Coniston | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Copse Rd | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Cox Green | Bolton | Kearsley 132 GSP | Blackburn with Darwen | Lancashire
Cox Green | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Cox Green | Bolton | Kearsley 132 GSP | Chorley | Lancashire
Craggs Row & Bushell St | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Crown Lane | Westhoughton | Kearsley 132 GSP | Bolton | Greater Manchester
Crown Lane | Westhoughton | Kearsley 132 GSP | Chorley | Lancashire
Crown Lane | Westhoughton | Kearsley 132 GSP | Wigan | Greater Manchester
Culcheth | Golborne | Bold | Salford | Greater Manchester
Culcheth | Golborne | Bold | Warrington | Warrington
Culcheth | Golborne | Bold | Wigan | Greater Manchester
Cutacre |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Deansgate | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Denton East | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Denton West | Droylsden | Stalybridge GSP | Manchester | Greater Manchester
Denton West | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Dickinson St | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Didsbury | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Dodgson Rd | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Douglas St | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Droylsden East | Droylsden | Stalybridge GSP | Manchester | Greater Manchester
Droylsden East | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Dukinfield | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Dumers Lane | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Dumplington | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Eastlands | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Easton | Spadeadam 11/33kV | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Egremont | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Embleton | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Exchange St | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Failsworth | Chadderton | Whitegate GSP | Manchester | Greater Manchester
Failsworth | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Fallowfield | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Farnworth |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Feniscowles | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Ferodo | New Mills | Stalybridge GSP | High Peak | Derbyshire
Flat Lane | Padiham | Padiham GSP | Craven | Lancashire
Flat Lane | Padiham | Padiham GSP | Ribble Valley | Lancashire
Frederick Rd | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Fusehill | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Gale | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Gale | Belfield | Rochdale SGTs 2 3 4 | Rossendale | Lancashire
Garstang | Thornton | Penwortham West GSP / Stanah GSP GROUP | Lancaster | Lancashire
Garstang | Thornton | Penwortham West GSP / Stanah GSP GROUP | Preston | Lancashire
Garstang | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Gatley | Moss Nook | South Manchester GSP | Manchester | Greater Manchester
Gatley | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Gidlow | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Bolton | Greater Manchester
Gidlow | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Gidlow | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Gillsrow | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Gillsrow | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Glaxo | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Glossop | Hyde | Stalybridge GSP | High Peak | Derbyshire
Golborne | Golborne | Bold | St. Helens | Merseyside
Golborne | Golborne | Bold | Warrington | Warrington
Golborne | Golborne | Bold | Wigan | Greater Manchester
Gowhole | New Mills | Stalybridge GSP | Cheshire East | Cheshire East
Gowhole | New Mills | Stalybridge GSP | High Peak | Derbyshire
Gowhole | New Mills | Stalybridge GSP | Stockport | Greater Manchester
Grane Rd & Prinny Hill | Rossendale | Padiham GSP | Hyndburn | Lancashire
Grane Rd & Prinny Hill | Rossendale | Padiham GSP | Rossendale | Lancashire
Grange | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Great Harwood | Huncoat | Padiham GSP | Hyndburn | Lancashire
Great Harwood | Huncoat | Padiham GSP | Ribble Valley | Lancashire
Green Lane (Altrincham) | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Green Lane (Hazel Grove) | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Green St T11 | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Green St T12 & T13 | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Greenfield | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Greenfield | Hartshead-Heyrod | Stalybridge GSP | Rochdale | Greater Manchester
Greenhill | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Griffin | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Griffin | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Griffin | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Hadfield | Hyde | Stalybridge GSP | High Peak | Derbyshire
Hadfield | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Hall Cross | Peel | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Handforth | Moss Nook | South Manchester GSP | Cheshire East | Cheshire East
Handforth | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Hanging Bridge | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Hanging Bridge | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Hareholme | Rossendale | Padiham GSP | Burnley | Lancashire
Hareholme | Rossendale | Padiham GSP | Rossendale | Lancashire
Harpurhey | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Harwood | Bolton | Kearsley 132 GSP | Blackburn with Darwen | Lancashire
Harwood | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Harwood | Bolton | Kearsley 132 GSP | Bury | Greater Manchester
Hattersley | Hyde | Stalybridge GSP | High Peak | Derbyshire
Hattersley | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Haverthwaite | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Hawk Green | Hazel Grove | Bredbury GSP | Cheshire East | Cheshire East
Hawk Green | Hazel Grove | Bredbury GSP | High Peak | Derbyshire
Hawk Green | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Haydock | Golborne | Bold | St. Helens | Merseyside
Haydock | Golborne | Bold | Wigan | Greater Manchester
HDA No1 & HDA No2 | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
HDA No1 & HDA No2 | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Heady Hill | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Heap Bridge | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Heap Bridge | Bury | Kearsley 132 GSP | Rochdale | Greater Manchester
Heasandford | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Heaton Moor | Vernon Park | Bredbury GSP | Manchester | Greater Manchester
Heaton Moor | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Heaton Norris | Vernon Park | Bredbury GSP | Manchester | Greater Manchester
Heaton Norris | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Helwith Bridge | Padiham | Padiham GSP | Craven | Lancashire
Hensingham | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Heyrod | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Heyside | Royton | Whitegate GSP | Oldham | Greater Manchester
Heywood | Castleton | Rochdale SGTs 2 3 4 | Bury | Greater Manchester
Heywood | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Higher Mill | Moss Nook | South Manchester GSP | Manchester | Greater Manchester
Higher Mill | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | Blackburn with Darwen | Lancashire
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | Preston | Lancashire
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Hill Top T11 & T12 |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Hill Top T11 & T12 |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Hill Top T11 & T12 |  | Kearsley Local 33 GSP | Wigan | Greater Manchester
Hill Top T13 |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Hill Top T13 |  | Kearsley Local 33 GSP | Wigan | Greater Manchester
Hindley Green | Atherton | Kearsley 132 GSP | Bolton | Greater Manchester
Hindley Green | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Hollinwood | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Holme Rd | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Holt St | Bury | Kearsley 132 GSP | Blackburn with Darwen | Lancashire
Holt St | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Holt St | Bury | Kearsley 132 GSP | Rossendale | Lancashire
Hurst | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Hurst | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Hutton End & Skelton C | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Hutton End & Skelton C | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Hutton End & Skelton C | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Hyde | Hyde | Stalybridge GSP | Stockport | Greater Manchester
Hyde | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Hyndburn Rd | Huncoat | Padiham GSP | Hyndburn | Lancashire
Hyndburn Rd | Huncoat | Padiham GSP | Rossendale | Lancashire
India St | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Ingleton | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Craven | Cumbria
Irlam | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Salford | Greater Manchester
Irlam | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Irlam | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Warrington | Warrington
James St | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Kay St | Huncoat | Padiham GSP | Blackburn with Darwen | Lancashire
Kay St | Huncoat | Padiham GSP | Hyndburn | Lancashire
Kay St | Huncoat | Padiham GSP | Rossendale | Lancashire
Kendal | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Keswick | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Keswick | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Kingsway | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Kinkry Hill | Spadeadam 11/33kV | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Kirkby Lonsdale | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Kirkby Lonsdale | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Kirkby Moor | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Kirkby Moor | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Kirkby Stephen | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Kirkby Stephen | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Richmondshire | Cumbria
Kirkby Thore | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Kirkhall Lane | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Kitt Green | Orrell | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Knott Mill | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Knott Mill | Bloom St | South Manchester GSP | Salford | Greater Manchester
Knott Mill | Bloom St | South Manchester GSP | Trafford | Greater Manchester
Lamberhead | Orrell | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Lancaster | Lancaster | Heysham GSP | Lancaster | Lancashire
Langley | Chadderton | Whitegate GSP | Rochdale | Greater Manchester
Langroyd Rd | Nelson | Padiham GSP | Pendle | Lancashire
Leigh | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Levenshulme | Longsight | Bredbury GSP | Manchester | Greater Manchester
Leyland National | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Little Hulton |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Little Hulton |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Little Hulton |  | Kearsley Local 33 GSP | Wigan | Greater Manchester
Little Salkeld | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Little Salkeld | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Littleborough | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Longford Bridge | Stretford | South Manchester GSP | Trafford | Greater Manchester
Longridge | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Longridge | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Longsight | Longsight | Bredbury GSP | Manchester | Greater Manchester
Lostock | Westhoughton | Kearsley 132 GSP | Bolton | Greater Manchester
Lostock | Westhoughton | Kearsley 132 GSP | Chorley | Lancashire
Lower Darwen | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Lower Darwen | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Hyndburn | Lancashire
Lower Darwen | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Rossendale | Lancashire
Lyons Rd | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Manchester University | Longsight | Bredbury GSP | Manchester | Greater Manchester
Marple | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Marton | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Marton | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Maryport | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Melling | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Craven | Cumbria
Melling | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Melling | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Mereside | Peel | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Mereside | Peel | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Mereside | Peel | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Middleton Junction | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Middleton Junction | Chadderton | Whitegate GSP | Rochdale | Greater Manchester
Midway | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Milnrow | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Mintsfeet | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Monsall | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Monton | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Salford | Greater Manchester
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Fylde | Lancashire
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Wyre | Lancashire
Morton Park & Pirelli | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Morton Park & Pirelli | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Mosley Rd | Stretford | South Manchester GSP | Trafford | Greater Manchester
Moss Lane |  | Kearsley Local 33 GSP | Bury | Greater Manchester
Moss Lane |  | Kearsley Local 33 GSP | Rochdale | Greater Manchester
Moss Nook Primary | Moss Nook Primary | South Manchester GSP | Cheshire East | Cheshire East
Moss Nook Primary | Moss Nook Primary | South Manchester GSP | Manchester | Greater Manchester
Moss Nook Primary | Moss Nook Primary | South Manchester GSP | Stockport | Greater Manchester
Moss Side (Leyland) & Seven Stars | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Moss Side (Leyland) & Seven Stars | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Moss Side (Longsight) | Longsight | Bredbury GSP | Manchester | Greater Manchester
Moss Side (Longsight) | Longsight | Bredbury GSP | Trafford | Greater Manchester
Mossley | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Mossley | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Mount St | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Salford | Greater Manchester
Musgrave Rd | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Nelson | Nelson | Padiham GSP | Pendle | Lancashire
New Moston | Chadderton | Whitegate GSP | Manchester | Greater Manchester
New Moston | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Newbiggin on Lune | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Newby | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Newton | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Newton Heath | Chadderton | Whitegate GSP | Manchester | Greater Manchester
Newton Heath | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Newton Le Willows | Golborne | Bold | St. Helens | Merseyside
Newtongate T11 & T12 | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Newtongate T13 | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Norbreck | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Norbury | Hazel Grove | Bredbury GSP | Cheshire East | Cheshire East
Norbury | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Northenden | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Northenden | West Didsbury | South Manchester GSP | Trafford | Greater Manchester
NWGB Partington | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Offerton | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Openshaw | Droylsden | Stalybridge GSP | Manchester | Greater Manchester
Openshaw | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Ormskirk | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Padiham | Padiham | Padiham GSP | Burnley | Lancashire
Padiham | Padiham | Padiham GSP | Hyndburn | Lancashire
Padiham | Padiham | Padiham GSP | Pendle | Lancashire
Padiham | Padiham | Padiham GSP | Ribble Valley | Lancashire
Peel St & Ribblesdale T13 | Padiham | Padiham GSP | Pendle | Lancashire
Peel St & Ribblesdale T13 | Padiham | Padiham GSP | Ribble Valley | Lancashire
Pendleton | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Petteril Bank | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Petteril Bank | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Phillips Lane | Nelson | Padiham GSP | Pendle | Lancashire
Piccadilly | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Pimbo | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Portwood | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Poulton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Poulton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Poynton | Hazel Grove | Bredbury GSP | Cheshire East | Cheshire East
Preesall | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Preston East | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Preston East | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Preston Old Rd | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Prestwich | Agecroft | Kearsley 132 GSP | Bury | Greater Manchester
Prestwich | Agecroft | Kearsley 132 GSP | Manchester | Greater Manchester
Prestwich | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Pringle St | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Queens Park | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Radcliffe | Radcliffe | Kearsley 132 GSP | Bolton | Greater Manchester
Radcliffe | Radcliffe | Kearsley 132 GSP | Bury | Greater Manchester
Randal St | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Randal St | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Rawtenstall Rd | Rossendale | Padiham GSP | Hyndburn | Lancashire
Rawtenstall Rd | Rossendale | Padiham GSP | Rossendale | Lancashire
Reddish Vale | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Reddish Vale | Vernon Park | Bredbury GSP | Tameside | Greater Manchester
Ribblesdale T14 | Padiham | Padiham GSP | Ribble Valley | Lancashire
Ribbleton | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Ringley |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Risley | Risley | Risley | Warrington | Warrington
Robert Hall St | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Rochdale Central | Rochdale Central | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Roman Rd | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Romiley | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Rossall | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Royton | Royton | Whitegate GSP | Oldham | Greater Manchester
S.E. Macclesfield |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
S.E. Macclesfield |  | Macclesfield 33 GSP | Staffordshire Moorlands | Staffordshire
S.W. Macclesfield |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
Sale | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Sale Moor | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Salford Quays | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Sandgate | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Scarisbrick | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | Sefton | Merseyside
Scarisbrick | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Sebergham | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Sebergham | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Sebergham | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Sedbergh | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Richmondshire | Cumbria
Sedbergh | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Selsmire | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Selsmire | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Settle | Padiham | Padiham GSP | Craven | Lancashire
Shannon St South | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Shap | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Shaw | Royton | Whitegate GSP | Oldham | Greater Manchester
Shaw | Royton | Whitegate GSP | Rochdale | Greater Manchester
Siddick | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Silloth | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Skelmersdale | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Slipway | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Snipe | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
South Park | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Spa Rd | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Spadeadam 132/11kV* | Spadeadam 132/11kV* | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Spadeadam 132/11kV* | Spadeadam 132/11kV* | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Northumberland | Cumbria
Spotland | Rochdale Central | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Spring Cottage | Nelson | Padiham GSP | Pendle | Lancashire
Spring Garden St 11kV | Lancaster | Heysham GSP | Lancaster | Lancashire
Spring Garden St 6.6kV | Lancaster | Heysham GSP | Lancaster | Lancashire
Squires Gate | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Squires Gate | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
St Annes | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
St Marys | Greenhill | Whitegate GSP | Oldham | Greater Manchester
St Marys St | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
St Thomas Rd | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Stainburn | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Standish | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Standish | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Standish | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Wigan | Lancashire
Strangeways | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Strangeways | Red Bank | Whitegate GSP | Salford | Greater Manchester
Strawberry Bank | Huncoat | Padiham GSP | Hyndburn | Lancashire
Stuart St | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Stuart St | Stuart St | Stalybridge GSP | Tameside | Greater Manchester
Stubbins | Rossendale | Padiham GSP | Bury | Greater Manchester
Stubbins | Rossendale | Padiham GSP | Rossendale | Lancashire
Swinton | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Tame Valley | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Tardy Gate | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Tarleton | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Tarleton | Wrightington | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Tarleton | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
The Height | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Thornton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Thornton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Townley St | Chadderton | Whitegate GSP | Rochdale | Greater Manchester
Trafford | Stretford | South Manchester GSP | Trafford | Greater Manchester
Trafford Park North | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Trimpell | Trimpell | Heysham GSP | Lancaster | Lancashire
Trinity | Frederick Rd | Kearsley 132 GSP | Manchester | Greater Manchester
Trinity | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Tulketh | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Ulverston | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Ulverston | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Union Rd | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Upholland | Orrell | Washway Farm GSP / Kirkby GSP GROUP | St. Helens | Merseyside
Upholland | Orrell | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Upholland | Orrell | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Urmston | Stretford | South Manchester GSP | Trafford | Greater Manchester
Victoria Park | Longsight | Bredbury GSP | Manchester | Greater Manchester
Warbreck | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Warbreck | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Wardleworth | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Warton | Peel | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Waterhead | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Waterswallows | Buxton | Stalybridge GSP | Derbyshire Dales | Derbyshire
Waterswallows | Buxton | Stalybridge GSP | High Peak | Derbyshire
Weaste | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Werneth | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Wesley Place Bacup | Rossendale | Padiham GSP | Rossendale | Lancashire
West Didsbury | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Westgate | Lancaster | Heysham GSP | Lancaster | Lancashire
Westhoughton | Westhoughton | Kearsley 132 GSP | Bolton | Greater Manchester
Westhoughton | Westhoughton | Kearsley 132 GSP | Salford | Greater Manchester
Westhoughton | Westhoughton | Kearsley 132 GSP | Wigan | Greater Manchester
Westlinton | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Whalley | Padiham | Padiham GSP | Pendle | Lancashire
Whalley | Padiham | Padiham GSP | Ribble Valley | Lancashire
Whalley Range | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Whalley Range | West Didsbury | South Manchester GSP | Trafford | Greater Manchester
Whasset | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Whittle Le Woods | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Whittle Le Woods | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Whitworth | Rochdale Central | Rochdale SGTs 2 3 4 | Rossendale | Lancashire
Wigton | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Wigton | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Willow Hey | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Willowbank | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Willowbank | Greenhill | Whitegate GSP | Rochdale | Greater Manchester
Willowholme | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Wilmslow | Moss Nook | South Manchester GSP | Cheshire East | Cheshire East
Windermere | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Winifred Rd | Adswood | Bredbury GSP | Stockport | Greater Manchester
Withington | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Withyfold Drive |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
Woodbine St | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Woodfield Rd | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Woodhill Lane | Lancaster | Heysham GSP | Lancaster | Lancashire
Woodhouse Park | Moss Nook | South Manchester GSP | Manchester | Greater Manchester
Woodhouse Park | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Woodley | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Woolfold | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Wordsworth St | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Worsley Mesnes | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Wrightington | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Wrightington | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Wrightington | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Wigan | Lancashire
Yealand | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Yealand | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria

## 2 - Demand headroom table
Select Primary | Albion St |  | Primary Demand Headroom (MVA)
BSP | LOWER DARWEN | 367434 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051
GSP | ROCHDALE
Grid Coordinates | Easting | Northing
| 367434 | 426087
Best View | Firm |  | 8.6068 | 8.3576 | 8.1121 | 7.8149 | 7.5145 | 7.2842 | 6.863 | 6.5161 | 6.1812 | 5.7052 | 4.1756 | 2.7136 | 2.7025 | 3.0641
| Non Firm |  | 13.2438 | 12.9946 | 12.7491 | 12.4519 | 12.1515 | 11.9212 | 11.5 | 11.1531 | 10.8182 | 10.3422 | 8.8126 | 7.3506 | 7.3395 | 7.7011
Steady Progression | Firm |  | 8.7874 | 8.6869 | 8.3881 | 8.0655 | 7.7952 | 7.5897 | 7.1916 | 6.8648 | 6.5403 | 6.1281 | 5.0947 | 4.4825 | 4.117 | 4.0767
| Non Firm |  | 13.4244 | 13.3239 | 13.0251 | 12.7025 | 12.4322 | 12.2267 | 11.8286 | 11.5018 | 11.1773 | 10.7651 | 9.7317 | 9.1195 | 8.754 | 8.7137
System Transformation | Firm |  | 8.6168 | 8.3808 | 8.1498 | 7.8658 | 7.5821 | 7.3676 | 6.9642 | 6.6335 | 6.3209 | 5.8931 | 4.4954 | 3.1415 | 3.1619 | 3.5498
| Non Firm |  | 13.2538 | 13.0178 | 12.7868 | 12.5028 | 12.2191 | 12.0046 | 11.6012 | 11.2705 | 10.9579 | 10.5301 | 9.1324 | 7.7785 | 7.7989 | 8.1868
Consumer Transformation | Firm |  | 8.6181 | 8.3822 | 8.1578 | 7.8867 | 7.6345 | 7.4608 | 7.0968 | 6.8113 | 6.5959 | 6.2964 | 3.5991 | -1.87 | -6.1462 | -8.7305
| Non Firm |  | 13.2551 | 13.0192 | 12.7948 | 12.5237 | 12.2715 | 12.0978 | 11.7338 | 11.4483 | 11.2329 | 10.9334 | 8.2361 | 2.767 | -1.5092 | -4.0935
Leading the Way | Firm |  | 8.6554 | 8.4218 | 8.207 | 7.9813 | 7.653 | 7.5506 | 7.2544 | 7.0455 | 6.5837 | 4.7816 | -1.2205 | -5.8365 | -8.6009 | -7.4049
| Non Firm |  | 13.2924 | 13.0588 | 12.844 | 12.6183 | 12.29 | 12.1876 | 11.8914 | 11.6825 | 11.2207 | 9.4186 | 3.4165 | -1.1995 | -3.9639 | -2.7679
Select BSP | Adswood |  | BSP Demand Headroom (MVA)
GSP | BREDBURY |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051
Grid Coordinates | Easting | Northing
| 389188 | 388310
Best View | Firm |  | 54.6641 | 45.5345 | 44.8965 | 44.0559 | 42.8721 | 41.5098 | 39.8999 | 38.3439 | 36.7654 | 34.9981 | 28.6677 | 25.4915 | 24.8542 | 25.5513
| Non Firm |  | 72.6641 | 63.5345 | 62.8965 | 62.0559 | 60.8721 | 59.5098 | 57.8999 | 56.3439 | 54.7654 | 52.9981 | 46.6677 | 43.4915 | 42.8542 | 43.5513
Steady Progression | Firm |  | 59.4247 | 54.8911 | 53.9733 | 53.0448 | 51.9491 | 50.686 | 49.1692 | 47.6804 | 46.1227 | 44.5389 | 39.8896 | 36.7517 | 35.0036 | 33.9783
| Non Firm |  | 77.4247 | 72.8911 | 71.9733 | 71.0448 | 69.9491 | 68.686 | 67.1692 | 65.6804 | 64.1227 | 62.5389 | 57.8896 | 54.7517 | 53.0036 | 51.9783
System Transformation | Firm |  | 54.7176 | 45.6662 | 45.084 | 44.2124 | 43.0836 | 41.7851 | 40.2399 | 38.7464 | 37.2585 | 35.6802 | 29.8935 | 27.3114 | 26.9819 | 27.8367
| Non Firm |  | 72.7176 | 63.6662 | 63.084 | 62.2124 | 61.0836 | 59.7851 | 58.2399 | 56.7464 | 55.2585 | 53.6802 | 47.8935 | 45.3114 | 44.9819 | 45.8367
Consumer Transformation | Firm |  | 54.7183 | 45.6608 | 45.129 | 44.4041 | 43.4121 | 42.2554 | 40.8369 | 39.4934 | 38.3155 | 37.1311 | 28.8948 | 11.4004 | -2.0657 | -10.7857
| Non Firm |  | 72.7183 | 63.6608 | 63.129 | 62.4041 | 61.4121 | 60.2554 | 58.8369 | 57.4934 | 56.3155 | 55.1311 | 46.8948 | 29.4004 | 15.9343 | 7.2143
Leading the Way | Firm |  | 54.7368 | 45.5852 | 45.0855 | 44.4816 | 43.6516 | 42.7417 | 41.5453 | 40.4652 | 39.0215 | 34.8503 | 15.2455 | -0.37915 | -9.0785 | -5.9478
| Non Firm |  | 72.7368 | 63.5852 | 63.0855 | 62.4816 | 61.6516 | 60.7417 | 59.5453 | 58.4652 | 57.0215 | 52.8503 | 33.2455 | 17.6208 | 8.9215 | 12.0522

## 3 - Generation headroom table
Select Primary | ALBION ST |  | Primary Generation Headroom (MVA)
Select Technology | Generation – Synchronous (HV)
BSP | LOWER DARWEN | ROCHDALE
GSP | ROCHDALE | ROCHDALE
Grid Coordinates | Easting | Northing | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051
| 367434 | 426087
Best View | Non Firm |  | 11.0248 | 10.8637 | 10.6855 | 10.4665 | 10.186 | 9.9966 | 10.0743 | 10.0926 | 10.0918 | 10.0534 | 9.8531 | 10.0553 | 11.3873 | 12.2171
Steady Progression | Non Firm |  | 11.0963 | 10.9815 | 10.8349 | 10.6583 | 10.5108 | 10.3541 | 10.3005 | 10.251 | 10.1963 | 10.1293 | 10.0251 | 10.3054 | 11.466 | 11.9278
System Transformation | Non Firm |  | 11.09 | 11.0609 | 10.9678 | 10.8627 | 10.7485 | 10.5957 | 10.5438 | 10.4972 | 10.4213 | 10.393 | 10.2146 | 10.4592 | 12.0448 | 12.8499
Consumer Transformation | Non Firm |  | 11.0248 | 10.8782 | 10.711 | 10.5069 | 10.2715 | 10.089 | 10.1241 | 10.1289 | 10.1038 | 10.0369 | 9.5519 | 9.0848 | 9.7108 | 10.1794
Leading the Way | Non Firm |  | 11.0311 | 11.0461 | 11.009 | 10.9105 | 10.8438 | 10.8285 | 10.7644 | 10.7156 | 10.6405 | 10.3939 | 10.6893 | 9.8695 | 10.7283 | 10.6485
Capacity Limited Primary | Reason
Heasandford | Project in flight to replace Switchgear - PIU 2023
Trinity | Switchgear to be replaced in RIIO-ED2
Spring Cottage | Switchgear to be replaced in RIIO-ED2
Rossall | Thermal capacity limits headroom - Review in RIIO-ED2
Select BSP | LOWER DARWEN |  | BSP Generation Headroom (MVA)
Select Technology | Generation – Synchronous
GSP | ROCHDALE
Grid Coordinates | Easting | Northing | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051
| 369695 | 424981
Best View | Non Firm |  | 14.0012 | 10.6661 | 7.6812 | 4.6934 | 2.0354 | -0.79402 | -1.2555 | -1.6762 | -2.1801 | -2.8066 | -4.059 | 4.6419 | 23.5544 | 27.9995
Steady Progression | Non Firm |  | 14.3423 | 11.3559 | 8.4624 | 5.5665 | 3.0252 | 0.39016 | 0.055839 | -0.23463 | -0.5501 | -0.92379 | -0.82283 | 6.0106 | 18.1634 | 20.8131
System Transformation | Non Firm |  | 14.3243 | 11.3571 | 8.465 | 5.5771 | 3.0069 | 0.47281 | 0.069117 | -0.3191 | -0.73048 | -1.2055 | -1.26 | 9.0563 | 28.851 | 33.9158
Consumer Transformation | Non Firm |  | 13.9994 | 10.6605 | 7.6419 | 4.624 | 1.9618 | -0.84779 | -1.3607 | -1.8783 | -2.427 | -3.0994 | -5.4754 | -0.24107 | 15.1222 | 17.2165
Leading the Way | Non Firm |  | 14.0193 | 13.3322 | 12.736 | 11.8926 | 11.294 | 10.1569 | 9.3242 | 8.9993 | 8.5439 | 7.645 | 25.3662 | 20.4016 | 19.0969 | 18.7541
Capacity Limited BSPs | Reason
Kendal BSP | Project in flight to replace Switchgear - PIU 2023
Royton BSP | Switchgear to be replaced in RIIO-ED2
Stainburn & Siddick | Switchgear to be replaced in RIIO-ED2

## Primary Headroom
Click the scenario name to move directly to the associated results | Best View
Steady Progression
System Transformation
Consumer Transformation
Leading the Way
| Primary | Best View Firm Headroom MVA | [13 empty] | Best View Non Firm Headroom MVA | [13 empty] | Steady Progression Firm Headroom MVA | [13 empty] | Steady Progression Non Firm Headroom MVA | [13 empty] | System Transformation Firm Headroom MVA | [13 empty] | System Transformation Non Firm Headroom MVA | [13 empty] | Consumer Transformation Firm Headroom MVA | [13 empty] | Consumer Transformation Non Firm Headroom MVA | [13 empty] | Leading the Way Firm Headroom MVA | [13 empty] | Leading the Way Non Firm Headroom MVA
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | Easting | Northing | BSP | GSP
| Albion St | 8.6068 | 8.3576 | 8.1121 | 7.8149 | 7.5145 | 7.2842 | 6.863 | 6.5161 | 6.1812 | 5.7052 | 4.1756 | 2.7136 | 2.7025 | 3.0641 | 13.2438 | 12.9946 | 12.7491 | 12.4519 | 12.1515 | 11.9212 | 11.5 | 11.1531 | 10.8182 | 10.3422 | 8.8126 | 7.3506 | 7.3395 | 7.7011 | 8.7874 | 8.6869 | 8.3881 | 8.0655 | 7.7952 | 7.5897 | 7.1916 | 6.8648 | 6.5403 | 6.1281 | 5.0947 | 4.4825 | 4.117 | 4.0767 | 13.4244 | 13.3239 | 13.0251 | 12.7025 | 12.4322 | 12.2267 | 11.8286 | 11.5018 | 11.1773 | 10.7651 | 9.7317 | 9.1195 | 8.754 | 8.7137 | 8.6168 | 8.3808 | 8.1498 | 7.8658 | 7.5821 | 7.3676 | 6.9642 | 6.6335 | 6.3209 | 5.8931 | 4.4954 | 3.1415 | 3.1619 | 3.5498 | 13.2538 | 13.0178 | 12.7868 | 12.5028 | 12.2191 | 12.0046 | 11.6012 | 11.2705 | 10.9579 | 10.5301 | 9.1324 | 7.7785 | 7.7989 | 8.1868 | 8.6181 | 8.3822 | 8.1578 | 7.8867 | 7.6345 | 7.4608 | 7.0968 | 6.8113 | 6.5959 | 6.2964 | 3.5991 | -1.87 | -6.1462 | -8.7305 | 13.2551 | 13.0192 | 12.7948 | 12.5237 | 12.2715 | 12.0978 | 11.7338 | 11.4483 | 11.2329 | 10.9334 | 8.2361 | 2.767 | -1.5092 | -4.0935 | 8.6554 | 8.4218 | 8.207 | 7.9813 | 7.653 | 7.5506 | 7.2544 | 7.0455 | 6.5837 | 4.7816 | -1.2205 | -5.8365 | -8.6009 | -7.4049 | 13.2924 | 13.0588 | 12.844 | 12.6183 | 12.29 | 12.1876 | 11.8914 | 11.6825 | 11.2207 | 9.4186 | 3.4165 | -1.1995 | -3.9639 | -2.7679 | 367434 | 426087 | LOWER DARWEN | ROCHDALE
| Alderley & Chelford | 10.2703 | 9.1063 | 8.6761 | 8.1984 | 7.6469 | 7.0104 | 6.2341 | 5.6925 | 2.627 | 1.918 | -1.3054 | -3.1921 | -3.5235 | -3.25 | 16.9603 | 15.7963 | 15.3661 | 14.8884 | 14.3369 | 13.7004 | 12.9241 | 12.3825 | 9.317 | 8.608 | 5.3846 | 3.4979 | 3.1665 | 3.44 | 10.8757 | 10.2567 | 9.7619 | 9.2833 | 8.7739 | 8.2044 | 7.4838 | 6.9714 | 6.3489 | 5.7343 | 3.829 | 2.3466 | 1.5089 | 1.0854 | 17.5657 | 16.9467 | 16.4519 | 15.9733 | 15.4639 | 14.8944 | 14.1738 | 13.6614 | 13.0389 | 12.4243 | 10.519 | 9.0366 | 8.1989 | 7.7754 | 10.2776 | 9.1352 | 8.725 | 8.2639 | 7.7346 | 7.1213 | 6.3685 | 5.8462 | 2.814 | 2.1802 | -0.7782 | -2.4768 | -2.7291 | -2.4412 | 16.9676 | 15.8252 | 15.415 | 14.9539 | 14.4246 | 13.8113 | 13.0585 | 12.5362 | 9.504 | 8.8702 | 5.9118 | 4.2132 | 3.9609 | 4.2488 | 10.3176 | 9.2039 | 8.8322 | 8.4131 | 7.9313 | 7.3663 | 6.6398 | 6.1557 | 3.2448 | 2.7576 | -0.42797 | -5.2243 | -7.1647 | -8.3156 | 17.0076 | 15.8939 | 15.5222 | 15.1031 | 14.6213 | 14.0563 | 13.3298 | 12.8457 | 9.9348 | 9.4476 | 6.262 | 1.4657 | -0.47471 | -1.6256 | 10.1268 | 8.8187 | 8.4687 | 8.1076 | 7.6625 | 7.1653 | 6.516 | 5.5709 | 2.7076 | 1.8486 | -3.8163 | -6.4969 | -7.5051 | -6.6475 | 16.8168 | 15.5087 | 15.5087 | 14.7976 | 14.3525 | 13.8553 | 13.206 | 12.2609 | 9.3976 | 8.5386 | 2.8737 | 0.19312 | -0.81511 | 0.042465 | 385044 | 379026 | MOSS NOOK | SOUTH MANCHESTER
| Alston | 0.0038159 | -0.084594 | -0.13047 | -0.16382 | -0.23684 | -0.31154 | -0.37831 | -0.42001 | -0.50097 | -0.66117 | -1.3424 | -1.742 | -1.96 | -1.8982 | 1.3038 | 1.2154 | 1.1695 | 1.1362 | 1.0632 | 0.98846 | 0.92169 | 0.87999 | 0.79903 | 0.63883 | -0.042412 | -0.442 | -0.66005 | -0.59816 | 0.048071 | -0.0015247 | -0.056642 | -0.12978 | -0.18405 | -0.26451 | -0.34916 | -0.44304 | -0.54654 | -0.63452 | -0.84225 | -1.2855 | -1.658 | -1.913 | 1.3481 | 1.2985 | 1.2434 | 1.1702 | 1.116 | 1.0355 | 0.95084 | 0.85696 | 0.75346 | 0.66548 | 0.45775 | 0.014459 | -0.35798 | -0.61303 | 0.0052413 | -0.081282 | -0.12537 | -0.15716 | -0.22764 | -0.29966 | -0.36399 | -0.40387 | -0.48134 | -0.59871 | -1.225 | -1.5832 | -1.7738 | -1.713 | 1.3052 | 1.2187 | 1.1746 | 1.1428 | 1.0724 | 1.0003 | 0.93601 | 0.89613 | 0.81866 | 0.70129 | 0.074975 | -0.28317 | -0.47384 | -0.41303 | 0.0045599 | -0.086923 | -0.13669 | -0.18731 | -0.29045 | -0.37616 | -0.51763 | -0.60214 | -0.73511 | -0.89537 | -1.5608 | -2.4232 | -2.9554 | -3.3155 | 1.3046 | 1.2131 | 1.1633 | 1.1127 | 1.0095 | 0.92384 | 0.78237 | 0.69786 | 0.56489 | 0.40463 | -0.26078 | -1.1232 | -1.6554 | -2.0155 | 0.0015535 | -0.09674 | -0.14793 | -0.19734 | -0.31093 | -0.39826 | -0.5315 | -0.60734 | -0.75567 | -1.0251 | -2.1082 | -2.8528 | -3.1942 | -3.0921 | 1.3016 | 1.2033 | 1.2033 | 1.1027 | 0.98907 | 0.90174 | 0.7685 | 0.69266 | 0.54433 | 0.2749 | -0.80816 | -1.5528 | -1.8942 | -1.7921 | 372125 | 546499 | PENRITH & SHAP | HUTTON
| Ambleside | 6.845 | 6.3643 | 6.0642 | 5.9524 | 5.7912 | 5.4564 | 5.2022 | 5.1106 | 4.8265 | 4.5181 | 3.4275 | 2.8324 | 2.6268 | 2.7809 | 16.045 | 15.5643 | 15.2642 | 15.1524 | 14.9912 | 14.6564 | 14.4022 | 14.3106 | 14.0265 | 13.7181 | 12.6275 | 12.0324 | 11.8268 | 11.9809 | 7.0356 | 6.6773 | 6.3614 | 6.151 | 5.8984 | 5.4708 | 5.1069 | 4.8863 | 4.4378 | 3.963 | 3.5081 | 3.1748 | 3.0398 | 2.9212 | 16.2356 | 15.8773 | 15.5614 | 15.351 | 15.0984 | 14.6708 | 14.3069 | 14.0863 | 13.6378 | 13.163 | 12.7081 | 12.3748 | 12.2398 | 12.1212 | 6.8823 | 6.411 | 6.2118 | 5.9963 | 5.8956 | 5.6304 | 5.3328 | 5.2031 | 4.9075 | 4.6283 | 3.6282 | 3.1011 | 2.9296 | 3.0882 | 16.0823 | 15.611 | 15.4118 | 15.1963 | 15.0956 | 14.8304 | 14.5328 | 14.4031 | 14.1075 | 13.8283 | 12.8282 | 12.3011 | 12.1296 | 12.2882 | 6.8587 | 6.389 | 6.1341 | 5.9946 | 5.8718 | 5.5685 | 5.2473 | 5.0859 | 4.7809 | 4.5471 | 3.2909 | 0.73759 | -1.1846 | -2.527 | 16.0587 | 15.589 | 15.3341 | 15.1946 | 15.0718 | 14.7685 | 14.4473 | 14.2859 | 13.9809 | 13.7471 | 12.4909 | 9.9376 | 8.0154 | 6.673 | 6.8317 | 6.3618 | 6.1322 | 6.0097 | 5.9168 | 5.668 | 5.3839 | 5.2828 | 5.0199 | 4.4055 | 1.5125 | -0.74053 | -2.0852 | -1.7034 | 16.0317 | 15.5618 | 15.5618 | 15.2097 | 15.1168 | 14.868 | 14.5839 | 14.4828 | 14.2199 | 13.6055 | 10.7125 | 8.4595 | 7.1148 | 7.4966 | 337602 | 503506 | KENDAL (PARKSIDE RD) | HUTTON
| Ancoats North T11 & T12 | 6.0811 | 5.0572 | 4.6571 | 4.4406 | 4.2422 | 4.0002 | 3.7561 | 3.5031 | 3.1896 | 2.9156 | 1.7768 | 0.85534 | 0.32711 | 0.08173 | 10.2181 | 9.1942 | 8.7941 | 8.5776 | 8.3792 | 8.1372 | 7.8931 | 7.6401 | 7.3266 | 7.0526 | 5.9138 | 4.9923 | 4.4641 | 4.2187 | 6.5802 | 6.0321 | 5.6593 | 5.3824 | 5.1045 | 4.771 | 4.4426 | 4.0258 | 3.3479 | 2.639 | 1.998 | 1.5731 | 1.1883 | 0.82822 | 10.7172 | 10.1691 | 9.7963 | 9.5194 | 9.2415 | 8.908 | 8.5796 | 8.1628 | 7.4849 | 6.776 | 6.135 | 5.7101 | 5.3253 | 4.9652 | 6.0936 | 5.0871 | 4.7092 | 4.5298 | 4.375 | 4.1563 | 3.9698 | 3.7313 | 3.4759 | 3.2019 | 2.0567 | 1.2669 | 0.80248 | 0.62504 | 10.2306 | 9.2241 | 8.8462 | 8.6668 | 8.512 | 8.2933 | 8.1068 | 7.8683 | 7.6129 | 7.3389 | 6.1937 | 5.4039 | 4.9395 | 4.762 | 6.0918 | 5.0739 | 4.6854 | 4.4822 | 4.2792 | 4.0203 | 3.7399 | 3.4345 | 3.0972 | 2.7755 | 1.1463 | -2.0179 | -4.563 | -6.4115 | 10.2288 | 9.2109 | 8.8224 | 8.6192 | 8.4162 | 8.1573 | 7.8769 | 7.5715 | 7.2342 | 6.9125 | 5.2833 | 2.1191 | -0.42596 | -2.2745 | 6.105 | 5.0936 | 4.7349 | 4.5724 | 4.4059 | 4.1923 | 3.9548 | 3.6617 | 3.3225 | 2.6468 | -0.94211 | -3.9529 | -5.6604 | -5.3696 | 10.242 | 9.2306 | 9.2306 | 8.7094 | 8.5429 | 8.3293 | 8.0918 | 7.7987 | 7.4595 | 6.7838 | 3.1949 | 0.18409 | -1.5234 | -1.2326 | 385022 | 398830 | RED BANK | WHITEGATE
| Ancoats North T14 | 2.3065 | 2.0182 | 1.9529 | 1.9218 | 1.7672 | 1.6244 | 1.4683 | 1.3943 | 1.2124 | 1.0783 | 0.71471 | 0.44638 | 0.3262 | 0.272 | 7.0565 | 6.7682 | 6.7029 | 6.6718 | 6.5172 | 6.3744 | 6.2183 | 6.1443 | 5.9624 | 5.8283 | 5.4647 | 5.1964 | 5.0762 | 5.022 | 2.5135 | 2.3876 | 2.1912 | 2.0402 | 1.7772 | 1.5399 | 1.2126 | 0.75514 | 0.22552 | -0.33077 | -0.61508 | -0.79303 | -0.91774 | -0.95722 | 7.2635 | 7.1376 | 6.9412 | 6.7902 | 6.5272 | 6.2899 | 5.9626 | 5.5051 | 4.9755 | 4.4192 | 4.1349 | 3.957 | 3.8323 | 3.7928 | 2.3189 | 2.0442 | 1.9933 | 1.9745 | 1.8363 | 1.7091 | 1.57 | 1.5104 | 1.3491 | 1.2377 | 0.90168 | 0.69384 | 0.60186 | 0.59638 | 7.0689 | 6.7942 | 6.7433 | 6.7245 | 6.5863 | 6.4591 | 6.32 | 6.2604 | 6.0991 | 5.9877 | 5.6517 | 5.4438 | 5.3519 | 5.3464 | 2.3224 | 2.0497 | 1.9997 | 1.9824 | 1.839 | 1.7045 | 1.5538 | 1.4821 | 1.3041 | 1.1779 | 0.758 | 0.15999 | -0.22741 | -0.58582 | 7.0724 | 6.7997 | 6.7497 | 6.7324 | 6.589 | 6.4545 | 6.3038 | 6.2321 | 6.0541 | 5.9279 | 5.508 | 4.91 | 4.5226 | 4.1642 | 2.3365 | 2.0743 | 2.0435 | 2.0517 | 1.9369 | 1.8328 | 1.7106 | 1.6684 | 1.5264 | 1.3538 | 0.61645 | -0.053534 | -0.46594 | -0.23682 | 7.0865 | 6.8243 | 6.8243 | 6.8017 | 6.6869 | 6.5828 | 6.4606 | 6.4184 | 6.2764 | 6.1038 | 5.3664 | 4.6965 | 4.2841 | 4.5132 | 385032 | 398840 | RED BANK | WHITEGATE
| Annie Pit | 4.4859 | 4.1526 | 4.1432 | 3.8984 | 3.6457 | 3.337 | 2.9273 | 2.518 | 2.1566 | 1.6804 | 0.17857 | -0.95528 | -1.3741 | -1.4438 | 9.9859 | 9.6526 | 9.6432 | 9.3984 | 9.1457 | 8.837 | 8.4273 | 8.018 | 7.6566 | 7.1804 | 5.6786 | 4.5447 | 4.1259 | 4.0562 | 4.8071 | 4.7161 | 4.3669 | 3.9073 | 3.3603 | 2.9035 | 2.2008 | 1.4983 | 0.78344 | -0.098103 | -0.90188 | -1.3812 | -1.629 | -1.6023 | 10.3071 | 10.2161 | 9.8669 | 9.4073 | 8.8603 | 8.4035 | 7.7008 | 6.9983 | 6.2834 | 5.4019 | 4.5981 | 4.1188 | 3.871 | 3.8977 | 4.4417 | 4.1171 | 4.2662 | 3.9748 | 3.7875 | 3.5416 | 3.1491 | 2.8386 | 2.5559 | 2.0432 | 0.62214 | -0.31718 | -0.64737 | -0.61631 | 9.9417 | 9.6171 | 9.7662 | 9.4748 | 9.2875 | 9.0416 | 8.6491 | 8.3386 | 8.0559 | 7.5432 | 6.1221 | 5.1828 | 4.8526 | 4.8837 | 4.5141 | 4.2106 | 4.2088 | 3.8398 | 3.7798 | 3.3155 | 2.8037 | 2.3849 | 2.0368 | 1.4811 | -1.1258 | -7.0372 | -11.8005 | -14.9918 | 10.0141 | 9.7106 | 9.7088 | 9.3398 | 9.2798 | 8.8155 | 8.3037 | 7.8849 | 7.5368 | 6.9811 | 4.3742 | -1.5372 | -6.3005 | -9.4918 | 4.5357 | 4.2314 | 4.3334 | 4.0532 | 4.0409 | 3.6724 | 3.2386 | 2.9018 | 2.4803 | 0.90754 | -5.768 | -11.0961 | -14.3056 | -13.4333 | 10.0357 | 9.7314 | 9.7314 | 9.5532 | 9.5409 | 9.1724 | 8.7386 | 8.4018 | 7.9803 | 6.4075 | -0.26801 | -5.5961 | -8.8056 | -7.9333 | 300011 | 527810 | STAINBURN & SIDDICK | HARKER
| Ansdell | 6.4691 | 6.137 | 5.8052 | 5.4616 | 5.1057 | 4.7257 | 4.2881 | 3.86 | 3.4293 | 2.9377 | 1.315 | 0.62811 | 0.62583 | 0.88337 | 9.4691 | 9.137 | 8.8052 | 8.4616 | 8.1057 | 7.7257 | 7.2881 | 6.86 | 6.4293 | 5.9377 | 4.315 | 3.6281 | 3.6258 | 3.8834 | 6.5738 | 6.3398 | 6.0112 | 5.717 | 5.4336 | 5.1215 | 4.7504 | 4.3865 | 4.0141 | 3.6328 | 2.4289 | 1.6244 | 1.2031 | 0.95612 | 9.5738 | 9.3398 | 9.0112 | 8.717 | 8.4336 | 8.1215 | 7.7504 | 7.3865 | 7.0141 | 6.6328 | 5.4289 | 4.6244 | 4.2031 | 3.9561 | 6.4735 | 6.1632 | 5.8535 | 5.5222 | 5.1823 | 4.818 | 4.3958 | 3.962 | 3.5261 | 3.0591 | 1.5809 | 0.9749 | 0.9858 | 1.2213 | 9.4735 | 9.1632 | 8.8535 | 8.5222 | 8.1823 | 7.818 | 7.3958 | 6.962 | 6.5261 | 6.0591 | 4.5809 | 3.9749 | 3.9858 | 4.2213 | 6.4813 | 6.1634 | 5.8559 | 5.5388 | 5.2308 | 4.9001 | 4.5093 | 4.1398 | 3.8109 | 3.4808 | 1.7818 | -0.99298 | -2.9178 | -4.1789 | 9.4813 | 9.1634 | 8.8559 | 8.5388 | 8.2308 | 7.9001 | 7.5093 | 7.1398 | 6.8109 | 6.4808 | 4.7818 | 2.007 | 0.082229 | -1.1789 | 6.4385 | 6.0518 | 5.7285 | 5.4262 | 5.1374 | 4.8498 | 4.505 | 4.1973 | 3.867 | 3.1108 | -0.27896 | -2.7095 | -3.9092 | -3.3155 | 9.4385 | 9.0518 | 9.0518 | 8.4262 | 8.1374 | 7.8498 | 7.505 | 7.1973 | 6.867 | 6.1108 | 2.721 | 0.29054 | -0.90924 | -0.31547 | 334416 | 428229 | LYTHAM | PENWORTHAM
| Ardwick | 1.9304 | 1.39 | -0.72 | -2.9356 | -4.9824 | -7.2807 | -9.531 | 1.2492 | 0.026243 | -1.3364 | -2.4146 | -3.162 | -3.5794 | -3.7238 | 6.9304 | 6.39 | 4.28 | 2.0644 | 0.017597 | -2.2807 | -4.531 | -5.7508 | -6.9738 | -8.3364 | -9.4146 | -10.162 | -10.5794 | -10.7238 | 2.3455 | 2.1603 | -0.047307 | -2.348 | -4.4481 | -6.7656 | -9.0564 | 1.6808 | 0.40364 | -0.98898 | -1.7432 | -2.4324 | -2.9113 | -3.2026 | 7.3455 | 7.1603 | 4.9527 | 2.652 | 0.5519 | -1.7656 | -4.0564 | -5.3192 | -6.5964 | -7.989 | -8.7432 | -9.4324 | -9.9113 | -10.2026 | 1.938 | 1.405 | -0.69623 | -2.9031 | -4.9406 | -7.2267 | -9.4666 | 1.3239 | 0.11484 | -1.2238 | -2.2056 | -2.8464 | -3.2 | -3.3033 | 6.938 | 6.405 | 4.3038 | 2.0969 | 0.059412 | -2.2267 | -4.4666 | -5.6761 | -6.8852 | -8.2238 | -9.2056 | -9.8464 | -10.2 | -10.3033 | 1.9483 | 1.425 | -0.66923 | -2.8741 | -4.9158 | -7.2192 | -9.5054 | 1.233 | -0.015623 | -1.3592 | -2.6355 | -4.7827 | -6.3409 | -7.3893 | 6.9483 | 6.425 | 4.3308 | 2.1259 | 0.084195 | -2.2192 | -4.5054 | -5.767 | -7.0156 | -8.3592 | -9.6355 | -11.7827 | -13.3409 | -14.3893 | 1.951 | 1.4229 | -0.66457 | -2.8547 | -4.9052 | -7.2015 | -9.463 | 1.3051 | 0.074379 | -1.5575 | -4.0389 | -5.9544 | -6.9937 | -6.6873 | 6.951 | 6.4229 | 6.4229 | 2.1453 | 0.094788 | -2.2015 | -4.463 | -5.6949 | -6.9256 | -8.5575 | -11.0389 | -12.9544 | -13.9937 | -13.6873 | 384753 | 397415 | STUART ST | STALYBRIDGE
| Arnside | 10.8332 | 10.6069 | 10.574 | 10.4318 | 10.3882 | 10.1529 | 9.9968 | 9.8177 | 9.604 | 9.292 | 8.1903 | 7.667 | 7.5268 | 7.7617 | 13.3332 | 13.1069 | 13.074 | 12.9318 | 12.8882 | 12.6529 | 12.4968 | 12.3177 | 12.104 | 11.792 | 10.6903 | 10.167 | 10.0268 | 10.2617 | 10.9387 | 10.7984 | 10.7305 | 10.6012 | 10.5807 | 10.3643 | 10.228 | 10.1734 | 10.0003 | 9.812 | 9.2223 | 8.6723 | 8.2699 | 8.0368 | 13.4387 | 13.2984 | 13.2305 | 13.1012 | 13.0807 | 12.8643 | 12.728 | 12.6734 | 12.5003 | 12.312 | 11.7223 | 11.1723 | 10.7699 | 10.5368 | 10.8344 | 10.6149 | 10.6099 | 10.4815 | 10.4156 | 10.2162 | 10.0701 | 9.8798 | 9.6756 | 9.3914 | 8.3932 | 7.9389 | 7.8231 | 8.0477 | 13.3344 | 13.1149 | 13.1099 | 12.9815 | 12.9156 | 12.7162 | 12.5701 | 12.3798 | 12.1756 | 11.8914 | 10.8932 | 10.4389 | 10.3231 | 10.5477 | 10.8395 | 10.6039 | 10.5612 | 10.4106 | 10.3279 | 10.0512 | 9.827 | 9.6955 | 9.4803 | 9.2491 | 8.2446 | 6.9862 | 6.3298 | 5.8489 | 13.3395 | 13.1039 | 13.0612 | 12.9106 | 12.8279 | 12.5512 | 12.327 | 12.1955 | 11.9803 | 11.7491 | 10.7446 | 9.4862 | 8.8298 | 8.3489 | 10.8308 | 10.58 | 10.5334 | 10.377 | 10.274 | 10.0039 | 9.7983 | 9.6796 | 9.4961 | 9.1216 | 7.4596 | 6.4761 | 6.1075 | 6.424 | 13.3308 | 13.08 | 13.08 | 12.877 | 12.774 | 12.5039 | 12.2983 | 12.1796 | 11.9961 | 11.6216 | 9.9596 | 8.9761 | 8.6075 | 8.924 | 346495 | 478180 | KENDAL (PARKSIDE RD) | HUTTON
| Ashton (Golborne) | 4.2071 | 3.0111 | 2.5219 | 2.0226 | 1.7496 | 1.0561 | 0.36244 | -0.27356 | -1.0455 | -1.9323 | -4.9342 | -7.0125 | -8.2937 | -9.0224 | 10.0071 | 8.8111 | 8.3219 | 7.8226 | 7.5496 | 6.8561 | 6.1624 | 5.5264 | 4.7545 | 3.8677 | 0.86585 | -1.2125 | -2.4937 | -3.2224 | 4.7153 | 4.0224 | 3.552 | 3.06 | 2.8177 | 2.2059 | 1.6428 | 1.137 | 0.45701 | -0.24777 | -2.4354 | -4.1807 | -5.4064 | -6.1179 | 10.5153 | 9.8224 | 9.352 | 8.86 | 8.6177 | 8.0059 | 7.4428 | 6.937 | 6.257 | 5.5522 | 3.3646 | 1.6193 | 0.39356 | -0.31791 | 4.209 | 2.9858 | 2.5532 | 2.0676 | 1.8147 | 1.1553 | 0.46352 | -0.1501 | -0.88479 | -1.6926 | -4.3291 | -5.8214 | -6.5003 | -6.7622 | 10.009 | 8.7858 | 8.3532 | 7.8676 | 7.6147 | 6.9553 | 6.2635 | 5.6499 | 4.9152 | 4.1074 | 1.4709 | -0.02145 | -0.70028 | -0.96217 | 4.2204 | 3.0529 | 2.5837 | 2.1184 | 1.9273 | 1.3167 | 0.72326 | 0.17504 | -0.4441 | -1.1373 | -5.2137 | -13.4265 | -20.225 | -24.1099 | 10.0204 | 8.8529 | 8.3837 | 7.9184 | 7.7273 | 7.1167 | 6.5233 | 5.975 | 5.3559 | 4.6627 | 0.58632 | -7.6265 | -14.425 | -18.3099 | 4.2232 | 3.0019 | 2.5367 | 2.104 | 1.91 | 1.3134 | 0.70989 | 0.18722 | -0.61847 | -2.4639 | -10.8134 | -17.743 | -22.1294 | -21.791 | 10.0232 | 8.8019 | 8.8019 | 7.904 | 7.71 | 7.1134 | 6.5099 | 5.9872 | 5.1815 | 3.3361 | -5.0134 | -11.943 | -16.3294 | -15.991 | 357056 | 400663 | GOLBORNE | BOLD
| Ashton (Ribble) | 3.9157 | 3.4963 | 3.1512 | 2.8138 | 2.7181 | 2.3881 | 2.029 | 1.6744 | 1.3469 | 0.84355 | -0.67097 | -1.2875 | -1.3148 | -0.93417 | 3.4157 | 2.9963 | 2.6512 | 2.3138 | 2.2181 | 1.8881 | 1.529 | 1.1744 | 0.84691 | 0.34355 | -1.171 | -1.7875 | -1.8148 | -1.4342 | 4.1652 | 3.9678 | 3.6456 | 3.3421 | 3.2854 | 3.0171 | 2.7216 | 2.4296 | 2.1642 | 1.7923 | 0.86361 | 0.1632 | -0.26798 | -0.38093 | 3.6652 | 3.4678 | 3.1456 | 2.8421 | 2.7854 | 2.5171 | 2.2216 | 1.9296 | 1.6642 | 1.2923 | 0.36361 | -0.3368 | -0.76798 | -0.88093 | 3.9201 | 3.5067 | 3.1686 | 2.8383 | 2.7487 | 2.4272 | 2.0762 | 1.7291 | 1.4148 | 0.95087 | -0.43478 | -0.94901 | -0.94603 | -0.55467 | 3.4201 | 3.0067 | 2.6686 | 2.3383 | 2.2487 | 1.9272 | 1.5762 | 1.2291 | 0.91478 | 0.45087 | -0.93478 | -1.449 | -1.446 | -1.0547 | 3.9288 | 3.5214 | 3.1938 | 2.8789 | 2.8152 | 2.5214 | 2.1907 | 1.8735 | 1.6266 | 1.2694 | -0.11038 | -2.2746 | -3.8908 | -4.793 | 3.4288 | 3.0214 | 2.6938 | 2.3789 | 2.3152 | 2.0214 | 1.6907 | 1.3735 | 1.1266 | 0.76937 | -0.61038 | -2.7746 | -4.3908 | -5.293 | 3.8935 | 3.4231 | 3.0714 | 2.752 | 2.6846 | 2.4058 | 2.0991 | 1.8205 | 1.5596 | 0.86639 | -1.8237 | -3.6841 | -4.7064 | -4.1083 | 3.3935 | 2.9231 | 2.9231 | 2.252 | 2.1846 | 1.9058 | 1.5991 | 1.3205 | 1.0596 | 0.36639 | -2.3237 | -4.1841 | -5.2064 | -4.6083 | 350275 | 430526 | RIBBLE | PENWORTHAM
| Ashton On Mersey | 9.6721 | 8.9922 | 8.6073 | 8.1869 | 8.0098 | 7.7017 | 7.1805 | 6.8252 | 6.1367 | 5.6113 | 3.7486 | 2.7836 | 2.6475 | 2.855 | 13.8121 | 13.1322 | 12.7473 | 12.3269 | 12.1498 | 11.8417 | 11.3205 | 10.9652 | 10.2767 | 9.7513 | 7.8886 | 6.9236 | 6.7875 | 6.995 | 9.9335 | 9.515 | 9.1451 | 8.75 | 8.6799 | 8.3829 | 7.8907 | 7.5784 | 7.0852 | 6.7152 | 5.4433 | 4.3481 | 3.7144 | 3.2193 | 14.0735 | 13.655 | 13.2851 | 12.89 | 12.8199 | 12.5229 | 12.0307 | 11.7184 | 11.2252 | 10.8552 | 9.5833 | 8.4881 | 7.8544 | 7.3593 | 9.6797 | 9.032 | 8.6437 | 8.2352 | 8.0214 | 7.7854 | 7.2793 | 6.9365 | 6.2744 | 5.8056 | 4.1427 | 3.3113 | 3.2168 | 3.4217 | 13.8197 | 13.172 | 12.7837 | 12.3752 | 12.1614 | 11.9254 | 11.4193 | 11.0765 | 10.4144 | 9.9456 | 8.2827 | 7.4513 | 7.3568 | 7.5617 | 9.6846 | 9.0234 | 8.6592 | 8.2629 | 8.2007 | 7.8919 | 7.3547 | 7.0138 | 6.5294 | 6.201 | 3.9996 | -0.44704 | -3.7249 | -5.9939 | 13.8246 | 13.1634 | 12.7992 | 12.4029 | 12.3407 | 12.0319 | 11.4947 | 11.1538 | 10.6694 | 10.341 | 8.1396 | 3.693 | 0.41509 | -1.8539 | 9.6706 | 8.9192 | 8.578 | 8.25 | 8.1368 | 7.8772 | 7.4394 | 7.1788 | 6.6192 | 5.5606 | 0.56715 | -3.4105 | -5.4923 | -4.7435 | 13.8106 | 13.0592 | 13.0592 | 12.39 | 12.2768 | 12.0172 | 11.5794 | 11.3188 | 10.7592 | 9.7006 | 4.7072 | 0.72954 | -1.3523 | -0.60349 | 377188 | 392252 | SALE | CARRINGTON
| Ashton Under Lyne T11 & T12 | 4.9349 | 4.5057 | 4.2648 | 3.9887 | 3.7863 | 3.4061 | 2.9363 | 2.5542 | 2.1067 | 1.5536 | -0.30923 | -1.4465 | -1.9255 | -1.9705 | 9.0719 | 8.6427 | 8.4018 | 8.1257 | 7.9233 | 7.5431 | 7.0733 | 6.6912 | 6.2437 | 5.6906 | 3.8278 | 2.6905 | 2.2115 | 2.1665 | 5.2407 | 4.9133 | 4.6682 | 4.2845 | 4.0499 | 3.5201 | 3.0447 | 2.6159 | 1.9942 | 1.3945 | 0.24012 | -0.70416 | -1.212 | -1.4542 | 9.3777 | 9.0503 | 8.8052 | 8.4215 | 8.1869 | 7.6571 | 7.1817 | 6.7529 | 6.1312 | 5.5315 | 4.3771 | 3.4328 | 2.925 | 2.6828 | 4.9508 | 4.5367 | 4.2963 | 3.9936 | 3.8575 | 3.3924 | 2.9391 | 2.5719 | 2.1471 | 1.6454 | -0.04836 | -0.99538 | -1.403 | -1.4498 | 9.0878 | 8.6737 | 8.4333 | 8.1306 | 7.9945 | 7.5294 | 7.0761 | 6.7089 | 6.2841 | 5.7824 | 4.0886 | 3.1416 | 2.734 | 2.6872 | 4.9525 | 4.5241 | 4.3039 | 4.0276 | 3.8182 | 3.3973 | 2.8819 | 2.4435 | 1.9652 | 1.4238 | -1.3426 | -6.6379 | -11.1212 | -14.0646 | 9.0895 | 8.6611 | 8.4409 | 8.1646 | 7.9552 | 7.5343 | 7.0189 | 6.5805 | 6.1022 | 5.5608 | 2.7944 | -2.5009 | -6.9842 | -9.9276 | 4.975 | 4.5712 | 4.3292 | 4.0685 | 3.9214 | 3.4985 | 3.0395 | 2.676 | 2.1732 | 0.85666 | -5.2438 | -10.4361 | -13.3986 | -12.4103 | 9.112 | 8.7082 | 8.7082 | 8.2055 | 8.0584 | 7.6355 | 7.1765 | 6.813 | 6.3102 | 4.9937 | -1.1068 | -6.2991 | -9.2616 | -8.2733 | 393275 | 399319 | HARTSHEAD-HEYROD | STALYBRIDGE
| Ashton Under Lyne T13 | 6.7959 | 6.5715 | 6.5955 | 6.503 | 6.5049 | 6.3629 | 6.2789 | 6.1934 | 6.0524 | 5.9435 | 5.5254 | 5.2613 | 5.1771 | 5.2078 | 11.5459 | 11.3215 | 11.3455 | 11.253 | 11.2549 | 11.1129 | 11.0289 | 10.9434 | 10.8024 | 10.6935 | 10.2754 | 10.0113 | 9.9271 | 9.9578 | 6.9291 | 6.8158 | 6.7805 | 6.6577 | 6.6407 | 6.4958 | 6.4024 | 6.304 | 6.1461 | 6.0292 | 5.7515 | 5.5215 | 5.4148 | 5.3994 | 11.6791 | 11.5658 | 11.5305 | 11.4077 | 11.3907 | 11.2458 | 11.1524 | 11.054 | 10.8961 | 10.7792 | 10.5015 | 10.2715 | 10.1648 | 10.1494 | 6.799 | 6.5803 | 6.609 | 6.5217 | 6.5284 | 6.3923 | 6.3136 | 6.2283 | 6.0911 | 5.9975 | 5.6133 | 5.3774 | 5.3048 | 5.337 | 11.549 | 11.3303 | 11.359 | 11.2717 | 11.2784 | 11.1423 | 11.0636 | 10.9783 | 10.8411 | 10.7475 | 10.3633 | 10.1274 | 10.0548 | 10.087 | 6.8057 | 6.5896 | 6.6198 | 6.5318 | 6.5353 | 6.3926 | 6.3029 | 6.2089 | 6.0661 | 5.9675 | 5.3731 | 3.9456 | 2.8098 | 2.0935 | 11.5557 | 11.3396 | 11.3698 | 11.2818 | 11.2853 | 11.1426 | 11.0529 | 10.9589 | 10.8161 | 10.7175 | 10.1231 | 8.6956 | 7.5598 | 6.8435 | 6.8112 | 6.5935 | 6.626 | 6.548 | 6.5632 | 6.4378 | 6.3644 | 6.2856 | 6.1332 | 5.8244 | 4.2949 | 2.9693 | 2.2488 | 2.5896 | 11.5612 | 11.3435 | 11.3435 | 11.298 | 11.3132 | 11.1878 | 11.1144 | 11.0356 | 10.8832 | 10.5744 | 9.0449 | 7.7193 | 6.9988 | 7.3396 | 393285 | 399329 | HARTSHEAD-HEYROD | STALYBRIDGE
| Ashwood Dale | 4.5857 | 4.2387 | 4.3101 | 4.0443 | 3.9698 | 3.6231 | 3.3246 | 3.096 | 2.7199 | 2.3385 | 1.0231 | 0.061953 | -0.40694 | -0.5147 | 11.8667 | 11.5197 | 11.5911 | 11.3253 | 11.2508 | 10.9041 | 10.6056 | 10.377 | 10.0009 | 9.6195 | 8.3041 | 7.343 | 6.8741 | 6.7663 | 4.6087 | 4.2625 | 4.2154 | 3.8933 | 3.7693 | 3.3638 | 2.9917 | 2.6811 | 2.2035 | 1.7711 | 0.81624 | -0.094112 | -0.70679 | -1.1637 | 11.8897 | 11.5435 | 11.4964 | 11.1743 | 11.0503 | 10.6448 | 10.2727 | 9.9621 | 9.4845 | 9.0521 | 8.0972 | 7.1869 | 6.5742 | 6.1173 | 4.6011 | 4.2875 | 4.3862 | 4.1434 | 4.0896 | 3.7681 | 3.4929 | 3.2857 | 2.94 | 2.6036 | 1.4191 | 0.57049 | 0.15285 | 0.076025 | 11.8821 | 11.5685 | 11.6672 | 11.4244 | 11.3706 | 11.0491 | 10.7739 | 10.5667 | 10.221 | 9.8846 | 8.7001 | 7.8515 | 7.4339 | 7.357 | 4.5897 | 4.2453 | 4.3193 | 4.042 | 3.957 | 3.5849 | 3.2252 | 2.9281 | 2.5336 | 2.1921 | 0.10882 | -4.9477 | -8.8169 | -11.506 | 11.8707 | 11.5263 | 11.6003 | 11.323 | 11.238 | 10.8659 | 10.5062 | 10.2091 | 9.8146 | 9.4731 | 7.3898 | 2.3333 | -1.5359 | -4.225 | 4.6433 | 4.3468 | 4.4658 | 4.2513 | 4.2098 | 3.901 | 3.6182 | 3.4 | 2.9799 | 1.817 | -3.6152 | -8.2633 | -10.9004 | -10.2174 | 11.9243 | 11.6278 | 11.6278 | 11.5323 | 11.4908 | 11.182 | 10.8992 | 10.681 | 10.2609 | 9.098 | 3.6658 | -0.98234 | -3.6194 | -2.9364 | 406537 | 373050 | BUXTON | STALYBRIDGE
| Askam & Dalton | 1.4908 | 1.0349 | 0.88989 | 0.41687 | 0.17504 | -0.35956 | -0.94958 | -1.3852 | -1.938 | -2.8373 | -5.7389 | -7.2319 | -7.6544 | -6.9253 | 8.4708 | 8.0149 | 7.8699 | 7.3969 | 7.155 | 6.6204 | 6.0304 | 5.5948 | 5.042 | 4.1427 | 1.2411 | -0.25193 | -0.67445 | 0.054664 | 1.6471 | 1.3572 | 1.1251 | 0.75965 | 0.61852 | 0.18485 | -0.30807 | -0.65697 | -1.1471 | -1.7305 | -3.0746 | -4.4552 | -5.4693 | -5.9915 | 8.6271 | 8.3372 | 8.1051 | 7.7396 | 7.5985 | 7.1648 | 6.6719 | 6.323 | 5.8329 | 5.2495 | 3.9054 | 2.5248 | 1.5107 | 0.98848 | 1.5005 | 1.0826 | 0.94483 | 0.50548 | 0.29156 | -0.21152 | -0.76987 | -1.1778 | -1.6955 | -2.5014 | -5.0981 | -6.4196 | -6.7774 | -6.0138 | 8.4805 | 8.0626 | 7.9248 | 7.4855 | 7.2716 | 6.7685 | 6.2101 | 5.8022 | 5.2845 | 4.4786 | 1.8819 | 0.56038 | 0.20255 | 0.96619 | 1.4922 | 0.9853 | 0.78603 | 0.27906 | -0.043148 | -0.70117 | -1.4811 | -2.1147 | -2.7537 | -3.4988 | -6.8884 | -13.1862 | -17.3285 | -20.1575 | 8.4722 | 7.9653 | 7.766 | 7.2591 | 6.9369 | 6.2788 | 5.4989 | 4.8653 | 4.2263 | 3.4812 | 0.091594 | -6.2062 | -10.3485 | -13.1775 | 1.5406 | 1.0352 | 0.85837 | 0.38826 | 0.080664 | -0.57421 | -1.2289 | -1.7027 | -2.2749 | -3.9691 | -11.3776 | -16.6647 | -19.229 | -17.7784 | 8.5206 | 8.0152 | 8.0152 | 7.3683 | 7.0607 | 6.4058 | 5.7511 | 5.2773 | 4.7051 | 3.0109 | -4.3976 | -9.6847 | -12.249 | -10.7984 | 321558 | 477806 | ULVERSTON | HARKER
| Askerton Castle | 0.91989 | 0.87131 | 0.87197 | 0.82543 | 0.81634 | 0.77739 | 0.7353 | 0.68794 | 0.6356 | 0.58732 | 0.40678 | 0.35636 | 0.34046 | 0.32617 | 1.6199 | 1.5713 | 1.572 | 1.5254 | 1.5163 | 1.4774 | 1.4353 | 1.3879 | 1.3356 | 1.2873 | 1.1068 | 1.0564 | 1.0405 | 1.0262 | 0.9678 | 0.95847 | 0.93032 | 0.88882 | 0.85739 | 0.81526 | 0.76847 | 0.73102 | 0.67415 | 0.60732 | 0.50935 | 0.47249 | 0.47041 | 0.50375 | 1.6678 | 1.6585 | 1.6303 | 1.5888 | 1.5574 | 1.5153 | 1.4685 | 1.431 | 1.3742 | 1.3073 | 1.2093 | 1.1725 | 1.1704 | 1.2038 | 0.92051 | 0.87268 | 0.89161 | 0.82863 | 0.82175 | 0.78715 | 0.76252 | 0.71864 | 0.66938 | 0.62693 | 0.46167 | 0.42043 | 0.40344 | 0.37856 | 1.6205 | 1.5727 | 1.5916 | 1.5286 | 1.5218 | 1.4871 | 1.4625 | 1.4186 | 1.3694 | 1.3269 | 1.1617 | 1.1204 | 1.1034 | 1.0786 | 0.92342 | 0.87753 | 0.88065 | 0.83054 | 0.81851 | 0.77535 | 0.74341 | 0.6908 | 0.64168 | 0.60677 | 0.37523 | 0.1764 | 0.096885 | 0.070644 | 1.6234 | 1.5775 | 1.5806 | 1.5305 | 1.5185 | 1.4754 | 1.4434 | 1.3908 | 1.3417 | 1.3068 | 1.0752 | 0.8764 | 0.79689 | 0.77064 | 0.9214 | 0.87166 | 0.87009 | 0.82195 | 0.80962 | 0.76761 | 0.73645 | 0.68697 | 0.64295 | 0.61447 | 0.41315 | 0.29441 | 0.29196 | 0.34403 | 1.6214 | 1.5717 | 1.5717 | 1.5219 | 1.5096 | 1.4676 | 1.4365 | 1.387 | 1.3429 | 1.3145 | 1.1132 | 0.99441 | 0.99196 | 1.044 | 354779 | 568913 | - | HARKER
| Aspatria | 3.7575 | 3.237 | 2.8923 | 2.6077 | 2.5567 | 2.2295 | 1.902 | 1.8098 | 1.4098 | 0.96857 | -0.76973 | -1.8872 | -2.5576 | -2.3614 | 5.7575 | 5.237 | 4.8923 | 4.6077 | 4.5567 | 4.2295 | 3.902 | 3.8098 | 3.4098 | 2.9686 | 1.2303 | 0.1128 | -0.55762 | -0.36135 | 3.9522 | 3.6213 | 3.2992 | 3.0528 | 3.0173 | 2.7107 | 2.3972 | 2.3023 | 1.9312 | 1.6675 | 0.81832 | -0.38587 | -1.5307 | -2.208 | 5.9522 | 5.6213 | 5.2992 | 5.0528 | 5.0173 | 4.7107 | 4.3972 | 4.3023 | 3.9312 | 3.6675 | 2.8183 | 1.6141 | 0.46929 | -0.208 | 3.7627 | 3.2611 | 2.9369 | 2.6722 | 2.6334 | 2.3218 | 2.0088 | 1.9252 | 1.5508 | 1.163 | -0.35497 | -1.2687 | -1.7992 | -1.5871 | 5.7627 | 5.2611 | 4.9369 | 4.6722 | 4.6334 | 4.3218 | 4.0088 | 3.9252 | 3.5508 | 3.163 | 1.645 | 0.73132 | 0.20085 | 0.41285 | 3.76 | 3.2139 | 2.8424 | 2.5274 | 2.4164 | 2.0015 | 1.5461 | 1.3399 | 0.88056 | 0.54877 | -1.1469 | -3.3286 | -4.6287 | -5.3489 | 5.76 | 5.2139 | 4.8424 | 4.5274 | 4.4164 | 4.0015 | 3.5461 | 3.3399 | 2.8806 | 2.5488 | 0.85313 | -1.3286 | -2.6287 | -3.3489 | 3.7771 | 3.229 | 2.8605 | 2.5533 | 2.4148 | 2.0031 | 1.5883 | 1.4329 | 1.006 | 0.41954 | -2.3529 | -4.1919 | -5.0248 | -4.5492 | 5.7771 | 5.229 | 5.229 | 4.5533 | 4.4148 | 4.0031 | 3.5883 | 3.4329 | 3.006 | 2.4195 | -0.35287 | -2.1919 | -3.0248 | -2.5492 | 314417 | 542840 | STAINBURN & SIDDICK | HARKER
| Atherton Town Centre | 8.602 | 7.5956 | 7.4509 | 5.8912 | 5.2103 | 2.8026 | 0.56413 | -1.0351 | -2.9292 | -4.7431 | -8.3283 | -10.1908 | -10.6856 | -10.42 | 20.362 | 19.3556 | 19.2109 | 17.6512 | 16.9703 | 14.5626 | 12.3241 | 10.7249 | 8.8308 | 7.0169 | 3.4317 | 1.5692 | 1.0744 | 1.34 | 8.8757 | 8.0953 | 7.8101 | 6.6997 | 6.4923 | 5.2417 | 4.1385 | 3.2942 | 2.0396 | 0.84637 | -1.581 | -3.3734 | -4.578 | -5.0843 | 20.6357 | 19.8553 | 19.5701 | 18.4597 | 18.2523 | 17.0017 | 15.8985 | 15.0542 | 13.7996 | 12.6064 | 10.179 | 8.3866 | 7.182 | 6.6757 | 8.6271 | 7.6601 | 7.5442 | 6.019 | 5.3649 | 2.9981 | 0.79572 | -0.81797 | -2.6117 | -4.3186 | -7.542 | -8.9932 | -9.301 | -8.747 | 20.3871 | 19.4201 | 19.3042 | 17.779 | 17.1249 | 14.7581 | 12.5557 | 10.942 | 9.1483 | 7.4414 | 4.218 | 2.7668 | 2.459 | 3.013 | 8.6231 | 7.6393 | 7.5258 | 6.004 | 5.3982 | 3.0725 | 0.89197 | -0.57192 | -2.3565 | -3.8652 | -8.65 | -19.0254 | -27.3589 | -32.5296 | 20.3831 | 19.3993 | 19.2858 | 17.764 | 17.1582 | 14.8325 | 12.652 | 11.1881 | 9.4035 | 7.8948 | 3.11 | -7.2654 | -15.5989 | -20.7696 | 8.6205 | 7.5666 | 7.4399 | 5.9677 | 5.4228 | 3.1972 | 1.1087 | -0.29758 | -2.2167 | -5.5068 | -17.146 | -26.3992 | -31.8816 | -29.9589 | 20.3805 | 19.3266 | 19.3266 | 17.7277 | 17.1828 | 14.9572 | 12.8687 | 11.4624 | 9.5433 | 6.2532 | -5.386 | -14.6392 | -20.1216 | -18.1989 | 367546 | 403338 | ATHERTON | KEARSLEY
| Athletic St | 6.8933 | 5.9943 | 5.5509 | 5.3235 | 4.9484 | 4.6449 | 4.131 | 3.7016 | 3.3893 | 2.8786 | 1.1842 | 0.38775 | 0.28213 | 0.57086 | 10.3933 | 9.4943 | 9.0509 | 8.8235 | 8.4484 | 8.1449 | 7.631 | 7.2016 | 6.8893 | 6.3786 | 4.6842 | 3.8877 | 3.7821 | 4.0709 | 7.2862 | 6.8965 | 6.4432 | 6.246 | 5.9287 | 5.6762 | 5.2284 | 4.8571 | 4.5863 | 4.199 | 3.0882 | 2.2904 | 1.8209 | 1.5547 | 10.7862 | 10.3965 | 9.9432 | 9.746 | 9.4287 | 9.1762 | 8.7284 | 8.3571 | 8.0863 | 7.699 | 6.5882 | 5.7904 | 5.3209 | 5.0547 | 6.9045 | 6.0002 | 5.5944 | 5.3802 | 5.0228 | 4.7355 | 4.2402 | 3.8272 | 3.536 | 3.0776 | 1.5632 | 0.91112 | 0.85882 | 1.158 | 10.4045 | 9.5002 | 9.0944 | 8.8802 | 8.5228 | 8.2355 | 7.7402 | 7.3272 | 7.036 | 6.5776 | 5.0632 | 4.4111 | 4.3588 | 4.658 | 6.8995 | 6.008 | 5.5632 | 5.3437 | 4.9875 | 4.6972 | 4.1799 | 3.7492 | 3.494 | 3.1145 | 1.0484 | -3.0434 | -5.9979 | -7.8887 | 10.3995 | 9.508 | 9.0632 | 8.8437 | 8.4875 | 8.1972 | 7.6799 | 7.2492 | 6.994 | 6.6145 | 4.5484 | 0.45663 | -2.4979 | -4.3887 | 6.9053 | 5.9964 | 5.5363 | 5.339 | 5.0027 | 4.7569 | 4.294 | 3.9331 | 3.6337 | 2.5668 | -2.1896 | -5.7443 | -7.5835 | -6.7013 | 10.4053 | 9.4964 | 9.4964 | 8.839 | 8.5027 | 8.2569 | 7.794 | 7.4331 | 7.1337 | 6.0668 | 1.3104 | -2.2443 | -4.0835 | -3.2013 | 385381 | 432208 | BURNLEY | ROCHDALE
| Avenham | 6.9317 | 6.7549 | 6.6388 | 6.4009 | 6.3176 | 6.2121 | 5.9451 | 11.1589 | 11.0337 | 10.7333 | 10.1024 | 9.8666 | 9.7018 | 9.8802 | 10.4317 | 10.2549 | 10.1388 | 9.9009 | 9.8176 | 9.7121 | 9.4451 | 9.2589 | 9.1337 | 8.8333 | 8.2024 | 7.9666 | 7.8018 | 7.9802 | 7.1401 | 7.1239 | 6.8762 | 6.542 | 6.3764 | 6.158 | 5.7181 | 10.7579 | 10.3495 | 9.9478 | 9.4689 | 9.3118 | 9.1187 | 9.2157 | 10.6401 | 10.6239 | 10.3762 | 10.042 | 9.8764 | 9.658 | 9.2181 | 8.8579 | 8.4495 | 8.0478 | 7.5689 | 7.4118 | 7.2187 | 7.3157 | 6.9377 | 6.779 | 6.692 | 6.4731 | 6.3997 | 6.3057 | 6.0612 | 11.29 | 11.1807 | 10.9129 | 10.3374 | 10.1377 | 9.9926 | 10.1694 | 10.4377 | 10.279 | 10.192 | 9.9731 | 9.8997 | 9.8057 | 9.5612 | 9.39 | 9.2807 | 9.0129 | 8.4374 | 8.2377 | 8.0926 | 8.2694 | 6.9447 | 6.7805 | 6.6771 | 6.4478 | 6.366 | 6.2597 | 5.9844 | 11.188 | 11.0619 | 10.7766 | 9.9891 | 8.584 | 7.4316 | 6.896 | 10.4447 | 10.2805 | 10.1771 | 9.9478 | 9.866 | 9.7597 | 9.4844 | 9.288 | 9.1619 | 8.8766 | 8.0891 | 6.684 | 5.5316 | 4.996 | 6.9552 | 6.7918 | 6.702 | 6.4974 | 6.4407 | 6.3686 | 6.1332 | 11.3835 | 11.2967 | 10.7814 | 8.9656 | 7.7225 | 6.9527 | 7.5264 | 10.4552 | 10.2918 | 10.2918 | 9.9974 | 9.9407 | 9.8686 | 9.6332 | 9.4835 | 9.3967 | 8.8814 | 7.0656 | 5.8225 | 5.0527 | 5.6264 | 354028 | 429192 | PRESTON EAST | PENWORTHAM
| Baguley | 1.9051 | 1.1419 | 0.9363 | 0.84567 | 0.56492 | -0.16977 | -0.766 | 3.7286 | 2.6693 | 1.9706 | -0.83435 | -2.7612 | -3.4552 | -3.8674 | 6.5421 | 5.7789 | 5.5733 | 5.4827 | 5.2019 | 4.4672 | 3.871 | 3.3656 | 2.3063 | 1.6076 | -1.1973 | -3.1242 | -3.8182 | -4.2304 | 2.0971 | 1.4957 | 1.1689 | 1.0731 | 0.82969 | 0.15092 | -0.39769 | 4.2435 | 3.2877 | 2.6814 | 0.64108 | -1.1261 | -2.1368 | -3.0332 | 6.7341 | 6.1327 | 5.8059 | 5.7101 | 5.4667 | 4.7879 | 4.2393 | 3.8805 | 2.9247 | 2.3184 | 0.27808 | -1.4891 | -2.4998 | -3.3962 | 1.9309 | 1.2012 | 1.0249 | 0.94926 | 0.69145 | -0.01498 | -0.58562 | 3.8758 | 2.8549 | 2.224 | -0.2821 | -1.8262 | -2.3255 | -2.5132 | 6.5679 | 5.8382 | 5.6619 | 5.5863 | 5.3285 | 4.622 | 4.0514 | 3.5128 | 2.4919 | 1.861 | -0.6451 | -2.1892 | -2.6885 | -2.8762 | 1.9134 | 1.1638 | 0.97247 | 0.88106 | 0.62514 | -0.093301 | -0.70901 | 3.8514 | 2.8772 | 2.3137 | -1.2125 | -7.9839 | -12.8808 | -16.6097 | 6.5504 | 5.8008 | 5.6095 | 5.5181 | 5.2621 | 4.5437 | 3.928 | 3.4884 | 2.5142 | 1.9507 | -1.5755 | -8.3469 | -13.2438 | -16.9727 | 1.9418 | 1.1726 | 0.97977 | 0.92895 | 0.72003 | 0.069863 | -0.48672 | 4.069 | 3.0703 | 1.5796 | -5.7464 | -11.8564 | -15.1915 | -14.784 | 6.5788 | 5.8096 | 5.8096 | 5.5659 | 5.357 | 4.7069 | 4.1503 | 3.706 | 2.7073 | 1.2166 | -6.1094 | -12.2194 | -15.5545 | -15.147 | 380562 | 389035 | SALE | CARRINGTON
| Bamber Bridge | 8.2858 | 8.0144 | 7.7676 | 7.3786 | 7.3684 | 6.9709 | 6.5707 | 6.1998 | 5.9031 | 5.3162 | 3.5177 | 2.2644 | 1.3607 | 0.91647 | 12.4228 | 12.1514 | 11.9046 | 11.5156 | 11.5054 | 11.1079 | 10.7077 | 10.3368 | 10.0401 | 9.4532 | 7.6547 | 6.4014 | 5.4977 | 5.0535 | 8.5047 | 8.3811 | 8.0738 | 7.6484 | 7.6164 | 7.2304 | 6.8299 | 6.4432 | 6.109 | 5.5697 | 4.2163 | 3.2442 | 2.2737 | 1.7619 | 12.6417 | 12.5181 | 12.2108 | 11.7854 | 11.7534 | 11.3674 | 10.9669 | 10.5802 | 10.246 | 9.7067 | 8.3533 | 7.3812 | 6.4107 | 5.8989 | 8.2933 | 8.0326 | 7.7983 | 7.4222 | 7.4213 | 7.038 | 6.6517 | 6.2941 | 6.0151 | 5.473 | 3.886 | 3.0043 | 2.2961 | 2.1219 | 12.4303 | 12.1696 | 11.9353 | 11.5592 | 11.5583 | 11.175 | 10.7887 | 10.4311 | 10.1521 | 9.61 | 8.023 | 7.1413 | 6.4331 | 6.2589 | 8.2959 | 8.0348 | 7.7993 | 7.4161 | 7.4241 | 7.0313 | 6.6138 | 6.2163 | 5.9198 | 5.3834 | 2.5131 | -2.8934 | -7.4659 | -10.375 | 12.4329 | 12.1718 | 11.9363 | 11.5531 | 11.5611 | 11.1683 | 10.7508 | 10.3533 | 10.0568 | 9.5204 | 6.6501 | 1.2436 | -3.3289 | -6.238 | 8.3155 | 8.0542 | 7.8351 | 7.4889 | 7.5285 | 7.1691 | 6.7716 | 6.389 | 5.9555 | 4.5628 | -1.539 | -6.463 | -9.6242 | -9.2571 | 12.4525 | 12.1912 | 12.1912 | 11.6259 | 11.6655 | 11.3061 | 10.9086 | 10.526 | 10.0925 | 8.6998 | 2.598 | -2.326 | -5.4872 | -5.1201 | 356431 | 426698 | RIBBLE | PENWORTHAM
| Barbara St | 3.6594 | 3.426 | 3.3698 | 3.0809 | 2.9482 | 2.6384 | 2.2959 | 1.9461 | 1.5825 | 1.1526 | -0.41476 | -1.3235 | -1.7714 | -1.7962 | 10.5594 | 10.326 | 10.2698 | 9.9809 | 9.8482 | 9.5384 | 9.1959 | 8.8461 | 8.4825 | 8.0526 | 6.4852 | 5.5765 | 5.1286 | 5.1038 | 3.6987 | 3.49 | 3.3652 | 3.0736 | 2.9548 | 2.6574 | 2.3225 | 1.9778 | 1.617 | 1.2576 | 0.26121 | -0.48953 | -1.0895 | -1.4271 | 10.5987 | 10.39 | 10.2652 | 9.9736 | 9.8548 | 9.5574 | 9.2225 | 8.8778 | 8.517 | 8.1576 | 7.1612 | 6.4105 | 5.8105 | 5.4729 | 3.6719 | 3.4513 | 3.44 | 3.1663 | 3.0477 | 2.7198 | 2.4293 | 2.0875 | 1.7326 | 1.3473 | -0.045488 | -0.76471 | -1.1293 | -1.0695 | 10.5719 | 10.3513 | 10.34 | 10.0663 | 9.9477 | 9.6198 | 9.3293 | 8.9875 | 8.6326 | 8.2473 | 6.8545 | 6.1353 | 5.7707 | 5.8305 | 3.654 | 3.4115 | 3.3556 | 3.0602 | 2.9277 | 2.5554 | 2.2366 | 1.8436 | 1.5124 | 1.1213 | -1.2717 | -6.7943 | -11.2661 | -14.112 | 10.554 | 10.3115 | 10.2556 | 9.9602 | 9.8277 | 9.4554 | 9.1366 | 8.7436 | 8.4124 | 8.0213 | 5.6283 | 0.10572 | -4.3661 | -7.212 | 3.6944 | 3.4713 | 3.4122 | 3.1585 | 3.0652 | 2.7701 | 2.4836 | 2.1536 | 1.7316 | 0.39906 | -5.7028 | -10.6604 | -13.6583 | -12.8754 | 10.5944 | 10.3713 | 10.3713 | 10.0585 | 9.9652 | 9.6701 | 9.3836 | 9.0536 | 8.6316 | 7.2991 | 1.1972 | -3.7604 | -6.7583 | -5.9754 | 370695 | 407609 | BOLTON | KEARSLEY
| Barrow | 10.6076 | 10.5285 | 10.3749 | 10.0914 | 9.8803 | 9.5488 | 9.0939 | 8.6696 | 8.2646 | 7.7106 | 5.9348 | 5.0875 | 5.0017 | 5.407 | 8.6076 | 8.5285 | 8.3749 | 8.0914 | 7.8803 | 7.5488 | 7.0939 | 6.6696 | 6.2646 | 5.7106 | 3.9348 | 3.0875 | 3.0017 | 3.407 | 10.664 | 10.6376 | 10.4195 | 10.1582 | 10.0249 | 9.7707 | 9.3972 | 9.0564 | 8.7302 | 8.3317 | 7.2763 | 6.6073 | 6.2659 | 6.1977 | 8.664 | 8.6376 | 8.4195 | 8.1582 | 8.0249 | 7.7707 | 7.3972 | 7.0564 | 6.7302 | 6.3317 | 5.2763 | 4.6073 | 4.2659 | 4.1977 | 10.6145 | 10.536 | 10.4003 | 10.1279 | 9.9369 | 9.6195 | 9.1791 | 8.7677 | 8.3841 | 7.8871 | 6.2986 | 5.6021 | 5.5823 | 5.9897 | 8.6145 | 8.536 | 8.4003 | 8.1279 | 7.9369 | 7.6195 | 7.1791 | 6.7677 | 6.3841 | 5.8871 | 4.2986 | 3.6021 | 3.5823 | 3.9897 | 10.6117 | 10.5422 | 10.3844 | 10.1107 | 9.9711 | 9.6836 | 9.2614 | 8.8795 | 8.5847 | 8.2212 | 5.6034 | 0.31923 | -3.8622 | -6.3052 | 8.6117 | 8.5422 | 8.3844 | 8.1107 | 7.9711 | 7.6836 | 7.2614 | 6.8795 | 6.5847 | 6.2212 | 3.6034 | -1.6808 | -5.8622 | -8.3052 | 10.6484 | 10.5593 | 10.4357 | 10.2087 | 10.0473 | 9.8242 | 9.4742 | 9.1797 | 8.7571 | 7.3569 | 1.0701 | -3.7449 | -6.2952 | -4.8613 | 8.6484 | 8.5593 | 8.5593 | 8.2087 | 8.0473 | 7.8242 | 7.4742 | 7.1797 | 6.7571 | 5.3569 | -0.92992 | -5.7449 | -8.2952 | -6.8613 | 319709 | 470489 | BARROW & SANDGATE | HARKER
| Barton Dock Rd | 1.6774 | 1.333 | 1.3071 | 1.4381 | 1.3716 | 1.1332 | 1.023 | 0.94041 | 0.59265 | 0.43679 | -2.3237 | -3.7572 | -4.9428 | -5.9159 | 7.9774 | 7.633 | 7.6071 | 7.7381 | 7.6716 | 7.4332 | 7.323 | 7.2404 | 6.8927 | 6.7368 | 3.9763 | 2.5428 | 1.3572 | 0.3841 | 1.9716 | 1.8735 | 1.74 | 1.7917 | 1.6997 | 1.4307 | 1.2977 | 1.232 | 0.81898 | 0.69037 | 0.029925 | -0.77934 | -1.799 | -2.409 | 8.2716 | 8.1735 | 8.04 | 8.0917 | 7.9997 | 7.7307 | 7.5977 | 7.532 | 7.119 | 6.9904 | 6.3299 | 5.5207 | 4.501 | 3.891 | 1.6817 | 1.3346 | 1.3212 | 1.4432 | 1.3516 | 1.1351 | 1.0171 | 0.93632 | 0.59434 | 0.45007 | -2.1363 | -3.0472 | -3.9659 | -4.4477 | 7.9817 | 7.6346 | 7.6212 | 7.7432 | 7.6516 | 7.4351 | 7.3171 | 7.2363 | 6.8943 | 6.7501 | 4.1637 | 3.2528 | 2.3341 | 1.8523 | 1.6967 | 1.3724 | 1.3645 | 1.5098 | 1.4563 | 1.2121 | 1.0619 | 0.92705 | 0.51366 | 0.28659 | -3.6355 | -7.4299 | -9.837 | -10.7939 | 7.9967 | 7.6724 | 7.6645 | 7.8098 | 7.7563 | 7.5121 | 7.3619 | 7.2271 | 6.8137 | 6.5866 | 2.6645 | -1.1299 | -3.537 | -4.4939 | 1.6879 | 1.3457 | 1.3265 | 1.4579 | 1.3769 | 1.1056 | 0.89397 | 0.45268 | -1.1191 | -2.7033 | -6.3402 | -9.0617 | -10.7468 | -10.3962 | 7.9879 | 7.6457 | 7.6457 | 7.7579 | 7.6769 | 7.4056 | 7.194 | 6.7527 | 5.1809 | 3.5967 | -0.040208 | -2.7617 | -4.4468 | -4.0962 | 378864 | 395534 | BARTON | CARRINGTON
| Bedford | 5.2864 | 4.7932 | 4.5593 | 4.3112 | 3.7893 | 3.2581 | 2.8392 | 2.35 | 1.7536 | 1.1859 | -1.6733 | -3.4103 | -4.2142 | -4.2907 | 9.7864 | 9.2932 | 9.0593 | 8.8112 | 8.2893 | 7.7581 | 7.3392 | 6.85 | 6.2536 | 5.6859 | 2.8267 | 1.0897 | 0.28578 | 0.20935 | 5.576 | 5.2949 | 4.8652 | 4.4937 | 3.8886 | 3.2981 | 2.7977 | 2.2015 | 1.3485 | 0.025381 | -1.2871 | -2.0793 | -2.7077 | -2.8243 | 10.076 | 9.7949 | 9.3652 | 8.9937 | 8.3886 | 7.7981 | 7.2977 | 6.7015 | 5.8485 | 4.5254 | 3.2129 | 2.4207 | 1.7923 | 1.6757 | 5.305 | 4.8337 | 4.6222 | 4.3946 | 3.9008 | 3.3983 | 3.0049 | 2.5432 | 1.985 | 1.4772 | -1.2361 | -2.5859 | -3.1887 | -3.0686 | 9.805 | 9.3337 | 9.1222 | 8.8946 | 8.4008 | 7.8983 | 7.5049 | 7.0432 | 6.485 | 5.9772 | 3.2639 | 1.9141 | 1.3113 | 1.4314 | 5.3134 | 4.848 | 4.6484 | 4.4463 | 3.9802 | 3.4996 | 3.119 | 2.6687 | 2.129 | 1.5298 | -2.0576 | -8.5807 | -13.6577 | -16.8952 | 9.8134 | 9.348 | 9.1484 | 8.9463 | 8.4802 | 7.9996 | 7.619 | 7.1687 | 6.629 | 6.0298 | 2.4424 | -4.0807 | -9.1577 | -12.3952 | 5.3269 | 4.839 | 4.6484 | 4.4853 | 4.0629 | 3.6446 | 3.319 | 2.9392 | 2.3771 | 0.77563 | -6.6799 | -12.4229 | -15.7749 | -14.7532 | 9.8269 | 9.339 | 9.339 | 8.9853 | 8.5629 | 8.1446 | 7.819 | 7.4392 | 6.8771 | 5.2756 | -2.1799 | -7.9229 | -11.2749 | -10.2532 | 366258 | 399876 | ATHERTON | KEARSLEY
| Belgrave | 7.8444 | 7.612 | 7.5942 | 7.4523 | 7.2895 | 7.0449 | 6.8076 | 6.4877 | 6.151 | 5.7836 | 4.4772 | 3.7769 | 3.551 | 3.5876 | 11.3444 | 11.112 | 11.0942 | 10.9523 | 10.7895 | 10.5449 | 10.3076 | 9.9877 | 9.651 | 9.2836 | 7.9772 | 7.2769 | 7.051 | 7.0876 | 8.0157 | 7.9205 | 7.7923 | 7.5566 | 7.4271 | 7.1805 | 6.9398 | 6.6511 | 6.3397 | 6.0314 | 5.1172 | 4.4439 | 4.0249 | 3.7304 | 11.5157 | 11.4205 | 11.2923 | 11.0566 | 10.9271 | 10.6805 | 10.4398 | 10.1511 | 9.8397 | 9.5314 | 8.6172 | 7.9439 | 7.5249 | 7.2304 | 7.8522 | 7.6264 | 7.6145 | 7.475 | 7.3201 | 7.0851 | 6.8562 | 6.5523 | 6.2193 | 5.9204 | 4.745 | 4.1382 | 3.9291 | 3.9494 | 11.3522 | 11.1264 | 11.1145 | 10.975 | 10.8201 | 10.5851 | 10.3562 | 10.0523 | 9.7193 | 9.4204 | 8.245 | 7.6382 | 7.4291 | 7.4494 | 7.8598 | 7.6456 | 7.6499 | 7.5148 | 7.374 | 7.0964 | 6.7976 | 6.456 | 6.1496 | 5.8581 | 4.0022 | -0.064169 | -3.2795 | -5.5502 | 11.3598 | 11.1456 | 11.1499 | 11.0148 | 10.874 | 10.5964 | 10.2976 | 9.956 | 9.6496 | 9.3581 | 7.5022 | 3.4358 | 0.22051 | -2.0502 | 7.8692 | 7.6512 | 7.6638 | 7.5766 | 7.4783 | 7.2542 | 7.0089 | 6.7315 | 6.377 | 5.4109 | 0.87436 | -2.7672 | -4.9028 | -4.3885 | 11.3692 | 11.1512 | 11.1512 | 11.0766 | 10.9783 | 10.7542 | 10.5089 | 10.2315 | 9.877 | 8.9109 | 4.3744 | 0.73281 | -1.4028 | -0.88853 | 393008 | 403366 | GREENHILL | WHITEGATE
| Benchill | 7.8252 | 7.7769 | 7.7068 | 7.6498 | 7.5444 | 7.4224 | 7.2917 | 7.1558 | 7.0204 | 6.8589 | 6.231 | 5.9259 | 5.8629 | 5.9088 | 9.8252 | 9.7769 | 9.7068 | 9.6498 | 9.5444 | 9.4224 | 9.2917 | 9.1558 | 9.0204 | 8.8589 | 8.231 | 7.9259 | 7.8629 | 7.9088 | 7.8504 | 7.8215 | 7.7324 | 7.6797 | 7.5849 | 7.4758 | 7.3582 | 7.2362 | 7.1128 | 6.9826 | 6.5326 | 6.2335 | 6.0784 | 5.9702 | 9.8504 | 9.8215 | 9.7324 | 9.6797 | 9.5849 | 9.4758 | 9.3582 | 9.2362 | 9.1128 | 8.9826 | 8.5326 | 8.2335 | 8.0784 | 7.9702 | 7.8322 | 7.7875 | 7.7214 | 7.6672 | 7.5658 | 7.4481 | 7.3217 | 7.1899 | 7.0606 | 6.914 | 6.3629 | 6.098 | 6.0407 | 6.0562 | 9.8322 | 9.7875 | 9.7214 | 9.6672 | 9.5658 | 9.4481 | 9.3217 | 9.1899 | 9.0606 | 8.914 | 8.3629 | 8.098 | 8.0407 | 8.0562 | 7.8249 | 7.7757 | 7.7014 | 7.6351 | 7.5262 | 7.3972 | 7.2495 | 7.0914 | 6.9587 | 6.8157 | 6.1035 | 4.7484 | 3.7242 | 2.9091 | 9.8249 | 9.7757 | 9.7014 | 9.6351 | 9.5262 | 9.3972 | 9.2495 | 9.0914 | 8.9587 | 8.8157 | 8.1035 | 6.7484 | 5.7242 | 4.9091 | 7.8295 | 7.7759 | 7.7038 | 7.6481 | 7.5528 | 7.4432 | 7.3142 | 7.1787 | 7.0516 | 6.7092 | 5.1221 | 3.9073 | 3.2049 | 3.3328 | 9.8295 | 9.7759 | 9.7759 | 9.6481 | 9.5528 | 9.4432 | 9.3142 | 9.1787 | 9.0516 | 8.7092 | 7.1221 | 5.9073 | 5.2049 | 5.3328 | 382454 | 388020 | WEST DIDSBURY | SOUTH MANCHESTER
| Bentham | 0.74926 | 0.5464 | 0.53964 | 0.41421 | 0.36295 | 0.20749 | 0.054655 | -0.032696 | -0.18405 | -0.40276 | -1.1308 | -1.5435 | -1.7278 | -1.6174 | 5.2493 | 5.0464 | 5.0396 | 4.9142 | 4.863 | 4.7075 | 4.5547 | 4.4673 | 4.316 | 4.0972 | 3.3692 | 2.9565 | 2.7722 | 2.8826 | 0.84876 | 0.72526 | 0.67719 | 0.55166 | 0.49436 | 0.34473 | 0.18965 | 0.077892 | -0.076183 | -0.27982 | -0.66458 | -1.1025 | -1.4464 | -1.6351 | 5.3488 | 5.2253 | 5.1772 | 5.0517 | 4.9944 | 4.8447 | 4.6897 | 4.5779 | 4.4238 | 4.2202 | 3.8354 | 3.3975 | 3.0536 | 2.8649 | 0.70723 | 0.55923 | 0.5607 | 0.44462 | 0.40052 | 0.25349 | 0.10864 | 0.027533 | -0.11262 | -0.3086 | -0.95881 | -1.3168 | -1.4667 | -1.3572 | 5.2072 | 5.0592 | 5.0607 | 4.9446 | 4.9005 | 4.7535 | 4.6086 | 4.5275 | 4.3874 | 4.1914 | 3.5412 | 3.1832 | 3.0333 | 3.1428 | 0.75765 | 0.54818 | 0.53319 | 0.3997 | 0.32937 | 0.14513 | -0.051722 | -0.18313 | -0.35345 | -0.53732 | -1.2937 | -2.4528 | -3.1792 | -3.6806 | 5.2577 | 5.0482 | 5.0332 | 4.8997 | 4.8294 | 4.6451 | 4.4483 | 4.3169 | 4.1465 | 3.9627 | 3.2063 | 2.0472 | 1.3208 | 0.81941 | 0.75858 | 0.54227 | 0.531 | 0.40179 | 0.32928 | 0.15435 | -0.020366 | -0.12246 | -0.27191 | -0.60667 | -2.0496 | -3.0274 | -3.4914 | -3.2487 | 5.2586 | 5.0423 | 5.0423 | 4.9018 | 4.8293 | 4.6543 | 4.4796 | 4.3775 | 4.2281 | 3.8933 | 2.4504 | 1.4726 | 1.0086 | 1.2513 | 366887 | 470130 | KENDAL (PARKSIDE RD) | HUTTON
| Bispham | 5.262 | 5.1389 | 4.9381 | 4.5805 | 4.2574 | 3.8657 | 3.3757 | 2.8822 | 2.3797 | 1.7509 | -0.17377 | -1.0634 | -1.1379 | -0.6676 | 9.899 | 9.7759 | 9.5751 | 9.2175 | 8.8944 | 8.5027 | 8.0127 | 7.5192 | 7.0167 | 6.3879 | 4.4632 | 3.5736 | 3.4991 | 3.9694 | 5.2871 | 5.1745 | 4.8809 | 4.5294 | 4.2366 | 3.864 | 3.3828 | 2.8908 | 2.3768 | 1.8183 | 0.5717 | -0.38207 | -0.91314 | -1.1913 | 9.9241 | 9.8115 | 9.5179 | 9.1664 | 8.8736 | 8.501 | 8.0198 | 7.5278 | 7.0138 | 6.4553 | 5.2087 | 4.2549 | 3.7239 | 3.4457 | 5.2766 | 5.184 | 5.0155 | 4.6828 | 4.3844 | 4.017 | 3.5512 | 3.0808 | 2.6115 | 2.0541 | 0.34986 | -0.39464 | -0.41696 | 0.037564 | 9.9136 | 9.821 | 9.6525 | 9.3198 | 9.0214 | 8.654 | 8.1882 | 7.7178 | 7.2485 | 6.6911 | 4.9869 | 4.2424 | 4.22 | 4.6746 | 5.2683 | 5.1512 | 4.9694 | 4.6335 | 4.3378 | 3.9627 | 3.4527 | 2.9467 | 2.5117 | 2.0496 | -0.70851 | -7.1072 | -11.9505 | -15.221 | 9.9053 | 9.7882 | 9.6064 | 9.2705 | 8.9748 | 8.5997 | 8.0897 | 7.5837 | 7.1487 | 6.6866 | 3.9285 | -2.4702 | -7.3135 | -10.584 | 5.3137 | 5.199 | 5.0375 | 4.7641 | 4.5029 | 4.2012 | 3.7918 | 3.4035 | 2.9185 | 1.3475 | -5.8278 | -11.6006 | -14.7358 | -13.4515 | 9.9507 | 9.836 | 9.836 | 9.4011 | 9.1399 | 8.8382 | 8.4288 | 8.0405 | 7.5555 | 5.9845 | -1.1908 | -6.9636 | -10.0988 | -8.8145 | 331655 | 439667 | BISPHAM | PENWORTHAM
| Blackbull | 7.8761 | 6.7573 | 6.5249 | 6.205 | 5.8247 | 5.3614 | 4.897 | 4.5127 | 3.9589 | 3.3478 | 1.4439 | 0.4817 | 0.23029 | 0.38293 | 12.0131 | 10.8943 | 10.6619 | 10.342 | 9.9617 | 9.4984 | 9.034 | 8.6497 | 8.0959 | 7.4848 | 5.5809 | 4.6187 | 4.3673 | 4.5199 | 8.3816 | 7.7437 | 7.5766 | 7.2739 | 6.9498 | 6.5619 | 6.1692 | 5.8496 | 5.3527 | 4.8823 | 3.5985 | 2.7055 | 2.1016 | 1.7494 | 12.5186 | 11.8807 | 11.7136 | 11.4109 | 11.0868 | 10.6989 | 10.3062 | 9.9866 | 9.4897 | 9.0193 | 7.7355 | 6.8425 | 6.2386 | 5.8864 | 7.8798 | 6.7662 | 6.5365 | 6.2208 | 5.8469 | 5.3916 | 4.9345 | 4.5561 | 4.016 | 3.4429 | 1.6846 | 0.90387 | 0.71518 | 0.96801 | 12.0168 | 10.9032 | 10.6735 | 10.3578 | 9.9839 | 9.5286 | 9.0715 | 8.6931 | 8.153 | 7.5799 | 5.8216 | 5.0409 | 4.8522 | 5.105 | 7.8981 | 6.8078 | 6.6176 | 6.3551 | 6.0522 | 5.6734 | 5.284 | 4.9806 | 4.5559 | 4.1594 | 2.1985 | -1.8517 | -4.9841 | -6.8603 | 12.0351 | 10.9448 | 10.7546 | 10.4921 | 10.1892 | 9.8104 | 9.421 | 9.1176 | 8.6929 | 8.2964 | 6.3355 | 2.2853 | -0.84705 | -2.7233 | 7.8713 | 6.7215 | 6.5272 | 6.2896 | 6.0093 | 5.6743 | 5.329 | 5.0835 | 4.6444 | 3.758 | -0.51896 | -4.2193 | -6.2276 | -5.367 | 12.0083 | 10.8585 | 10.8585 | 10.4266 | 10.1463 | 9.8113 | 9.466 | 9.2205 | 8.7814 | 7.895 | 3.618 | -0.082303 | -2.0906 | -1.23 | 353041 | 433005 | RIBBLE | PENWORTHAM
| Blackburn | 9.3015 | 8.6796 | 8.5557 | 8.5594 | 8.2731 | 7.9898 | 7.8091 | 7.7543 | 7.4899 | 7.2694 | 6.6061 | 5.8842 | 5.6142 | 5.3448 | 13.9385 | 13.3166 | 13.1927 | 13.1964 | 12.9101 | 12.6268 | 12.4461 | 12.3913 | 12.1269 | 11.9064 | 11.2431 | 10.5212 | 10.2512 | 9.9818 | 9.8158 | 9.6245 | 9.3982 | 9.2914 | 8.9402 | 8.6281 | 8.3979 | 8.2772 | 7.9344 | 7.6411 | 7.2096 | 6.6771 | 6.4057 | 6.2355 | 14.4528 | 14.2615 | 14.0352 | 13.9284 | 13.5772 | 13.2651 | 13.0349 | 12.9142 | 12.5714 | 12.2781 | 11.8466 | 11.3141 | 11.0427 | 10.8725 | 9.3075 | 8.6934 | 8.577 | 8.5873 | 8.3111 | 8.0381 | 7.8669 | 7.8202 | 7.5693 | 7.3705 | 6.8022 | 6.3124 | 6.1497 | 6.0796 | 13.9445 | 13.3304 | 13.214 | 13.2243 | 12.9481 | 12.6751 | 12.5039 | 12.4572 | 12.2063 | 12.0075 | 11.4392 | 10.9494 | 10.7867 | 10.7166 | 9.3292 | 8.7346 | 8.6365 | 8.6675 | 8.4068 | 8.1405 | 7.9649 | 7.9052 | 7.6362 | 7.426 | 6.4234 | 3.5277 | 1.0492 | -0.44394 | 13.9662 | 13.3716 | 13.2735 | 13.3045 | 13.0438 | 12.7775 | 12.6019 | 12.5422 | 12.2732 | 12.063 | 11.0604 | 8.1647 | 5.6862 | 4.1931 | 9.3321 | 8.728 | 8.6317 | 8.6758 | 8.4311 | 8.18 | 8.0068 | 7.9489 | 7.6653 | 7.2283 | 4.2625 | 1.5678 | -0.16222 | 0.46341 | 13.9691 | 13.365 | 13.365 | 13.3128 | 13.0681 | 12.817 | 12.6438 | 12.5859 | 12.3023 | 11.8653 | 8.8995 | 6.2048 | 4.4748 | 5.1004 | 370584 | 429294 | BLACKBURN | PENWORTHAM
| Blackburn Rd Clayton | 11.2452 | 10.9812 | 10.8339 | 10.6767 | 10.4911 | 10.2563 | 9.9942 | 9.7159 | 9.4386 | 9.1097 | 7.8677 | 7.0378 | 6.6868 | 6.5434 | 18.9252 | 18.6612 | 18.5139 | 18.3567 | 18.1711 | 17.9363 | 17.6742 | 17.3959 | 17.1186 | 16.7897 | 15.5477 | 14.7178 | 14.3668 | 14.2234 | 11.4013 | 11.2648 | 11.083 | 10.9129 | 10.7269 | 10.5046 | 10.2522 | 9.9804 | 9.7039 | 9.415 | 8.6295 | 8.0497 | 7.6817 | 7.4699 | 19.0813 | 18.9448 | 18.763 | 18.5929 | 18.4069 | 18.1846 | 17.9322 | 17.6604 | 17.3839 | 17.095 | 16.3095 | 15.7297 | 15.3617 | 15.1499 | 11.2533 | 10.9982 | 10.8601 | 10.7114 | 10.5244 | 10.2992 | 10.0478 | 9.7876 | 9.5242 | 9.2306 | 8.1014 | 7.5177 | 7.3485 | 7.3657 | 18.9333 | 18.6782 | 18.5401 | 18.3914 | 18.2044 | 17.9792 | 17.7278 | 17.4676 | 17.2042 | 16.9106 | 15.7814 | 15.1977 | 15.0285 | 15.0457 | 11.2508 | 10.9933 | 10.8565 | 10.713 | 10.5498 | 10.3361 | 10.0844 | 9.8151 | 9.583 | 9.3406 | 7.3864 | 2.9371 | -0.53488 | -2.6485 | 18.9308 | 18.6733 | 18.5365 | 18.393 | 18.2298 | 18.0161 | 17.7644 | 17.4951 | 17.263 | 17.0206 | 15.0664 | 10.6171 | 7.1451 | 5.0315 | 11.2477 | 10.9697 | 10.834 | 10.7076 | 10.5536 | 10.3632 | 10.1313 | 9.8861 | 9.5364 | 8.5013 | 3.665 | -0.36312 | -2.6093 | -1.8646 | 18.9277 | 18.6497 | 18.6497 | 18.3876 | 18.2336 | 18.0432 | 17.8113 | 17.5661 | 17.2164 | 16.1813 | 11.345 | 7.3169 | 5.0707 | 5.8154 | 374632 | 430529 | HUNCOAT | PADIHAM
| Blackfriars | 0.099539 | -0.98201 | -1.3741 | -1.7667 | -1.6054 | -2.0271 | -2.2206 | -0.20422 | -0.42624 | -0.81735 | -1.8818 | -2.5978 | -3.1126 | -3.1246 | 9.7995 | 8.718 | 8.3259 | 7.9333 | 8.0946 | 7.6729 | 7.4794 | 7.2958 | 7.0738 | 6.6826 | 5.6182 | 4.9022 | 4.3874 | 4.3754 | 0.70471 | 0.19118 | -0.16598 | -0.63148 | -0.56246 | -1.0277 | -1.2953 | 0.63603 | 0.32279 | -0.10639 | -0.91857 | -1.7026 | -2.4037 | -2.7725 | 10.4047 | 9.8912 | 9.534 | 9.0685 | 9.1375 | 8.6723 | 8.4047 | 8.136 | 7.8228 | 7.3936 | 6.5814 | 5.7974 | 5.0963 | 4.7275 | 0.10544 | -0.96514 | -1.3458 | -1.726 | -1.5579 | -1.9664 | -2.1492 | -0.12194 | -0.32969 | -0.69402 | -1.7006 | -2.3785 | -2.8767 | -2.8976 | 9.8054 | 8.7349 | 8.3542 | 7.974 | 8.1421 | 7.7336 | 7.5508 | 7.3781 | 7.1703 | 6.806 | 5.7994 | 5.1215 | 4.6233 | 4.6024 | 0.12558 | -0.92408 | -1.2784 | -1.6429 | -1.4583 | -1.8592 | -2.0661 | -0.062088 | -0.26188 | -0.57373 | -1.6182 | -3.481 | -5.0704 | -6.2215 | 9.8256 | 8.7759 | 8.4216 | 8.0571 | 8.2417 | 7.8408 | 7.6339 | 7.4379 | 7.2381 | 6.9263 | 5.8818 | 4.019 | 2.4296 | 1.2785 | 0.13961 | -0.9018 | -1.236 | -1.5724 | -1.3882 | -1.7704 | -1.9335 | 0.11932 | -0.044982 | -0.58524 | -2.6706 | -4.5863 | -5.8037 | -5.4995 | 9.8396 | 8.7982 | 8.7982 | 8.1276 | 8.3118 | 7.9296 | 7.7665 | 7.6193 | 7.455 | 6.9148 | 4.8294 | 2.9137 | 1.6963 | 2.0005 | 383030 | 399104 | FREDERICK RD | KEARSLEY
| Blackley | 10.8942 | 10.5518 | 10.3273 | 10.0032 | 9.6541 | 9.2446 | 8.853 | 8.4102 | 7.9466 | 7.4036 | 5.4591 | 4.4375 | 4.1629 | 4.3618 | 15.5312 | 15.1888 | 14.9643 | 14.6402 | 14.2911 | 13.8816 | 13.49 | 13.0472 | 12.5836 | 12.0406 | 10.0961 | 9.0745 | 8.7999 | 8.9988 | 11.0378 | 10.8232 | 10.5664 | 10.2785 | 9.992 | 9.6459 | 9.3115 | 8.9255 | 8.52 | 8.1208 | 6.767 | 5.6769 | 5.0047 | 4.5813 | 15.6748 | 15.4602 | 15.2034 | 14.9155 | 14.629 | 14.2829 | 13.9485 | 13.5625 | 13.157 | 12.7578 | 11.404 | 10.3139 | 9.6417 | 9.2183 | 10.8853 | 10.564 | 10.3603 | 10.0495 | 9.7174 | 9.325 | 8.9492 | 8.5221 | 8.0826 | 7.5946 | 5.8576 | 4.9776 | 4.7299 | 4.9095 | 15.5223 | 15.201 | 14.9973 | 14.6865 | 14.3544 | 13.962 | 13.5862 | 13.1591 | 12.7196 | 12.2316 | 10.4946 | 9.6146 | 9.3669 | 9.5465 | 10.9025 | 10.5669 | 10.3533 | 10.0387 | 9.7161 | 9.3194 | 8.8946 | 8.4214 | 7.9929 | 7.5746 | 5.3298 | 1.3808 | -1.4165 | -3.4657 | 15.5395 | 15.2039 | 14.9903 | 14.6757 | 14.3531 | 13.9564 | 13.5316 | 13.0584 | 12.6299 | 12.2116 | 9.9668 | 6.0178 | 3.2205 | 1.1713 | 10.8918 | 10.5103 | 10.2781 | 9.9638 | 9.6193 | 9.2375 | 8.8636 | 8.4578 | 8.0369 | 7.0342 | 2.3831 | -1.1016 | -2.9789 | -2.4124 | 15.5288 | 15.1473 | 15.1473 | 14.6008 | 14.2563 | 13.8745 | 13.5006 | 13.0948 | 12.6739 | 11.6712 | 7.0201 | 3.5354 | 1.6581 | 2.2246 | 383882 | 403258 | RED BANK | WHITEGATE
| Blackpool | 12.0635 | 11.7843 | 11.7181 | 11.535 | 11.3452 | 11.1963 | 10.9162 | 10.711 | 10.4562 | 10.2647 | 9.6709 | 9.4336 | 9.3688 | 9.4923 | 19.8135 | 19.5343 | 19.4681 | 19.285 | 19.0952 | 18.9463 | 18.6662 | 18.461 | 18.2062 | 18.0147 | 17.4209 | 17.1836 | 17.1188 | 17.2423 | 12.2823 | 12.1587 | 11.8769 | 11.4998 | 11.1191 | 10.7483 | 9.9153 | 9.0529 | 8.0799 | 6.9219 | 6.7176 | 6.5991 | 6.6019 | 6.68 | 20.0323 | 19.9087 | 19.6269 | 19.2498 | 18.8691 | 18.4983 | 17.6653 | 16.8029 | 15.8299 | 14.6719 | 14.4676 | 14.3491 | 14.3519 | 14.43 | 12.087 | 11.8319 | 11.7935 | 11.6424 | 11.4851 | 11.3657 | 11.1231 | 10.9527 | 10.7391 | 10.5922 | 10.034 | 9.8144 | 9.7555 | 9.8755 | 19.837 | 19.5819 | 19.5435 | 19.3924 | 19.2351 | 19.1157 | 18.8731 | 18.7027 | 18.4891 | 18.3422 | 17.784 | 17.5644 | 17.5055 | 17.6255 | 12.0694 | 11.7947 | 11.7333 | 11.5544 | 11.3573 | 11.2036 | 10.9134 | 10.6962 | 10.4339 | 10.2558 | 9.4151 | 7.524 | 5.4165 | 3.8466 | 19.8194 | 19.5447 | 19.4833 | 19.3044 | 19.1073 | 18.9536 | 18.6634 | 18.4462 | 18.1839 | 18.0058 | 17.1651 | 15.274 | 13.1665 | 11.5966 | 12.1012 | 11.8517 | 11.8332 | 11.7088 | 11.5696 | 11.4827 | 11.2656 | 11.1299 | 10.9589 | 10.4722 | 8.0745 | 5.5037 | 3.9266 | 4.4467 | 19.8512 | 19.6017 | 19.6017 | 19.4588 | 19.3196 | 19.2327 | 19.0156 | 18.8799 | 18.7089 | 18.2222 | 15.8245 | 13.2537 | 11.6766 | 12.1967 | 330835 | 435308 | BLACKPOOL | PENWORTHAM
| Bollington | 2.3292 | 1.9825 | 1.761 | 1.5313 | 1.0964 | 0.75733 | 0.34115 | -0.12084 | -0.44181 | -1.0523 | -3.1267 | -4.3642 | -4.5048 | -4.3178 | 4.3292 | 3.9825 | 3.761 | 3.5313 | 3.0964 | 2.7573 | 2.3412 | 1.8792 | 1.5582 | 0.94769 | -1.1267 | -2.3642 | -2.5048 | -2.3178 | 2.423 | 2.161 | 1.8982 | 1.7207 | 1.3483 | 1.0705 | 0.71373 | 0.3092 | 0.067893 | -0.35981 | -1.5862 | -2.6387 | -3.2202 | -3.6859 | 4.423 | 4.161 | 3.8982 | 3.7207 | 3.3483 | 3.0705 | 2.7137 | 2.3092 | 2.0679 | 1.6402 | 0.41381 | -0.63871 | -1.2202 | -1.6859 | 2.3343 | 2.0059 | 1.8024 | 1.5881 | 1.174 | 0.85335 | 0.45361 | -0.00342 | -0.34142 | -0.8994 | -2.7989 | -3.9041 | -3.9971 | -3.7948 | 4.3343 | 4.0059 | 3.8024 | 3.5881 | 3.174 | 2.8534 | 2.4536 | 1.9966 | 1.6586 | 1.1006 | -0.79895 | -1.9041 | -1.9971 | -1.7948 | 2.3381 | 1.983 | 1.7549 | 1.5285 | 1.0935 | 0.73857 | 0.27566 | -0.23775 | -0.49999 | -0.95947 | -2.992 | -6.0699 | -7.7818 | -9.1652 | 4.3381 | 3.983 | 3.7549 | 3.5285 | 3.0935 | 2.7386 | 2.2757 | 1.7623 | 1.5 | 1.0405 | -0.99203 | -4.0699 | -5.7818 | -7.1652 | 2.3149 | 1.9235 | 1.7071 | 1.5021 | 1.0837 | 0.77357 | 0.38039 | -0.039467 | -0.25139 | -1.0793 | -4.7157 | -7.2465 | -8.233 | -7.7667 | 4.3149 | 3.9235 | 3.9235 | 3.5021 | 3.0837 | 2.7736 | 2.3804 | 1.9605 | 1.7486 | 0.9207 | -2.7157 | -5.2465 | -6.233 | -5.7667 | 393042 | 377873 | MACCLESFIELD | MACCLESFIELD
| Bolton By Bowland | -0.24818 | -0.416 | -0.47881 | -0.53619 | -0.6354 | -0.7593 | -0.89932 | -1.0418 | -1.2081 | -1.4042 | -2.0619 | -2.3453 | -2.3819 | -2.2451 | 4.2518 | 4.084 | 4.0212 | 3.9638 | 3.8646 | 3.7407 | 3.6007 | 3.4582 | 3.2919 | 3.0958 | 2.4381 | 2.1547 | 2.1181 | 2.2549 | -0.13491 | -0.20208 | -0.28849 | -0.38225 | -0.49725 | -0.62269 | -0.7664 | -0.9161 | -1.0726 | -1.2328 | -1.6433 | -2.0104 | -2.2396 | -2.3695 | 4.3651 | 4.2979 | 4.2115 | 4.1177 | 4.0028 | 3.8773 | 3.7336 | 3.5839 | 3.4274 | 3.2672 | 2.8567 | 2.4896 | 2.2604 | 2.1305 | -0.24588 | -0.41123 | -0.47149 | -0.52624 | -0.59881 | -0.71742 | -0.85209 | -1.0007 | -1.1593 | -1.3362 | -1.93 | -2.1743 | -2.1948 | -2.066 | 4.2541 | 4.0888 | 4.0285 | 3.9738 | 3.9012 | 3.7826 | 3.6479 | 3.4993 | 3.3407 | 3.1638 | 2.57 | 2.3257 | 2.3052 | 2.434 | -0.24209 | -0.40463 | -0.46206 | -0.51424 | -0.6129 | -0.7306 | -0.86481 | -0.99493 | -1.1152 | -1.2315 | -1.757 | -2.3118 | -2.574 | -2.7053 | 4.2579 | 4.0954 | 4.0379 | 3.9858 | 3.8871 | 3.7694 | 3.6352 | 3.5051 | 3.3848 | 3.2685 | 2.743 | 2.1882 | 1.926 | 1.7947 | -0.24651 | -0.41839 | -0.47649 | -0.52418 | -0.62769 | -0.73495 | -0.85402 | -0.96364 | -1.07 | -1.2582 | -2.086 | -2.5506 | -2.6893 | -2.4838 | 4.2535 | 4.0816 | 4.0816 | 3.9758 | 3.8723 | 3.765 | 3.646 | 3.5364 | 3.43 | 3.2418 | 2.414 | 1.9494 | 1.8107 | 2.0162 | 378320 | 449559 | PADIHAM | PADIHAM
| Bolton Le Sands | 5.5471 | 4.9661 | 4.7212 | 4.3767 | 3.9724 | 3.6051 | 3.1578 | 2.696 | 2.2101 | 1.601 | -1.1068 | -3.0877 | -4.2773 | -3.7624 | 9.0471 | 8.4661 | 8.2212 | 7.8767 | 7.4724 | 7.1051 | 6.6578 | 6.196 | 5.7101 | 5.101 | 2.3932 | 0.4123 | -0.77732 | -0.26242 | 5.7139 | 5.2993 | 5.0695 | 4.8277 | 4.5197 | 4.2406 | 3.8799 | 3.5007 | 3.0514 | 2.6933 | 1.3649 | -0.11631 | -1.3235 | -1.7594 | 9.2139 | 8.7993 | 8.5695 | 8.3277 | 8.0197 | 7.7406 | 7.3799 | 7.0007 | 6.5514 | 6.1933 | 4.8649 | 3.3837 | 2.1765 | 1.7406 | 5.5534 | 4.9897 | 4.7633 | 4.448 | 4.0735 | 3.7353 | 3.3189 | 2.8886 | 2.4343 | 1.8982 | -0.50115 | -2.1574 | -3.2408 | -2.6031 | 9.0534 | 8.4897 | 8.2633 | 7.948 | 7.5735 | 7.2353 | 6.8189 | 6.3886 | 5.9343 | 5.3982 | 2.9988 | 1.3426 | 0.25923 | 0.89693 | 5.5471 | 4.9232 | 4.6299 | 4.2601 | 3.7944 | 3.3154 | 2.681 | 1.9968 | 1.3562 | 0.79804 | -2.2225 | -7.39 | -11.3706 | -12.9591 | 9.0471 | 8.4232 | 8.1299 | 7.7601 | 7.2944 | 6.8154 | 6.181 | 5.4968 | 4.8562 | 4.298 | 1.2775 | -3.89 | -7.8706 | -9.4591 | 5.5678 | 4.9557 | 4.6824 | 4.3273 | 3.8698 | 3.4334 | 2.8852 | 2.3179 | 1.7723 | 0.70634 | -4.7289 | -8.9961 | -11.8884 | -10.6432 | 9.0678 | 8.4557 | 8.4557 | 7.8273 | 7.3698 | 6.9334 | 6.3852 | 5.8179 | 5.2723 | 4.2063 | -1.2289 | -5.4961 | -8.3884 | -7.1432 | 347707 | 467237 | LANCASTER | HEYSHAM
| Botany Bay | 2.0327 | 1.7423 | 1.4396 | 1.0544 | 0.69835 | 0.22854 | -0.26288 | -0.79882 | -1.3095 | -1.9148 | -3.9961 | -5.2994 | -5.7551 | -5.8182 | 10.0327 | 9.7423 | 9.4396 | 9.0544 | 8.6984 | 8.2285 | 7.7371 | 7.2012 | 6.6905 | 6.0852 | 4.0039 | 2.7006 | 2.2449 | 2.1818 | 2.0919 | 1.8596 | 1.5463 | 1.2129 | 0.93069 | 0.53948 | 0.13333 | -0.31423 | -0.75134 | -1.2244 | -2.7828 | -3.8536 | -4.4051 | -4.7806 | 10.0919 | 9.8596 | 9.5463 | 9.2129 | 8.9307 | 8.5395 | 8.1333 | 7.6858 | 7.2487 | 6.7756 | 5.2172 | 4.1464 | 3.5949 | 3.2194 | 2.0362 | 1.7546 | 1.4612 | 1.0864 | 0.74352 | 0.28982 | -0.18539 | -0.70467 | -1.1924 | -1.7442 | -3.6296 | -4.753 | -5.0661 | -5.0589 | 10.0362 | 9.7546 | 9.4612 | 9.0864 | 8.7435 | 8.2898 | 7.8146 | 7.2953 | 6.8076 | 6.2558 | 4.3704 | 3.247 | 2.9339 | 2.9411 | 2.0369 | 1.75 | 1.4566 | 1.0844 | 0.77089 | 0.3501 | -0.088045 | -0.56063 | -0.96167 | -1.3949 | -3.6616 | -6.9467 | -9.5546 | -11.5321 | 10.0369 | 9.75 | 9.4566 | 9.0844 | 8.7709 | 8.3501 | 7.912 | 7.4394 | 7.0383 | 6.6051 | 4.3384 | 1.0533 | -1.5546 | -3.5321 | 2.006 | 1.6604 | 1.3547 | 0.99929 | 0.71967 | 0.35095 | -0.042157 | -0.45213 | -0.85026 | -1.6689 | -5.2784 | -7.859 | -9.1558 | -9.2965 | 10.006 | 9.6604 | 9.6604 | 8.9993 | 8.7197 | 8.3509 | 7.9578 | 7.5479 | 7.1497 | 6.3311 | 2.7216 | 0.14102 | -1.1558 | -1.2965 | 359442 | 418850 | LEYLAND | PENWORTHAM
| Bow Lane | 4.5775 | 3.9614 | 3.5817 | 3.098 | 2.7061 | 2.0876 | 1.4583 | 0.75304 | 0.10546 | -0.70308 | -3.5851 | -5.5003 | -6.2312 | -6.7836 | 9.2145 | 8.5984 | 8.2187 | 7.735 | 7.3431 | 6.7246 | 6.0953 | 5.39 | 4.7425 | 3.9339 | 1.0519 | -0.86327 | -1.5942 | -2.1466 | 4.8994 | 4.5529 | 4.0842 | 3.5723 | 3.1892 | 2.6001 | 1.9947 | 1.3076 | 0.66176 | -0.075023 | -2.1616 | -3.7811 | -4.8342 | -5.6232 | 9.5364 | 9.1899 | 8.7212 | 8.2093 | 7.8262 | 7.2371 | 6.6317 | 5.9446 | 5.2988 | 4.562 | 2.4754 | 0.85586 | -0.19718 | -0.98616 | 4.5887 | 3.9901 | 3.6276 | 3.1617 | 2.7895 | 2.1946 | 1.5879 | 0.90588 | 0.29077 | -0.44519 | -3.0306 | -4.4591 | -4.9851 | -5.1612 | 9.2257 | 8.6271 | 8.2646 | 7.7987 | 7.4265 | 6.8316 | 6.2249 | 5.5429 | 4.9278 | 4.1918 | 1.6064 | 0.17791 | -0.34814 | -0.52424 | 4.5968 | 4.0051 | 3.6562 | 3.202 | 2.8773 | 2.3275 | 1.7526 | 1.1057 | 0.5778 | -0.035335 | -4.0214 | -11.645 | -17.7448 | -22.1913 | 9.2338 | 8.6421 | 8.2932 | 7.839 | 7.5143 | 6.9645 | 6.3896 | 5.7427 | 5.2148 | 4.6017 | 0.61557 | -7.008 | -13.1078 | -17.5543 | 4.568 | 3.9191 | 3.5753 | 3.1597 | 2.8745 | 2.3758 | 1.8374 | 1.2338 | 0.53113 | -1.2456 | -9.6785 | -16.5948 | -20.7313 | -20.4784 | 9.205 | 8.5561 | 8.5561 | 7.7967 | 7.5115 | 7.0128 | 6.4744 | 5.8708 | 5.1681 | 3.3914 | -5.0415 | -11.9578 | -16.0943 | -15.8414 | 354895 | 422392 | LEYLAND | PENWORTHAM
| Bowaters | 8.4712 | 8.1503 | 8.3066 | 8.4388 | 8.5455 | 8.0103 | 7.8029 | 7.8482 | 7.9036 | 7.5998 | 6.8103 | 6.3566 | 6.5716 | 7.2551 | 28.9712 | 28.6503 | 28.8066 | 28.9388 | 29.0455 | 28.5103 | 28.3029 | 28.3482 | 28.4036 | 28.0998 | 27.3103 | 26.8566 | 27.0716 | 27.7551 | 9.621 | 10.1624 | 9.998 | 9.902 | 9.86 | 9.3156 | 9.0551 | 9.0243 | 8.9902 | 8.6049 | 8.0798 | 8.3073 | 8.1764 | 8.8484 | 30.121 | 30.6624 | 30.498 | 30.402 | 30.36 | 29.8156 | 29.5551 | 29.5243 | 29.4902 | 29.1049 | 28.5798 | 28.8073 | 28.6764 | 29.3484 | 8.4723 | 8.1521 | 8.3094 | 8.4424 | 8.5501 | 8.0168 | 7.8111 | 7.8576 | 7.9157 | 7.6197 | 6.8894 | 6.5768 | 6.8628 | 7.6696 | 28.9723 | 28.6521 | 28.8094 | 28.9424 | 29.0501 | 28.5168 | 28.3111 | 28.3576 | 28.4157 | 28.1197 | 27.3894 | 27.0768 | 27.3628 | 28.1696 | 8.55 | 8.3089 | 8.5425 | 8.7518 | 8.9357 | 8.48 | 8.3445 | 8.4538 | 8.5706 | 8.3394 | -2.2391 | -1.5144 | 0.038238 | 1.8165 | 29.05 | 28.8089 | 29.0425 | 29.2518 | 29.4357 | 28.98 | 28.8445 | 28.9538 | 29.0706 | 28.8394 | 18.2609 | 18.9856 | 20.5382 | 22.3165 | 8.5379 | 8.2774 | 8.5001 | 8.7045 | 8.4337 | 7.9951 | 1.5639 | 2.1244 | 2.6434 | 2.723 | 1.6657 | 2.9908 | 4.2196 | 5.8879 | 29.0379 | 28.7774 | 28.7774 | 29.2045 | 28.9337 | 28.4951 | 22.0639 | 22.6244 | 23.1434 | 23.223 | 22.1657 | 23.4908 | 24.7196 | 26.3879 | 319579 | 472480 | BARROW & SANDGATE | HARKER
| Bowdon | 7.5192 | 6.9011 | 6.6208 | 6.285 | 6.1788 | 5.7261 | 5.202 | 4.8121 | 4.2873 | 3.798 | 2.2 | 1.3624 | 1.4045 | 1.6205 | 12.1562 | 11.5381 | 11.2578 | 10.922 | 10.8158 | 10.3631 | 9.839 | 9.4491 | 8.9243 | 8.435 | 6.837 | 5.9994 | 6.0415 | 6.2575 | 7.7363 | 7.2879 | 6.9413 | 6.6027 | 6.5082 | 6.0757 | 5.5523 | 5.1958 | 4.6478 | 4.2325 | 3.0964 | 2.102 | 1.6955 | 1.3185 | 12.3733 | 11.9249 | 11.5783 | 11.2397 | 11.1452 | 10.7127 | 10.1893 | 9.8328 | 9.2848 | 8.8695 | 7.7334 | 6.739 | 6.3325 | 5.9555 | 7.5269 | 6.9379 | 6.6627 | 6.3419 | 6.233 | 5.7909 | 5.2973 | 4.908 | 4.4277 | 3.9723 | 2.528 | 1.7816 | 1.84 | 2.0293 | 12.1639 | 11.5749 | 11.2997 | 10.9789 | 10.87 | 10.4279 | 9.9343 | 9.545 | 9.0647 | 8.6093 | 7.165 | 6.4186 | 6.477 | 6.6663 | 7.5438 | 6.9567 | 6.723 | 6.4352 | 6.3825 | 5.9925 | 5.5159 | 5.2253 | 4.8126 | 4.5401 | 2.5536 | -1.8333 | -4.852 | -6.8914 | 12.1808 | 11.5937 | 11.36 | 11.0722 | 11.0195 | 10.6295 | 10.1529 | 9.8623 | 9.4496 | 9.1771 | 7.1906 | 2.8037 | -0.21501 | -2.2544 | 7.4436 | 6.7434 | 6.5532 | 6.3453 | 6.3472 | 6.0443 | 5.6613 | 5.4421 | 5.0164 | 3.982 | -0.8991 | -4.8165 | -6.6076 | -5.6475 | 12.0806 | 11.3804 | 11.3804 | 10.9823 | 10.9842 | 10.6813 | 10.2983 | 10.0791 | 9.6534 | 8.619 | 3.7379 | -0.17947 | -1.9706 | -1.0105 | 376743 | 386810 | ALTRINCHAM | CARRINGTON
| Bradford | 8.9406 | 7.9482 | 7.8521 | 7.5831 | 7.6573 | 7.2831 | 7.0822 | 6.8719 | 6.5214 | 6.22 | 4.9653 | 3.8637 | 2.2055 | 0.98206 | 13.5776 | 12.5852 | 12.4891 | 12.2201 | 12.2943 | 11.9201 | 11.7192 | 11.5089 | 11.1584 | 10.857 | 9.6023 | 8.5007 | 6.8425 | 5.6191 | 9.4844 | 8.9797 | 8.8362 | 8.5133 | 8.5442 | 8.1838 | 7.9756 | 7.7528 | 7.3899 | 7.1049 | 6.1119 | 5.2016 | 4.6063 | 4.2106 | 14.1214 | 13.6167 | 13.4732 | 13.1503 | 13.1812 | 12.8208 | 12.6126 | 12.3898 | 12.0269 | 11.7419 | 10.7489 | 9.8386 | 9.2433 | 8.8476 | 8.9478 | 7.9651 | 7.876 | 7.6142 | 7.695 | 7.3308 | 7.1384 | 6.9366 | 6.5994 | 6.3221 | 5.203 | 4.3534 | 3.7839 | 3.5461 | 13.5848 | 12.6021 | 12.513 | 12.2512 | 12.332 | 11.9678 | 11.7754 | 11.5736 | 11.2364 | 10.9591 | 9.84 | 8.9904 | 8.4209 | 8.1831 | 8.949 | 7.9657 | 7.8743 | 7.6049 | 7.6747 | 7.2903 | 7.0635 | 6.8164 | 6.4375 | 6.1432 | 4.2531 | 0.25116 | -3.4946 | -5.9331 | 13.586 | 12.6027 | 12.5113 | 12.2419 | 12.3117 | 11.9273 | 11.7005 | 11.4534 | 11.0745 | 10.7802 | 8.8901 | 4.8882 | 1.1424 | -1.2961 | 8.9404 | 7.9337 | 7.8342 | 7.5663 | 7.6428 | 7.2648 | 7.0332 | 6.7814 | 6.3657 | 5.5256 | 1.3958 | -2.4078 | -5.1852 | -5.1762 | 13.5774 | 12.5707 | 12.5707 | 12.2033 | 12.2798 | 11.9018 | 11.6702 | 11.4184 | 11.0027 | 10.1626 | 6.0328 | 2.2292 | -0.5482 | -0.53919 | 387613 | 397710 | STUART ST | STALYBRIDGE
| Bradshawgate | 9.7036 | 9.3137 | 9.2271 | 9.1339 | 9.0423 | 8.7444 | 8.4956 | 8.371 | 8.1437 | 7.9236 | 7.0319 | 6.4981 | 6.1915 | 6.1516 | 20.3436 | 19.9537 | 19.8671 | 19.7739 | 19.6823 | 19.3844 | 19.1356 | 19.011 | 18.7837 | 18.5636 | 17.6719 | 17.1381 | 16.8315 | 16.7916 | 9.984 | 9.8299 | 9.6263 | 9.4481 | 9.2984 | 8.9707 | 8.6766 | 8.4928 | 8.1941 | 7.8294 | 7.3605 | 6.9892 | 6.6747 | 6.5881 | 20.624 | 20.4699 | 20.2663 | 20.0881 | 19.9384 | 19.6107 | 19.3166 | 19.1328 | 18.8341 | 18.4694 | 18.0005 | 17.6292 | 17.3147 | 17.2281 | 9.7118 | 9.3337 | 9.2585 | 9.1754 | 9.094 | 8.8101 | 8.5698 | 8.4607 | 8.2365 | 8.0214 | 7.1928 | 6.783 | 6.5367 | 6.5629 | 20.3518 | 19.9737 | 19.8985 | 19.8154 | 19.734 | 19.4501 | 19.2098 | 19.1007 | 18.8765 | 18.6614 | 17.8328 | 17.423 | 17.1767 | 17.2029 | 9.7167 | 9.3408 | 9.2674 | 9.1858 | 9.1012 | 8.8082 | 8.551 | 8.4141 | 8.1816 | 7.9808 | 6.762 | 4.7103 | 3.1086 | 2.227 | 20.3567 | 19.9808 | 19.9074 | 19.8258 | 19.7412 | 19.4482 | 19.191 | 19.0541 | 18.8216 | 18.6208 | 17.402 | 15.3503 | 13.7486 | 12.867 | 9.714 | 9.3222 | 9.2487 | 9.1784 | 9.1017 | 8.8264 | 8.5891 | 8.4785 | 8.2422 | 7.7043 | 5.26 | 3.4633 | 2.4326 | 2.9264 | 20.354 | 19.9622 | 19.9622 | 19.8184 | 19.7417 | 19.4664 | 19.2291 | 19.1185 | 18.8822 | 18.3443 | 15.9 | 14.1033 | 13.0726 | 13.5664 | 371891 | 408910 | BOLTON | KEARSLEY
| Bramhall | 4.8793 | 4.4787 | 4.1864 | 3.6891 | 3.674 | 3.3243 | 2.9204 | 2.5393 | 2.1941 | 1.8119 | 0.4712 | -0.029198 | -0.12899 | 0.18336 | 8.3793 | 7.9787 | 7.6864 | 7.1891 | 7.174 | 6.8243 | 6.4204 | 6.0393 | 5.6941 | 5.3119 | 3.9712 | 3.4708 | 3.371 | 3.6834 | 5.1401 | 4.9206 | 4.6466 | 4.1376 | 4.1388 | 3.8184 | 3.4351 | 3.067 | 2.7186 | 2.3625 | 1.3735 | 0.80049 | 0.44586 | 0.40196 | 8.6401 | 8.4206 | 8.1466 | 7.6376 | 7.6388 | 7.3184 | 6.9351 | 6.567 | 6.2186 | 5.8625 | 4.8735 | 4.3005 | 3.9459 | 3.902 | 4.917 | 4.4892 | 4.2369 | 3.7262 | 3.7402 | 3.401 | 3.0078 | 2.6364 | 2.3067 | 1.9618 | 0.72219 | 0.27265 | 0.21814 | 0.543 | 8.417 | 7.9892 | 7.7369 | 7.2262 | 7.2402 | 6.901 | 6.5078 | 6.1364 | 5.8067 | 5.4618 | 4.2222 | 3.7727 | 3.7181 | 4.043 | 4.9038 | 4.528 | 4.2909 | 3.8277 | 3.8992 | 3.6303 | 3.3115 | 3.0271 | 2.8152 | 2.6039 | 0.82732 | -2.8749 | -5.8703 | -7.6583 | 8.4038 | 8.028 | 7.7909 | 7.3277 | 7.3992 | 7.1303 | 6.8115 | 6.5271 | 6.3152 | 6.1039 | 4.3273 | 0.62508 | -2.3703 | -4.1583 | 4.8766 | 4.4522 | 4.2003 | 3.7903 | 3.894 | 3.6912 | 3.4342 | 3.2262 | 3.0015 | 2.108 | -2.089 | -5.4173 | -7.4929 | -6.5399 | 8.3766 | 7.9522 | 7.9522 | 7.2903 | 7.394 | 7.1912 | 6.9342 | 6.7262 | 6.5015 | 5.608 | 1.411 | -1.9173 | -3.9929 | -3.0399 | 389440 | 386463 | HAZEL GROVE | BREDBURY
| Bridgewater | 7.5013 | 6.9311 | 7.0098 | 6.9546 | 6.8554 | 6.6646 | 6.4855 | 6.3881 | 6.2648 | 6.1464 | 5.7079 | 5.4671 | 5.393 | 5.4333 | 14.5013 | 13.9311 | 14.0098 | 13.9546 | 13.8554 | 13.6646 | 13.4855 | 13.3881 | 13.2648 | 13.1464 | 12.7079 | 12.4671 | 12.393 | 12.4333 | 7.9282 | 7.7662 | 7.6827 | 7.5597 | 7.3748 | 7.1578 | 6.9149 | 6.7454 | 6.5639 | 6.3611 | 5.9193 | 5.5843 | 5.434 | 5.4197 | 14.9282 | 14.7662 | 14.6827 | 14.5597 | 14.3748 | 14.1578 | 13.9149 | 13.7454 | 13.5639 | 13.3611 | 12.9193 | 12.5843 | 12.434 | 12.4197 | 7.5051 | 6.9425 | 7.0278 | 6.9783 | 6.8846 | 6.6996 | 6.5261 | 6.434 | 6.317 | 6.2079 | 5.7848 | 5.5641 | 5.4966 | 5.5366 | 14.5051 | 13.9425 | 14.0278 | 13.9783 | 13.8846 | 13.6996 | 13.5261 | 13.434 | 13.317 | 13.2079 | 12.7848 | 12.5641 | 12.4966 | 12.5366 | 7.5271 | 6.9828 | 7.0857 | 7.0532 | 6.9654 | 6.7948 | 6.6114 | 6.5219 | 6.418 | 6.309 | 5.8207 | 4.6397 | 3.7532 | 3.1467 | 14.5271 | 13.9828 | 14.0857 | 14.0532 | 13.9654 | 13.7948 | 13.6114 | 13.5219 | 13.418 | 13.309 | 12.8207 | 11.6397 | 10.7532 | 10.1467 | 7.534 | 6.9955 | 7.1072 | 7.088 | 7.0186 | 6.8594 | 6.7081 | 6.6373 | 6.5418 | 6.234 | 4.8209 | 3.7053 | 3.1085 | 3.4538 | 14.534 | 13.9955 | 13.9955 | 14.088 | 14.0186 | 13.8594 | 13.7081 | 13.6373 | 13.5418 | 13.234 | 11.8209 | 10.7053 | 10.1085 | 10.4538 | 383543 | 397628 | BLOOM ST | SOUTH MANCHESTER
| Brinksway | 13.2082 | 12.5811 | 12.5486 | 12.3078 | 12.2536 | 12.0439 | 11.7445 | 1.6996 | 1.4675 | 1.2394 | 0.31723 | -0.64167 | -1.4165 | -1.7744 | 17.8452 | 17.2181 | 17.1856 | 16.9448 | 16.8906 | 16.6809 | 16.3815 | 16.3396 | 16.1075 | 15.8794 | 14.9572 | 13.9983 | 13.2235 | 12.8656 | 13.4855 | 13.1074 | 13.029 | 12.7403 | 12.6458 | 12.4125 | 12.0801 | 11.9884 | 11.7035 | 11.4436 | 10.7604 | 10.0331 | 9.4268 | 9.182 | 18.1225 | 17.7444 | 17.666 | 17.3773 | 17.2828 | 17.0495 | 16.7171 | 16.6254 | 16.3405 | 16.0806 | 15.3974 | 14.6701 | 14.0638 | 13.819 | 13.2152 | 12.6029 | 12.5808 | 12.3531 | 12.3093 | 12.1123 | 11.8272 | 11.7943 | 11.5787 | 11.3786 | 10.6294 | 9.9364 | 9.4201 | 9.4711 | 17.8522 | 17.2399 | 17.2178 | 16.9901 | 16.9463 | 16.7493 | 16.4642 | 16.4313 | 16.2157 | 16.0156 | 15.2664 | 14.5734 | 14.0571 | 14.1081 | 13.219 | 12.6018 | 12.5775 | 12.3423 | 12.2892 | 12.0716 | 11.7433 | 11.6675 | 11.4162 | 11.1976 | 10.0003 | 6.174 | 2.4673 | 0.38383 | 17.856 | 17.2388 | 17.2145 | 16.9793 | 16.9262 | 16.7086 | 16.3803 | 16.3045 | 16.0532 | 15.8346 | 14.6373 | 10.811 | 7.1043 | 5.0208 | 13.2267 | 12.6067 | 12.5954 | 12.3846 | 12.3454 | 12.1538 | 11.861 | 11.8236 | 11.5615 | 10.9616 | 7.6844 | 4.7614 | 2.5428 | 1.7028 | 17.8637 | 17.2437 | 17.2437 | 17.0216 | 16.9824 | 16.7908 | 16.498 | 16.4606 | 16.1985 | 15.5986 | 12.3214 | 9.3984 | 7.1798 | 6.3398 | 388434 | 389885 | ADSWOOD | BREDBURY
| Broadheath | 13.9617 | 13.2665 | 12.9757 | 12.5202 | 12.1802 | 11.8391 | 11.1896 | 10.6467 | 9.6849 | 8.7179 | 6.5254 | 4.8429 | 3.7628 | 3.5243 | 18.8617 | 18.1665 | 17.8757 | 17.4202 | 17.0802 | 16.7391 | 16.0896 | 15.5467 | 14.5849 | 13.6179 | 11.4254 | 9.7429 | 8.6628 | 8.4243 | 14.451 | 14.1518 | 13.6571 | 13.0955 | 12.6942 | 12.1931 | 11.5221 | 11.0214 | 9.9147 | 8.9471 | 7.4066 | 5.9627 | 4.9015 | 4.2945 | 19.351 | 19.0518 | 18.5571 | 17.9955 | 17.5942 | 17.0931 | 16.4221 | 15.9214 | 14.8147 | 13.8471 | 12.3066 | 10.8627 | 9.8015 | 9.1945 | 13.9788 | 13.3181 | 13.0631 | 12.6324 | 12.3261 | 12.077 | 11.349 | 10.7241 | 10.037 | 9.1584 | 7.2174 | 5.6883 | 4.7849 | 4.7038 | 18.8788 | 18.2181 | 17.9631 | 17.5324 | 17.2261 | 16.977 | 16.249 | 15.6241 | 14.937 | 14.0584 | 12.1174 | 10.5883 | 9.6849 | 9.6038 | 13.996 | 13.3322 | 13.068 | 12.6265 | 12.2937 | 12.0406 | 11.2568 | 10.5101 | 9.7636 | 9.0036 | 5.2254 | -2.3373 | -8.2983 | -12.4595 | 18.896 | 18.2322 | 17.968 | 17.5265 | 17.1937 | 16.9406 | 16.1568 | 15.4101 | 14.6636 | 13.9036 | 10.1254 | 2.5627 | -3.3983 | -7.5595 | 13.9809 | 13.2699 | 13.0214 | 12.6347 | 12.3585 | 12.2108 | 11.3438 | 10.6661 | 9.8495 | 8.0508 | -0.084672 | -6.9375 | -11.1792 | -10.1739 | 18.8809 | 18.1699 | 18.1699 | 17.5347 | 17.2585 | 17.1108 | 16.2438 | 15.5661 | 14.7495 | 12.9508 | 4.8153 | -2.0375 | -6.2792 | -5.2739 | 376412 | 389026 | ALTRINCHAM | CARRINGTON
| Broadway | 11.957 | 11.9015 | 11.7731 | 11.5188 | 11.1252 | 10.8239 | 10.436 | 9.9064 | 9.5196 | 9.0608 | 7.192 | 5.9864 | 5.2537 | 5.6841 | 16.094 | 16.0385 | 15.9101 | 15.6558 | 15.2622 | 14.9609 | 14.573 | 14.0434 | 13.6566 | 13.1978 | 11.329 | 10.1234 | 9.3907 | 9.8211 | 12.0227 | 11.979 | 11.8262 | 11.567 | 11.2221 | 10.9513 | 10.59 | 10.0908 | 9.7906 | 9.3804 | 8.0096 | 6.9384 | 5.9278 | 5.9673 | 16.1597 | 16.116 | 15.9632 | 15.704 | 15.3591 | 15.0883 | 14.727 | 14.2278 | 13.9276 | 13.5174 | 12.1466 | 11.0754 | 10.0648 | 10.1043 | 11.966 | 11.9167 | 11.815 | 11.5702 | 11.2009 | 10.9165 | 10.5458 | 10.0393 | 9.6704 | 9.2619 | 7.6036 | 6.6217 | 5.9613 | 6.4978 | 16.103 | 16.0537 | 15.952 | 15.7072 | 15.3379 | 15.0535 | 14.6828 | 14.1763 | 13.8074 | 13.3989 | 11.7406 | 10.7587 | 10.0983 | 10.6348 | 11.9623 | 11.9068 | 11.7879 | 11.5383 | 11.1665 | 10.8792 | 10.4871 | 9.9588 | 9.6934 | 9.3342 | 6.7165 | 1.2897 | -3.5179 | -5.5523 | 16.0993 | 16.0438 | 15.9249 | 15.6753 | 15.3035 | 15.0162 | 14.6241 | 14.0958 | 13.8304 | 13.4712 | 10.8535 | 5.4267 | 0.61909 | -1.4153 | 11.9839 | 11.933 | 11.8096 | 11.5855 | 11.236 | 10.9876 | 10.6389 | 10.1632 | 9.7909 | 8.6016 | 2.7073 | -2.291 | -5.8003 | -4.3469 | 16.1209 | 16.07 | 16.07 | 15.7225 | 15.373 | 15.1246 | 14.7759 | 14.3002 | 13.9279 | 12.7386 | 6.8443 | 1.846 | -1.6633 | -0.20986 | 344792 | 464471 | LANCASTER | HEYSHAM
| Buckshaw | 11.618 | 10.7884 | 10.3342 | 10.1562 | 9.9198 | 9.6508 | 9.3708 | 9.0925 | 8.8004 | 8.5021 | 7.2412 | 6.171 | 5.5715 | 4.9922 | 16.118 | 15.2884 | 14.8342 | 14.6562 | 14.4198 | 14.1508 | 13.8708 | 13.5925 | 13.3004 | 13.0021 | 11.7412 | 10.671 | 10.0715 | 9.4922 | 12.0579 | 11.6437 | 11.2841 | 11.0838 | 10.8507 | 10.5959 | 10.325 | 10.0503 | 9.7531 | 9.464 | 8.5417 | 7.7675 | 7.1611 | 6.6901 | 16.5579 | 16.1437 | 15.7841 | 15.5838 | 15.3507 | 15.0959 | 14.825 | 14.5503 | 14.2531 | 13.964 | 13.0417 | 12.2675 | 11.6611 | 11.1901 | 11.6219 | 10.7962 | 10.3458 | 10.1715 | 9.9402 | 9.6773 | 9.4033 | 9.1305 | 8.8483 | 8.5742 | 7.4635 | 6.7359 | 6.2932 | 6.0027 | 16.1219 | 15.2962 | 14.8458 | 14.6715 | 14.4402 | 14.1773 | 13.9033 | 13.6305 | 13.3483 | 13.0742 | 11.9635 | 11.2359 | 10.7932 | 10.5027 | 11.6339 | 10.8254 | 10.3982 | 10.2498 | 10.0553 | 9.8268 | 9.5815 | 9.3353 | 9.0836 | 8.837 | 7.1729 | 5.2122 | 3.4144 | 1.711 | 16.1339 | 15.3254 | 14.8982 | 14.7498 | 14.5553 | 14.3268 | 14.0815 | 13.8353 | 13.5836 | 13.337 | 11.6729 | 9.7122 | 7.9144 | 6.211 | 11.6009 | 10.7397 | 10.3021 | 10.1666 | 9.9865 | 9.7692 | 9.5142 | 9.2547 | 8.9636 | 8.564 | 6.392 | 4.0794 | 2.5037 | 2.3928 | 16.1009 | 15.2397 | 15.2397 | 14.6666 | 14.4865 | 14.2692 | 14.0142 | 13.7547 | 13.4636 | 13.064 | 10.892 | 8.5794 | 7.0037 | 6.8928 | 356748 | 421312 | LEYLAND | PENWORTHAM
| Burnley | 11.9256 | 11.7957 | 11.5278 | 11.453 | 11.2809 | 10.8889 | 10.4526 | 10.1659 | 9.7175 | 9.282 | 7.9005 | 7.1841 | 7.0639 | 7.2169 | 16.5626 | 16.4327 | 16.1648 | 16.09 | 15.9179 | 15.5259 | 15.0896 | 14.8029 | 14.3545 | 13.919 | 12.5375 | 11.8211 | 11.7009 | 11.8539 | 12.0424 | 12.0029 | 11.6803 | 11.5954 | 11.4383 | 11.1057 | 10.7188 | 10.4442 | 10.1413 | 9.8142 | 8.8702 | 8.1108 | 7.6769 | 7.3914 | 16.6794 | 16.6399 | 16.3173 | 16.2324 | 16.0753 | 15.7427 | 15.3558 | 15.0812 | 14.7783 | 14.4512 | 13.5072 | 12.7478 | 12.3139 | 12.0284 | 11.9305 | 11.806 | 11.5455 | 11.476 | 11.3113 | 10.9337 | 10.5096 | 10.2326 | 9.8024 | 9.4076 | 8.1758 | 7.5787 | 7.501 | 7.674 | 16.5675 | 16.443 | 16.1825 | 16.113 | 15.9483 | 15.5707 | 15.1466 | 14.8696 | 14.4394 | 14.0446 | 12.8128 | 12.2157 | 12.138 | 12.311 | 11.9356 | 11.8169 | 11.5645 | 11.5064 | 11.3681 | 11.0421 | 10.6428 | 10.3702 | 10.0672 | 9.7862 | 7.8784 | 3.6646 | 0.4136 | -1.7307 | 16.5726 | 16.4539 | 16.2015 | 16.1434 | 16.0051 | 15.6791 | 15.2798 | 15.0072 | 14.7042 | 14.4232 | 12.5154 | 8.3016 | 5.0506 | 2.9063 | 11.9549 | 11.8296 | 11.5808 | 11.5445 | 11.3963 | 11.0841 | 10.7313 | 10.535 | 10.088 | 9.0467 | 4.365 | 0.57759 | -1.4854 | -0.7352 | 16.5919 | 16.4666 | 16.4666 | 16.1815 | 16.0333 | 15.7211 | 15.3683 | 15.172 | 14.725 | 13.6837 | 9.002 | 5.2146 | 3.1516 | 3.9018 | 385569 | 434469 | BURNLEY | ROCHDALE
| Burnley Centre | 10.4429 | 10.1522 | 10.1069 | 10.0414 | 9.8554 | 9.5253 | 9.2849 | 9.1595 | 8.8534 | 8.6432 | 8.0206 | 7.5618 | 7.3515 | 7.3005 | 15.0799 | 14.7892 | 14.7439 | 14.6784 | 14.4924 | 14.1623 | 13.9219 | 13.7965 | 13.4904 | 13.2802 | 12.6576 | 12.1988 | 11.9885 | 11.9375 | 10.5778 | 10.4101 | 10.2106 | 10.0023 | 9.6817 | 9.2185 | 8.813 | 8.5491 | 7.9855 | 7.1244 | 6.8386 | 6.6657 | 6.5785 | 6.6044 | 15.2148 | 15.0471 | 14.8476 | 14.6393 | 14.3187 | 13.8555 | 13.45 | 13.1861 | 12.6225 | 11.7614 | 11.4756 | 11.3027 | 11.2155 | 11.2414 | 10.4548 | 10.297 | 10.1476 | 10.097 | 10.0004 | 9.7229 | 9.4277 | 9.2853 | 9.1784 | 8.8783 | 8.2629 | 7.8504 | 7.6603 | 7.6063 | 15.0918 | 14.934 | 14.7846 | 14.734 | 14.6374 | 14.3599 | 14.0647 | 13.9223 | 13.8154 | 13.5153 | 12.8999 | 12.4874 | 12.2973 | 12.2433 | 10.4468 | 10.1731 | 10.1143 | 10.0464 | 9.9052 | 9.5872 | 9.2996 | 9.1255 | 8.9521 | 8.6732 | 7.4933 | 3.9773 | 1.053 | -0.8157 | 15.0838 | 14.8101 | 14.7513 | 14.6834 | 14.5422 | 14.2242 | 13.9366 | 13.7625 | 13.5891 | 13.3102 | 12.1303 | 8.6143 | 5.69 | 3.8213 | 10.4812 | 10.2353 | 10.2014 | 10.1761 | 10.1069 | 9.8531 | 9.5907 | 9.4749 | 9.3222 | 8.4984 | 4.6937 | 1.4537 | -0.48742 | 0.13005 | 15.1182 | 14.8723 | 14.8723 | 14.8131 | 14.7439 | 14.4901 | 14.2277 | 14.1119 | 13.9592 | 13.1354 | 9.3307 | 6.0907 | 4.1496 | 4.767 | 384308 | 432288 | BURNLEY | ROCHDALE
| Burnley North | 3.124 | 2.9155 | 2.7903 | 2.5627 | 2.4014 | 2.2097 | 1.9006 | 1.6541 | 1.3264 | 0.88219 | -0.73229 | -1.8023 | -2.5151 | -3.1725 | 9.124 | 8.9155 | 8.7903 | 8.5627 | 8.4014 | 8.2097 | 7.9006 | 7.6541 | 7.3264 | 6.8822 | 5.2677 | 4.1977 | 3.4849 | 2.8275 | 3.3073 | 3.2497 | 3.0699 | 2.8158 | 2.6497 | 2.4704 | 2.1726 | 1.9405 | 1.6908 | 1.3944 | 0.24683 | -0.59513 | -0.95837 | -1.0992 | 9.3073 | 9.2497 | 9.0699 | 8.8158 | 8.6497 | 8.4704 | 8.1726 | 7.9405 | 7.6908 | 7.3944 | 6.2468 | 5.4049 | 5.0416 | 4.9008 | 3.1292 | 2.9251 | 2.8052 | 2.5845 | 2.4295 | 2.2449 | 1.9447 | 1.6618 | 1.3521 | 0.94703 | -0.5182 | -1.3621 | -1.5584 | -1.5165 | 9.1292 | 8.9251 | 8.8052 | 8.5845 | 8.4295 | 8.2449 | 7.9447 | 7.6618 | 7.3521 | 6.947 | 5.4818 | 4.6379 | 4.4416 | 4.4835 | 3.1357 | 2.9389 | 2.8253 | 2.6095 | 2.4626 | 2.2861 | 1.9928 | 1.7716 | 1.5546 | 1.2641 | -0.84701 | -5.3768 | -8.9886 | -11.0008 | 9.1357 | 8.9389 | 8.8253 | 8.6095 | 8.4626 | 8.2861 | 7.9928 | 7.7716 | 7.5546 | 7.2641 | 5.153 | 0.62319 | -2.9886 | -5.0008 | 3.1283 | 2.9035 | 2.7812 | 2.5764 | 2.4485 | 2.3032 | 2.0364 | 1.8529 | 1.5215 | 0.66801 | -2.9202 | -6.2733 | -8.8688 | -9.5651 | 9.1283 | 8.9035 | 8.9035 | 8.5764 | 8.4485 | 8.3032 | 8.0364 | 7.8529 | 7.5215 | 6.668 | 3.0798 | -0.27326 | -2.8688 | -3.5651 | 384418 | 434168 | BURNLEY | ROCHDALE
| Burrow Beck | 3.0638 | 1.9806 | 1.4707 | 1.1507 | 0.63338 | -0.049724 | -0.57264 | -1.1543 | -1.7647 | -2.5251 | -4.7208 | -6.3897 | -6.2226 | -4.9246 | 7.0638 | 5.9806 | 5.4707 | 5.1507 | 4.6334 | 3.9503 | 3.4274 | 2.8457 | 2.2353 | 1.4749 | -0.72084 | -2.3897 | -2.2226 | -0.92463 | 3.7634 | 3.2893 | 2.7483 | 2.3867 | 1.885 | 1.2524 | 0.75627 | 0.18568 | -0.42258 | -1.0862 | -2.5613 | -4.3885 | -4.9774 | -4.4445 | 7.7634 | 7.2893 | 6.7483 | 6.3867 | 5.885 | 5.2524 | 4.7563 | 4.1857 | 3.5774 | 2.9138 | 1.4387 | -0.38848 | -0.97743 | -0.44445 | 3.0729 | 1.9992 | 1.4988 | 1.1881 | 0.68427 | 0.017641 | -0.49137 | -1.0592 | -1.6465 | -2.3516 | -4.402 | -5.9783 | -5.8105 | -4.5573 | 7.0729 | 5.9992 | 5.4988 | 5.1881 | 4.6843 | 4.0176 | 3.5086 | 2.9408 | 2.3535 | 1.6484 | -0.40196 | -1.9783 | -1.8105 | -0.55735 | 3.1138 | 2.0814 | 1.6337 | 1.3875 | 0.95364 | 0.3678 | -0.069954 | -0.54894 | -0.99631 | -1.4882 | -3.3732 | -7.1113 | -9.4715 | -10.1988 | 7.1138 | 6.0814 | 5.6337 | 5.3875 | 4.9536 | 4.3678 | 3.93 | 3.4511 | 3.0037 | 2.5118 | 0.62683 | -3.1113 | -5.4715 | -6.1988 | 2.9659 | 1.8183 | 1.3746 | 1.1546 | 0.72571 | 0.18119 | -0.19852 | -0.59101 | -0.9993 | -1.7959 | -5.8567 | -9.4578 | -10.8181 | -9.0754 | 6.9659 | 5.8183 | 5.8183 | 5.1546 | 4.7257 | 4.1812 | 3.8015 | 3.409 | 3.0007 | 2.2041 | -1.8567 | -5.4578 | -6.8181 | -5.0754 | 347903 | 458401 | LANCASTER | HEYSHAM
| Burscough Bridge | 5.0198 | 3.7641 | 3.0305 | 2.6099 | 2.3231 | 1.8706 | 1.4167 | 0.91561 | 0.45746 | -0.20748 | -2.5326 | -3.9802 | -4.4761 | -4.536 | 8.5198 | 7.2641 | 6.5305 | 6.1099 | 5.8231 | 5.3706 | 4.9167 | 4.4156 | 3.9575 | 3.2925 | 0.96736 | -0.48016 | -0.97609 | -1.036 | 5.6337 | 4.9719 | 4.4421 | 4.1105 | 3.9076 | 3.5559 | 3.1992 | 2.7967 | 2.401 | 1.9487 | 0.64706 | -0.49645 | -1.3232 | -1.9379 | 9.1337 | 8.4719 | 7.9421 | 7.6105 | 7.4076 | 7.0559 | 6.6992 | 6.2967 | 5.901 | 5.4487 | 4.1471 | 3.0035 | 2.1768 | 1.5621 | 5.0246 | 3.7788 | 3.057 | 2.6537 | 2.3835 | 1.95 | 1.5147 | 1.0322 | 0.5958 | -0.0086668 | -2.06 | -3.1396 | -3.4803 | -3.3392 | 8.5246 | 7.2788 | 6.557 | 6.1537 | 5.8835 | 5.45 | 5.0147 | 4.5322 | 4.0958 | 3.4913 | 1.44 | 0.36038 | 0.019744 | 0.16077 | 5.0319 | 3.7654 | 3.0261 | 2.6192 | 2.3314 | 1.8521 | 1.3334 | 0.75469 | 0.27919 | -0.27097 | -2.7901 | -6.3021 | -8.2664 | -9.7355 | 8.5319 | 7.2654 | 6.5261 | 6.1192 | 5.8314 | 5.3521 | 4.8334 | 4.2547 | 3.7792 | 3.229 | 0.70992 | -2.8021 | -4.7664 | -6.2355 | 4.9987 | 3.6702 | 2.9222 | 2.5256 | 2.2487 | 1.803 | 1.3301 | 0.8192 | 0.40835 | -0.46673 | -4.5138 | -7.342 | -8.4957 | -8.0534 | 8.4987 | 7.1702 | 7.1702 | 6.0256 | 5.7487 | 5.303 | 4.8301 | 4.3192 | 3.9084 | 3.0333 | -1.0138 | -3.842 | -4.9957 | -4.5534 | 344595 | 412486 | WRIGHTINGTON | PENWORTHAM
| Bury Town Centre | 9.247 | 8.6627 | 8.703 | 8.29 | 8.1928 | 7.8391 | 7.4954 | 7.2307 | 6.6656 | 6.2298 | 4.6679 | 3.8033 | 3.356 | 3.3724 | 13.384 | 12.7997 | 12.84 | 12.427 | 12.3298 | 11.9761 | 11.6324 | 11.3677 | 10.8026 | 10.3668 | 8.8049 | 7.9403 | 7.493 | 7.5094 | 9.5641 | 9.1247 | 9.0432 | 8.5607 | 8.5255 | 8.0722 | 7.7057 | 7.4383 | 6.8133 | 5.8221 | 5.2561 | 4.8854 | 4.402 | 4.2163 | 13.7011 | 13.2617 | 13.1802 | 12.6977 | 12.6625 | 12.2092 | 11.8427 | 11.5753 | 10.9503 | 9.9591 | 9.3931 | 9.0224 | 8.539 | 8.3533 | 9.1878 | 8.6688 | 8.7212 | 8.3374 | 8.2408 | 7.8793 | 7.5588 | 7.2512 | 6.7071 | 6.3113 | 4.8861 | 4.1269 | 3.7253 | 3.7577 | 13.3248 | 12.8058 | 12.8582 | 12.4744 | 12.3778 | 12.0163 | 11.6958 | 11.3882 | 10.8441 | 10.4483 | 9.0231 | 8.2639 | 7.8623 | 7.8947 | 9.2615 | 8.6906 | 8.7384 | 8.3264 | 8.2277 | 7.8728 | 7.5163 | 7.1602 | 6.5679 | 6.1323 | 3.9447 | 0.053748 | -3.2797 | -5.3528 | 13.3985 | 12.8276 | 12.8754 | 12.4634 | 12.3647 | 12.0098 | 11.6533 | 11.2972 | 10.7049 | 10.2693 | 8.0817 | 4.1907 | 0.85726 | -1.2158 | 9.2481 | 8.665 | 8.7185 | 8.3493 | 8.27 | 7.9302 | 7.6046 | 7.2988 | 6.6844 | 5.6521 | 1.158 | -2.4096 | -4.6031 | -3.899 | 13.3851 | 12.802 | 12.802 | 12.4863 | 12.407 | 12.0672 | 11.7416 | 11.4358 | 10.8214 | 9.7891 | 5.295 | 1.7274 | -0.46606 | 0.23795 | 380863 | 410807 | BURY | KEARSLEY
| Campbell St | 6.668 | 5.9815 | 5.9547 | 5.712 | 5.6517 | 5.2783 | 4.9929 | 10.1561 | 9.8048 | 9.3281 | 7.2032 | 5.3672 | 4.117 | 3.3501 | 10.168 | 9.4815 | 9.4547 | 9.212 | 9.1517 | 8.7783 | 8.4929 | 8.2561 | 7.9048 | 7.4281 | 5.3032 | 3.4672 | 2.217 | 1.4501 | 7.0326 | 6.6625 | 6.5501 | 6.2638 | 6.1842 | 5.8258 | 5.543 | 10.702 | 10.345 | 9.9317 | 8.2756 | 6.8929 | 6.268 | 6.0861 | 10.5326 | 10.1625 | 10.0501 | 9.7638 | 9.6842 | 9.3258 | 9.043 | 8.802 | 8.445 | 8.0317 | 6.3756 | 4.9929 | 4.368 | 4.1861 | 6.6787 | 6.0054 | 5.9886 | 5.7564 | 5.7062 | 5.3477 | 5.0764 | 10.2535 | 9.9235 | 9.5149 | 7.5965 | 6.2412 | 5.7758 | 5.7687 | 10.1787 | 9.5054 | 9.4886 | 9.2564 | 9.2062 | 8.8477 | 8.5764 | 8.3535 | 8.0235 | 7.6149 | 5.6965 | 4.3412 | 3.8758 | 3.8687 | 6.6879 | 6.0255 | 6.0224 | 5.8047 | 5.7752 | 5.4355 | 5.1676 | 10.3416 | 9.9832 | 9.5314 | 6.8374 | 2.3262 | -3.0014 | -6.1734 | 10.1879 | 9.5255 | 9.5224 | 9.3047 | 9.2752 | 8.9355 | 8.6676 | 8.4416 | 8.0832 | 7.6314 | 4.9374 | 0.42624 | -4.9014 | -8.0734 | 6.6805 | 5.9844 | 5.9681 | 5.7556 | 5.736 | 5.4153 | 5.1621 | 10.1753 | 9.6625 | 8.8652 | 4.2229 | -0.32328 | -3.4799 | -4.6304 | 10.1805 | 9.4844 | 9.4844 | 9.2556 | 9.236 | 8.9153 | 8.6621 | 8.2753 | 7.7625 | 6.9652 | 2.3229 | -2.2233 | -5.3799 | -6.5304 | 372937 | 406428 | KEARSLEY LOCAL | KEARSLEY
| Cannon St | 9.8782 | 8.754 | 8.5399 | 8.4105 | 8.2624 | 8.0125 | 7.7699 | 7.5144 | 7.2018 | 7.0139 | 6.2587 | 5.9268 | 5.8831 | 6.0711 | 30.8782 | 29.754 | 29.5399 | 29.4105 | 29.2624 | 29.0125 | 28.7699 | 28.5144 | 28.2018 | 28.0139 | 27.2587 | 26.9268 | 26.8831 | 27.0711 | 10.8142 | 10.5368 | 10.1506 | 9.8145 | 9.3728 | 8.8643 | 8.3552 | 7.7445 | 7.0193 | 6.3231 | 5.6839 | 5.3873 | 5.3022 | 5.5258 | 31.8142 | 31.5368 | 31.1506 | 30.8145 | 30.3728 | 29.8643 | 29.3552 | 28.7445 | 28.0193 | 27.3231 | 26.6839 | 26.3873 | 26.3022 | 26.5258 | 9.888 | 8.7751 | 8.5734 | 8.4566 | 8.3209 | 8.084 | 7.8548 | 7.6136 | 7.318 | 7.1505 | 6.4184 | 6.101 | 6.0619 | 6.2484 | 30.888 | 29.7751 | 29.5734 | 29.4566 | 29.3209 | 29.084 | 28.8548 | 28.6136 | 28.318 | 28.1505 | 27.4184 | 27.101 | 27.0619 | 27.2484 | 9.9201 | 8.8395 | 8.6677 | 8.5814 | 8.4692 | 8.2597 | 8.0573 | 7.8421 | 7.5732 | 7.4425 | 6.7649 | 5.4045 | 4.4065 | 3.9082 | 30.9201 | 29.8395 | 29.6677 | 29.5814 | 29.4692 | 29.2597 | 29.0573 | 28.8421 | 28.5732 | 28.4425 | 27.7649 | 26.4045 | 25.4065 | 24.9082 | 9.9246 | 8.8437 | 8.6843 | 8.6165 | 8.5265 | 8.3449 | 8.1701 | 7.9885 | 7.7628 | 7.3736 | 5.5382 | 4.2246 | 3.5491 | 4.2384 | 30.9246 | 29.8437 | 29.8437 | 29.6165 | 29.5265 | 29.3449 | 29.1701 | 28.9885 | 28.7628 | 28.3736 | 26.5382 | 25.2246 | 24.5491 | 25.2384 | 384064 | 398635 | RED BANK | WHITEGATE
| Capontree | 15.595 | 15.2136 | 15.0558 | 14.816 | 14.6628 | 14.3656 | 14.0658 | 13.8711 | 13.5527 | 13.1155 | 11.4403 | 10.2451 | 9.5773 | 9.4725 | 19.732 | 19.3506 | 19.1928 | 18.953 | 18.7998 | 18.5026 | 18.2028 | 18.0081 | 17.6897 | 17.2525 | 15.5773 | 14.3821 | 13.7143 | 13.6095 | 15.7127 | 15.4437 | 15.275 | 15.0779 | 14.9553 | 14.6874 | 14.4118 | 14.2305 | 13.9213 | 13.6156 | 12.7472 | 11.7348 | 10.8468 | 10.2575 | 19.8497 | 19.5807 | 19.412 | 19.2149 | 19.0923 | 18.8244 | 18.5488 | 18.3675 | 18.0583 | 17.7526 | 16.8842 | 15.8718 | 14.9838 | 14.3945 | 15.6004 | 15.2386 | 15.0986 | 14.8771 | 14.7387 | 14.4584 | 14.1745 | 13.992 | 13.6969 | 13.3072 | 11.8481 | 10.9403 | 10.432 | 10.4884 | 19.7374 | 19.3756 | 19.2356 | 19.0141 | 18.8757 | 18.5954 | 18.3115 | 18.129 | 17.8339 | 17.4442 | 15.9851 | 15.0773 | 14.569 | 14.6254 | 15.5994 | 15.1941 | 15.0068 | 14.7384 | 14.5348 | 14.1535 | 13.7263 | 13.3968 | 12.9888 | 12.5811 | 10.5661 | 7.702 | 5.9438 | 4.6549 | 19.7364 | 19.3311 | 19.1438 | 18.8754 | 18.6718 | 18.2905 | 17.8633 | 17.5338 | 17.1258 | 16.7181 | 14.7031 | 11.839 | 10.0808 | 8.7919 | 15.5977 | 15.1805 | 14.9955 | 14.7293 | 14.5145 | 14.1399 | 13.7406 | 13.4495 | 13.0634 | 12.3556 | 9.0036 | 6.5942 | 5.4751 | 5.6662 | 19.7347 | 19.3175 | 19.3175 | 18.8663 | 18.6515 | 18.2769 | 17.8776 | 17.5865 | 17.2004 | 16.4926 | 13.1406 | 10.7312 | 9.6121 | 9.8032 | 352906 | 559671 | CARLISLE | HARKER
| Carleton | 2.9549 | 2.849 | 2.7566 | 2.6428 | 2.5447 | 2.4099 | 2.2603 | 2.126 | 1.9755 | 1.7599 | 1.0516 | 0.73945 | 0.67399 | 0.7303 | 5.4549 | 5.349 | 5.2566 | 5.1428 | 5.0447 | 4.9099 | 4.7603 | 4.626 | 4.4755 | 4.2599 | 3.5516 | 3.2394 | 3.174 | 3.2303 | 3.0149 | 2.9613 | 2.8591 | 2.7607 | 2.6789 | 2.5606 | 2.427 | 2.3045 | 2.1745 | 2.0232 | 1.6442 | 1.2342 | 0.92032 | 0.76248 | 5.5149 | 5.4613 | 5.3591 | 5.2607 | 5.1789 | 5.0606 | 4.927 | 4.8045 | 4.6745 | 4.5232 | 4.1442 | 3.7342 | 3.4203 | 3.2625 | 2.9572 | 2.8555 | 2.7681 | 2.6597 | 2.5659 | 2.4363 | 2.2918 | 2.1618 | 2.0195 | 1.8257 | 1.1769 | 0.91071 | 0.85835 | 1.0264 | 5.4572 | 5.3555 | 5.2681 | 5.1597 | 5.0659 | 4.9363 | 4.7918 | 4.6618 | 4.5195 | 4.3257 | 3.6769 | 3.4107 | 3.3584 | 3.5264 | 2.9573 | 2.8458 | 2.7496 | 2.6365 | 2.5319 | 2.3886 | 2.2252 | 2.0859 | 1.9549 | 1.815 | 1.0996 | 0.36321 | 0.0024184 | -0.17635 | 5.4573 | 5.3458 | 5.2496 | 5.1365 | 5.0319 | 4.8886 | 4.7252 | 4.5859 | 4.4549 | 4.315 | 3.5996 | 2.8632 | 2.5024 | 2.3237 | 2.9427 | 2.8064 | 2.7007 | 2.5838 | 2.465 | 2.3207 | 2.1679 | 2.0468 | 1.9353 | 1.7622 | 1.0821 | 0.64735 | 0.48287 | 0.47883 | 5.4427 | 5.3064 | 5.3064 | 5.0838 | 4.965 | 4.8207 | 4.6679 | 4.5468 | 4.4353 | 4.2622 | 3.5821 | 3.1474 | 2.9829 | 2.9788 | 308796 | 498305 | EGREMONT | HARKER
| Carlisle North | 10.0156 | 7.7089 | 6.6879 | 6.5994 | 6.5513 | 6.2271 | 6.0081 | 6.0242 | 5.6769 | 5.4408 | 4.5693 | 3.0333 | 2.0135 | 0.75641 | 30.5156 | 28.2089 | 27.1879 | 27.0994 | 27.0513 | 26.7271 | 26.5081 | 26.5242 | 26.1769 | 25.9408 | 25.0693 | 23.5333 | 22.5135 | 21.2564 | 11.297 | 10.2102 | 9.5238 | 9.3153 | 9.1629 | 8.8001 | 8.5084 | 8.4056 | 7.9696 | 7.6208 | 7.0139 | 6.0771 | 5.2547 | 4.5577 | 31.797 | 30.7102 | 30.0238 | 29.8153 | 29.6629 | 29.3001 | 29.0084 | 28.9056 | 28.4696 | 28.1208 | 27.5139 | 26.5771 | 25.7547 | 25.0577 | 10.0237 | 7.7272 | 6.7155 | 6.6356 | 6.5956 | 6.2834 | 6.0756 | 6.1 | 5.7693 | 5.5575 | 4.8971 | 4.036 | 3.3433 | 2.7229 | 30.5237 | 28.2272 | 27.2155 | 27.1356 | 27.0956 | 26.7834 | 26.5756 | 26.6 | 26.2693 | 26.0575 | 25.3971 | 24.536 | 23.8433 | 23.2229 | 10.0406 | 7.7603 | 6.7651 | 6.7014 | 6.6771 | 6.3531 | 6.1085 | 6.0762 | 5.663 | 5.3511 | 3.4217 | 0.66553 | -0.93912 | -2.2736 | 30.5406 | 28.2603 | 27.2651 | 27.2014 | 27.1771 | 26.8531 | 26.6085 | 26.5762 | 26.163 | 25.8511 | 23.9217 | 21.1655 | 19.5609 | 18.2264 | 10.0358 | 7.7354 | 6.7289 | 6.6642 | 6.6378 | 6.2859 | 5.9781 | 5.8634 | 5.3395 | 4.8163 | 2.2573 | -0.34995 | -1.9261 | -1.7291 | 30.5358 | 28.2354 | 28.2354 | 27.1642 | 27.1378 | 26.7859 | 26.4781 | 26.3634 | 25.8395 | 25.3163 | 22.7573 | 20.15 | 18.5739 | 18.7709 | 338547 | 560280 | - | HARKER
| Carr St | 8.1165 | 7.662 | 7.3181 | 6.9378 | 6.5029 | 5.9588 | 5.3733 | 4.8218 | 4.254 | 3.6153 | 1.198 | -0.30837 | -0.91342 | -1.241 | 12.2535 | 11.799 | 11.4551 | 11.0748 | 10.6399 | 10.0958 | 9.5103 | 8.9588 | 8.391 | 7.7523 | 5.335 | 3.8286 | 3.2236 | 2.896 | 8.3479 | 8.1003 | 7.6785 | 7.2893 | 6.8813 | 6.3809 | 5.8338 | 5.3177 | 4.7745 | 4.2058 | 2.1728 | 0.68956 | -0.2075 | -0.85819 | 12.4849 | 12.2373 | 11.8155 | 11.4263 | 11.0183 | 10.5179 | 9.9708 | 9.4547 | 8.9115 | 8.3428 | 6.3098 | 4.8266 | 3.9295 | 3.2788 | 8.1282 | 7.6973 | 7.3765 | 7.0127 | 6.6047 | 6.0893 | 5.5329 | 5.0094 | 4.4774 | 3.9013 | 1.7605 | 0.53814 | 0.053344 | -0.18074 | 12.2652 | 11.8343 | 11.5135 | 11.1497 | 10.7417 | 10.2263 | 9.6699 | 9.1464 | 8.6144 | 8.0383 | 5.8975 | 4.6751 | 4.1903 | 3.9563 | 8.1355 | 7.7025 | 7.3778 | 7.0015 | 6.6196 | 6.1329 | 5.6015 | 5.1049 | 4.6451 | 4.1568 | 0.98578 | -4.8227 | -9.3109 | -12.3264 | 12.2725 | 11.8395 | 11.5148 | 11.1385 | 10.7566 | 10.2699 | 9.7385 | 9.2419 | 8.7821 | 8.2938 | 5.1228 | -0.68565 | -5.1739 | -8.1894 | 8.1382 | 7.671 | 7.3356 | 6.9787 | 6.6418 | 6.2145 | 5.7273 | 5.2833 | 4.7096 | 3.316 | -3.2987 | -8.5739 | -11.6014 | -11.0336 | 12.2752 | 11.808 | 11.808 | 11.1157 | 10.7788 | 10.3515 | 9.8643 | 9.4203 | 8.8466 | 7.453 | 0.83827 | -4.4369 | -7.4644 | -6.8966 | 376984 | 401329 | KEARSLEY LOCAL | KEARSLEY
| Castleton | 6.2422 | 5.7514 | 5.3474 | 5.2757 | 5.0744 | 4.6435 | 4.1159 | 3.8489 | 3.5949 | 3.0919 | 1.6804 | 0.80714 | 0.46956 | 0.36639 | 10.8792 | 10.3884 | 9.9844 | 9.9127 | 9.7114 | 9.2805 | 8.7529 | 8.4859 | 8.2319 | 7.7289 | 6.3174 | 5.4441 | 5.1066 | 5.0034 | 6.6846 | 6.576 | 6.0897 | 5.9571 | 5.7248 | 5.3241 | 4.8101 | 4.5357 | 4.2409 | 3.7878 | 2.6196 | 1.7368 | 1.1657 | 0.87868 | 11.3216 | 11.213 | 10.7267 | 10.5941 | 10.3618 | 9.9611 | 9.4471 | 9.1727 | 8.8779 | 8.4248 | 7.2566 | 6.3738 | 5.8027 | 5.5157 | 6.251 | 5.7674 | 5.373 | 5.3077 | 5.148 | 4.694 | 4.1774 | 3.9188 | 3.6983 | 3.2107 | 2.0362 | 1.376 | 1.1011 | 1.0173 | 10.888 | 10.4044 | 10.01 | 9.9447 | 9.785 | 9.331 | 8.8144 | 8.5558 | 8.3353 | 7.8477 | 6.6732 | 6.013 | 5.7381 | 5.6543 | 6.2673 | 5.8 | 5.4181 | 5.3625 | 5.2209 | 4.7761 | 4.2538 | 3.9796 | 3.7704 | 3.3113 | 1.3705 | -2.9654 | -6.3472 | -8.5858 | 10.9043 | 10.437 | 10.0551 | 9.9995 | 9.8579 | 9.4131 | 8.8908 | 8.6166 | 8.4074 | 7.9483 | 6.0075 | 1.6716 | -1.7102 | -3.9488 | 6.2109 | 5.7125 | 5.3392 | 5.3004 | 5.1763 | 4.7539 | 4.2464 | 3.9923 | 3.686 | 2.4602 | -2.3743 | -6.3257 | -8.5552 | -7.8691 | 10.8479 | 10.3495 | 10.3495 | 9.9374 | 9.8133 | 9.3909 | 8.8834 | 8.6293 | 8.323 | 7.0972 | 2.2627 | -1.6887 | -3.9182 | -3.2321 | 388461 | 411290 | CASTLETON | ROCHDALE
| Catterall Waterworks | -3.0084 | -3.2661 | -3.2107 | -3.2866 | -3.3965 | -3.5308 | -3.6503 | -3.707 | -3.8615 | -4.025 | -4.4799 | -4.7925 | -4.8849 | -4.9461 | -0.50838 | -0.7661 | -0.71071 | -0.78655 | -0.89652 | -1.0308 | -1.1503 | -1.207 | -1.3615 | -1.525 | -1.9799 | -2.2925 | -2.3849 | -2.4461 | -2.8298 | -2.9376 | -2.9473 | -3.046 | -3.1658 | -3.2913 | -3.4079 | -3.4672 | -3.6325 | -3.7778 | -4.0704 | -4.3572 | -4.5319 | -4.6293 | -0.32985 | -0.43759 | -0.44725 | -0.54598 | -0.66584 | -0.79126 | -0.90792 | -0.96723 | -1.1325 | -1.2778 | -1.5704 | -1.8572 | -2.0319 | -2.1293 | -3.0072 | -3.263 | -3.2064 | -3.2805 | -3.3885 | -3.5204 | -3.6376 | -3.6923 | -3.8431 | -3.9995 | -4.4241 | -4.675 | -4.7395 | -4.7183 | -0.50715 | -0.76298 | -0.70635 | -0.78054 | -0.88845 | -1.0204 | -1.1376 | -1.1923 | -1.3431 | -1.4995 | -1.9241 | -2.175 | -2.2395 | -2.2183 | -2.9935 | -3.2416 | -3.1775 | -3.2403 | -3.3425 | -3.4765 | -3.6047 | -3.675 | -3.835 | -3.9739 | -4.4419 | -5.3429 | -6.0211 | -6.371 | -0.49348 | -0.74156 | -0.6775 | -0.74035 | -0.84253 | -0.97648 | -1.1047 | -1.175 | -1.335 | -1.4739 | -1.9419 | -2.8429 | -3.5211 | -3.871 | -2.9964 | -3.2471 | -3.1805 | -3.2418 | -3.3429 | -3.4727 | -3.5954 | -3.6572 | -3.804 | -4.0488 | -5.0204 | -5.7933 | -6.2218 | -5.9531 | -0.49636 | -0.74708 | -0.74708 | -0.74181 | -0.84292 | -0.97267 | -1.0954 | -1.1572 | -1.304 | -1.5488 | -2.5204 | -3.2933 | -3.7218 | -3.4531 | 349381 | 442178 | RIBBLE | PENWORTHAM
| Cecil St | 8.4796 | 8.0949 | 7.9525 | 7.7182 | 7.5084 | 7.2705 | 6.9101 | 6.5893 | 6.2836 | 5.8572 | 5.3351 | 5.1362 | 5.3295 | 5.6345 | 13.6696 | 13.2849 | 13.1425 | 12.9082 | 12.6984 | 12.4605 | 12.1001 | 11.7793 | 11.4736 | 11.0472 | 10.5251 | 10.3262 | 10.5195 | 10.8245 | 8.6838 | 8.4929 | 8.01 | 7.4761 | 6.9852 | 6.4497 | 5.7283 | 4.9853 | 4.1828 | 3.1675 | 2.7953 | 2.5937 | 2.6065 | 2.6896 | 13.8738 | 13.6829 | 13.2 | 12.6661 | 12.1752 | 11.6397 | 10.9183 | 10.1753 | 9.3728 | 8.3575 | 7.9853 | 7.7837 | 7.7965 | 7.8796 | 8.4976 | 8.1331 | 8.0115 | 7.9121 | 7.707 | 7.4577 | 7.2066 | 6.9867 | 6.6999 | 6.4227 | 5.744 | 5.4981 | 5.6889 | 5.9809 | 13.6876 | 13.3231 | 13.2015 | 13.1021 | 12.897 | 12.6477 | 12.3966 | 12.1767 | 11.8899 | 11.6127 | 10.934 | 10.6881 | 10.8789 | 11.1709 | 8.4975 | 8.1337 | 8.0192 | 7.829 | 7.6576 | 7.464 | 7.1571 | 6.8972 | 6.6613 | 6.3219 | 5.2005 | 0.42665 | -3.2521 | -5.7428 | 13.6875 | 13.3237 | 13.2092 | 13.019 | 12.8476 | 12.654 | 12.3471 | 12.0872 | 11.8513 | 11.5119 | 10.3905 | 5.6167 | 1.9379 | -0.55277 | 8.5333 | 8.1842 | 8.1014 | 8.0718 | 7.9412 | 7.7901 | 7.6367 | 7.5313 | 7.3303 | 6.5033 | 1.142 | -3.1952 | -5.5546 | -4.5719 | 13.7233 | 13.3742 | 13.3742 | 13.2618 | 13.1312 | 12.9801 | 12.8267 | 12.7213 | 12.5203 | 11.6933 | 6.332 | 1.9948 | -0.36456 | 0.61807 | 331301 | 437023 | BLACKPOOL | PENWORTHAM
| Central Manchester | 11.1186 | 9.9952 | 7.5094 | 5.2777 | -0.64907 | -8.7666 | -17.2248 | -0.38174 | -2.4636 | -2.9107 | -3.4044 | -3.6566 | -3.7242 | -3.4367 | 20.1186 | 18.9952 | 16.5094 | 14.2777 | 8.3509 | 0.2334 | -8.2248 | -10.3817 | -12.4636 | -12.9107 | -13.4044 | -13.6566 | -13.7242 | -13.4367 | 11.9862 | 11.6345 | 9.0997 | 6.7213 | 0.6619 | -7.5246 | -16.0674 | -18.3355 | -20.5698 | -21.1361 | -21.6493 | -22.0312 | -22.214 | -21.9858 | 20.9862 | 20.6345 | 18.0997 | 15.7213 | 9.6619 | 1.4754 | -7.0674 | -9.3355 | -11.5698 | -12.1361 | -12.6493 | -13.0312 | -13.214 | -12.9858 | 11.125 | 10.0118 | 7.5393 | 5.32 | -0.59771 | -8.7047 | -17.15 | -19.2952 | -21.3641 | -21.7912 | -22.2611 | -22.4974 | -22.5592 | -22.274 | 20.125 | 19.0118 | 16.5393 | 14.32 | 8.4023 | 0.29532 | -8.15 | -10.2952 | -12.3641 | -12.7912 | -13.2611 | -13.4974 | -13.5592 | -13.274 | 11.1533 | 10.0625 | 7.6085 | 5.4074 | -0.50024 | -8.5991 | -17.0402 | -19.1833 | -21.2469 | -21.6636 | -22.1234 | -23.1316 | -23.8423 | -24.01 | 20.1533 | 19.0625 | 16.6085 | 14.4074 | 8.4998 | 0.40095 | -8.0402 | -10.1833 | -12.2469 | -12.6636 | -13.1234 | -14.1316 | -14.8423 | -15.01 | 11.1591 | 10.0697 | 7.6275 | 5.4454 | -0.44138 | -8.5141 | -16.9283 | -19.0401 | -21.0615 | -21.658 | -22.9704 | -23.9098 | -24.3655 | -23.6413 | 20.1591 | 19.0697 | 19.0697 | 14.4454 | 8.5586 | 0.48595 | -7.9283 | -10.0401 | -12.0615 | -12.658 | -13.9704 | -14.9098 | -15.3655 | -14.6413 | 384852 | 397718 | STUART ST | STALYBRIDGE
| Chadderton | 23.1249 | 22.6879 | 22.5692 | 22.4342 | 22.1678 | 21.8806 | 21.5694 | 21.3309 | 20.974 | 20.649 | 19.2768 | 17.9605 | 16.2462 | 14.8423 | 30.1249 | 29.6879 | 29.5692 | 29.4342 | 29.1678 | 28.8806 | 28.5694 | 28.3309 | 27.974 | 27.649 | 26.2768 | 24.9605 | 23.2462 | 21.8423 | 23.4275 | 23.2444 | 23.0308 | 22.8303 | 22.5337 | 22.2441 | 21.9223 | 21.6887 | 21.3001 | 20.9706 | 20.0976 | 19.3049 | 18.5726 | 18.0299 | 30.4275 | 30.2444 | 30.0308 | 29.8303 | 29.5337 | 29.2441 | 28.9223 | 28.6887 | 28.3001 | 27.9706 | 27.0976 | 26.3049 | 25.5726 | 25.0299 | 23.1348 | 22.6956 | 22.5798 | 22.4272 | 22.1564 | 21.8743 | 21.569 | 21.3354 | 20.9886 | 20.6875 | 19.4617 | 18.5756 | 17.9782 | 17.1204 | 30.1348 | 29.6956 | 29.5798 | 29.4272 | 29.1564 | 28.8743 | 28.569 | 28.3354 | 27.9886 | 27.6875 | 26.4617 | 25.5756 | 24.9782 | 24.1204 | 23.142 | 22.7233 | 22.6227 | 22.5057 | 22.2442 | 21.9582 | 21.6348 | 21.374 | 20.9945 | 20.6606 | 18.5001 | 14.1117 | 10.0419 | 7.3962 | 30.142 | 29.7233 | 29.6227 | 29.5057 | 29.2442 | 28.9582 | 28.6348 | 28.374 | 27.9945 | 27.6606 | 25.5001 | 21.1117 | 17.0419 | 14.3962 | 23.1389 | 22.697 | 22.5888 | 22.4543 | 22.2009 | 21.9258 | 21.5946 | 21.3267 | 20.9061 | 20.2748 | 15.5872 | 10.9203 | 8.1722 | 8.473 | 30.1389 | 29.697 | 29.697 | 29.4543 | 29.2009 | 28.9258 | 28.5946 | 28.3267 | 27.9061 | 27.2748 | 22.5872 | 17.9203 | 15.1722 | 15.473 | 389161 | 403872 | CHADDERTON | WHITEGATE
| Chamberhall | 4.2932 | 3.5146 | 3.6068 | 2.9475 | 2.8276 | 2.1346 | 1.5801 | 1.1726 | 0.38727 | -0.25099 | -2.51 | -3.8332 | -4.4157 | -4.8431 | 9.6132 | 8.8346 | 8.9268 | 8.2675 | 8.1476 | 7.4546 | 6.9001 | 6.4926 | 5.7073 | 5.069 | 2.81 | 1.4868 | 0.90434 | 0.47686 | 4.4384 | 3.7966 | 3.7627 | 3.1014 | 3.0115 | 2.3629 | 1.8424 | 1.4586 | 0.69071 | 0.12535 | -1.4835 | -2.5929 | -3.491 | -3.9416 | 9.7584 | 9.1166 | 9.0827 | 8.4214 | 8.3315 | 7.6829 | 7.1624 | 6.7786 | 6.0107 | 5.4453 | 3.8365 | 2.7271 | 1.829 | 1.3784 | 4.2956 | 3.5566 | 3.6554 | 3.0203 | 2.9181 | 2.2523 | 1.7211 | 1.3328 | 0.58345 | 0.0093677 | -2.021 | -3.0182 | -3.6053 | -3.8455 | 9.6156 | 8.8766 | 8.9754 | 8.3403 | 8.2381 | 7.5723 | 7.0411 | 6.6528 | 5.9034 | 5.3294 | 3.299 | 2.3018 | 1.7147 | 1.4745 | 4.2993 | 3.5295 | 3.6328 | 2.9863 | 2.8903 | 2.2179 | 1.6709 | 1.2695 | 0.54712 | 0.041386 | -3.5124 | -10.2484 | -16.0891 | -19.8965 | 9.6193 | 8.8495 | 8.9528 | 8.3063 | 8.2103 | 7.5379 | 6.9909 | 6.5895 | 5.8671 | 5.3614 | 1.8076 | -4.9284 | -10.7691 | -14.5765 | 4.2991 | 3.4973 | 3.6142 | 3.0313 | 3.0035 | 2.4219 | 1.9506 | 1.632 | 0.82067 | -0.84349 | -8.6564 | -14.8336 | -18.6586 | -17.768 | 9.6191 | 8.8173 | 8.8173 | 8.3513 | 8.3235 | 7.7419 | 7.2706 | 6.952 | 6.1407 | 4.4765 | -3.3364 | -9.5136 | -13.3386 | -12.448 | 380280 | 411215 | BURY | KEARSLEY
| Chapel Wharf | 15.1741 | 14.2115 | 13.9142 | 13.8098 | 13.8148 | 13.7329 | 13.6493 | 13.6041 | 13.4991 | 13.3966 | 13.0743 | 12.831 | 12.6547 | 12.614 | 19.8111 | 18.8485 | 18.5512 | 18.4468 | 18.4518 | 18.3699 | 18.2863 | 18.2411 | 18.1361 | 18.0336 | 17.7113 | 17.468 | 17.2917 | 17.251 | 15.6643 | 15.1827 | 14.9915 | 14.8601 | 14.8264 | 14.7259 | 14.6168 | 14.5368 | 14.4023 | 14.2807 | 14.0336 | 13.7805 | 13.5715 | 13.4084 | 20.3013 | 19.8197 | 19.6285 | 19.4971 | 19.4634 | 19.3629 | 19.2538 | 19.1738 | 19.0393 | 18.9177 | 18.6706 | 18.4175 | 18.2085 | 18.0454 | 15.1768 | 14.2215 | 13.9308 | 13.8321 | 13.8415 | 13.7645 | 13.6857 | 13.6451 | 13.5466 | 13.4544 | 13.161 | 12.9415 | 12.7808 | 12.7423 | 19.8138 | 18.8585 | 18.5678 | 18.4691 | 18.4785 | 18.4015 | 18.3227 | 18.2821 | 18.1836 | 18.0914 | 17.798 | 17.5785 | 17.4178 | 17.3793 | 15.183 | 14.2275 | 13.9365 | 13.8355 | 13.8396 | 13.7506 | 13.6477 | 13.5813 | 13.4634 | 13.3648 | 12.9813 | 12.2512 | 11.5154 | 10.9464 | 19.82 | 18.8645 | 18.5735 | 18.4725 | 18.4766 | 18.3876 | 18.2847 | 18.2183 | 18.1004 | 18.0018 | 17.6183 | 16.8882 | 16.1524 | 15.5834 | 15.1924 | 14.245 | 13.9612 | 13.8686 | 13.8729 | 13.789 | 13.6993 | 13.6467 | 13.5354 | 13.338 | 12.5153 | 11.7565 | 11.2118 | 11.2721 | 19.8294 | 18.882 | 18.882 | 18.5056 | 18.5099 | 18.426 | 18.3363 | 18.2837 | 18.1724 | 17.975 | 17.1523 | 16.3935 | 15.8488 | 15.9091 | 383499 | 398634 | FREDERICK RD | KEARSLEY
| Chassen Rd | 2.5333 | 2.2108 | 1.7621 | 1.1694 | 1.1761 | 0.64013 | -0.018056 | -0.42326 | -1.0622 | -1.5352 | -3.6454 | -4.7479 | -4.971 | -4.7035 | 13.4333 | 13.1108 | 12.6621 | 12.0694 | 12.0761 | 11.5401 | 10.8819 | 10.4767 | 9.8378 | 9.3648 | 7.2546 | 6.1521 | 5.929 | 6.1965 | 2.7608 | 2.6249 | 2.0831 | 1.4934 | 1.5284 | 1.0431 | 0.42859 | 0.053595 | -0.55079 | -0.91388 | -2.4203 | -3.6425 | -4.345 | -4.7675 | 13.6608 | 13.5249 | 12.9831 | 12.3934 | 12.4284 | 11.9431 | 11.3286 | 10.9536 | 10.3492 | 9.9861 | 8.4797 | 7.2575 | 6.555 | 6.1325 | 2.5419 | 2.2343 | 1.804 | 1.228 | 1.245 | 0.727 | 0.087796 | -0.30316 | -0.91464 | -1.3291 | -3.2347 | -4.1947 | -4.3666 | -4.1119 | 13.4419 | 13.1343 | 12.704 | 12.128 | 12.145 | 11.627 | 10.9878 | 10.5968 | 9.9854 | 9.5709 | 7.6653 | 6.7053 | 6.5334 | 6.7881 | 2.5537 | 2.253 | 1.8349 | 1.2782 | 1.3375 | 0.85412 | 0.21358 | -0.17019 | -0.71216 | -1.0044 | -3.8284 | -9.8435 | -14.4685 | -17.6093 | 13.4537 | 13.153 | 12.7349 | 12.1782 | 12.2375 | 11.7541 | 11.1136 | 10.7298 | 10.1878 | 9.8956 | 7.0716 | 1.0565 | -3.5685 | -6.7093 | 2.5393 | 2.1787 | 1.7407 | 1.1924 | 1.2435 | 0.78692 | 0.20348 | -0.1047 | -0.75566 | -2.0824 | -8.8766 | -14.3055 | -17.3327 | -16.3839 | 13.4393 | 13.0787 | 13.0787 | 12.0924 | 12.1435 | 11.6869 | 11.1035 | 10.7953 | 10.1443 | 8.8176 | 2.0234 | -3.4055 | -6.4327 | -5.4839 | 375542 | 394453 | BARTON | CARRINGTON
| Chatsworth St | 6.2773 | 5.9565 | 6.0274 | 5.8299 | 5.7728 | 5.412 | 5.1393 | 4.9952 | 4.6892 | 4.4348 | 3.5237 | 3.0595 | 2.9684 | 3.189 | 13.6773 | 13.3565 | 13.4274 | 13.2299 | 13.1728 | 12.812 | 12.5393 | 12.3952 | 12.0892 | 11.8348 | 10.9237 | 10.4595 | 10.3684 | 10.589 | 6.4172 | 6.249 | 6.192 | 5.9299 | 5.847 | 5.4643 | 5.1549 | 4.9333 | 4.5948 | 4.3118 | 3.7697 | 3.4049 | 3.221 | 3.238 | 13.8172 | 13.649 | 13.592 | 13.3299 | 13.247 | 12.8643 | 12.5549 | 12.3333 | 11.9948 | 11.7118 | 11.1697 | 10.8049 | 10.621 | 10.638 | 6.2876 | 5.9909 | 6.0768 | 5.8971 | 5.8549 | 5.5142 | 5.2594 | 5.1136 | 4.8469 | 4.6275 | 3.8066 | 3.4167 | 3.3579 | 3.5914 | 13.6876 | 13.3909 | 13.4768 | 13.2971 | 13.2549 | 12.9142 | 12.6594 | 12.5136 | 12.2469 | 12.0275 | 11.2066 | 10.8167 | 10.7579 | 10.9914 | 6.2783 | 5.956 | 6.0244 | 5.8242 | 5.7578 | 5.3814 | 5.0811 | 4.8892 | 4.5957 | 4.3842 | 2.5201 | -2.5093 | -6.6488 | -9.2799 | 13.6783 | 13.356 | 13.4244 | 13.2242 | 13.1578 | 12.7814 | 12.4811 | 12.2892 | 11.9957 | 11.7842 | 9.9201 | 4.8907 | 0.75121 | -1.8799 | 6.3355 | 6.0409 | 6.137 | 5.9898 | 5.9762 | 5.6686 | 5.4313 | 5.334 | 4.9263 | 3.7429 | -1.8392 | -6.438 | -9.1847 | -8.1306 | 13.7355 | 13.4409 | 13.4409 | 13.3898 | 13.3762 | 13.0686 | 12.8313 | 12.734 | 12.3263 | 11.1429 | 5.5608 | 0.96195 | -1.7847 | -0.73056 | 319188 | 470003 | BARROW & SANDGATE | HARKER
| Cheadle Heath | 5.2163 | 5.1164 | 4.8695 | 4.7062 | 4.453 | 4.2471 | 3.6853 | 3.5204 | 3.3963 | 2.9865 | 1.8784 | 1.2874 | 1.0266 | 1.0822 | 8.7163 | 8.6164 | 8.3695 | 8.2062 | 7.953 | 7.7471 | 7.1853 | 7.0204 | 6.8963 | 6.4865 | 5.3784 | 4.7874 | 4.5266 | 4.5822 | 5.3199 | 5.2992 | 4.9929 | 4.8197 | 4.5822 | 4.3999 | 3.8624 | 3.7164 | 3.6015 | 3.2374 | 2.4003 | 1.8126 | 1.3437 | 1.136 | 8.8199 | 8.7992 | 8.4929 | 8.3197 | 8.0822 | 7.8999 | 7.3624 | 7.2164 | 7.1015 | 6.7374 | 5.9003 | 5.3126 | 4.8437 | 4.636 | 5.2214 | 5.1286 | 4.8907 | 4.7333 | 4.4881 | 4.2901 | 3.7392 | 3.5808 | 3.4677 | 3.0903 | 2.1013 | 1.6394 | 1.4293 | 1.5389 | 8.7214 | 8.6286 | 8.3907 | 8.2333 | 7.9881 | 7.7901 | 7.2392 | 7.0808 | 6.9677 | 6.5903 | 5.6013 | 5.1394 | 4.9293 | 5.0389 | 5.2272 | 5.1436 | 4.9219 | 4.7856 | 4.573 | 4.4143 | 3.9038 | 3.7874 | 3.7448 | 3.4555 | 1.8342 | -1.8925 | -5.0543 | -7.0361 | 8.7272 | 8.6436 | 8.4219 | 8.2856 | 8.073 | 7.9143 | 7.4038 | 7.2874 | 7.2448 | 6.9555 | 5.3342 | 1.6075 | -1.5543 | -3.5361 | 5.2324 | 5.1322 | 4.9198 | 4.8225 | 4.6522 | 4.5451 | 4.0803 | 4.0097 | 3.8877 | 2.9335 | -1.1843 | -4.5484 | -6.684 | -6.0693 | 8.7324 | 8.6322 | 8.6322 | 8.3225 | 8.1522 | 8.0451 | 7.5803 | 7.5097 | 7.3877 | 6.4335 | 2.3157 | -1.0484 | -3.184 | -2.5693 | 387062 | 389054 | ADSWOOD | BREDBURY
| Cheadle Hulme | 6.8751 | 6.5794 | 6.1191 | 5.7658 | 5.6172 | 5.0529 | 4.2254 | 3.8119 | 3.3805 | 2.6716 | 0.71892 | 0.062463 | 0.113 | 0.8355 | 11.5121 | 11.2164 | 10.7561 | 10.4028 | 10.2542 | 9.6899 | 8.8624 | 8.4489 | 8.0175 | 7.3086 | 5.3559 | 4.6995 | 4.75 | 5.4725 | 7.3771 | 7.4743 | 6.8308 | 6.4569 | 6.3085 | 5.8011 | 5.0194 | 4.6357 | 4.2151 | 3.576 | 1.9606 | 0.99189 | 0.42917 | 0.46721 | 12.0141 | 12.1113 | 11.4678 | 11.0939 | 10.9455 | 10.4381 | 9.6564 | 9.2727 | 8.8521 | 8.213 | 6.5976 | 5.6289 | 5.0662 | 5.1042 | 6.8824 | 6.6012 | 6.1585 | 5.797 | 5.6594 | 5.109 | 4.2962 | 3.8937 | 3.4828 | 2.8321 | 1.0655 | 0.51197 | 0.58199 | 1.2726 | 11.5194 | 11.2382 | 10.7955 | 10.434 | 10.2964 | 9.746 | 8.9332 | 8.5307 | 8.1198 | 7.4691 | 5.7025 | 5.149 | 5.219 | 5.9096 | 6.9337 | 6.7107 | 6.3432 | 6.1035 | 6.085 | 5.6822 | 5.0336 | 4.8069 | 4.6243 | 4.2246 | 2.0668 | -2.6357 | -6.4459 | -8.5776 | 11.5707 | 11.3477 | 10.9802 | 10.7405 | 10.722 | 10.3192 | 9.6706 | 9.4439 | 9.2613 | 8.8616 | 6.7038 | 2.0013 | -1.8089 | -3.9406 | 6.9339 | 6.6528 | 6.2805 | 6.0478 | 6.0868 | 5.7732 | 5.205 | 5.0782 | 4.8226 | 3.5498 | -1.9387 | -6.1541 | -8.5388 | -6.962 | 11.5709 | 11.2898 | 11.2898 | 10.6848 | 10.7238 | 10.4102 | 9.842 | 9.7152 | 9.4596 | 8.1868 | 2.6983 | -1.5171 | -3.9018 | -2.325 | 387386 | 386308 | ADSWOOD | BREDBURY
| Cheetham Hill | 2.9901 | 2.5861 | 2.4425 | 2.059 | 1.9073 | 1.5094 | 1.0871 | 0.66072 | 0.24723 | -0.26708 | -2.114 | -3.2423 | -3.8255 | -3.7567 | 5.6997 | 5.2957 | 5.1521 | 4.7685 | 4.6168 | 4.219 | 3.7966 | 3.3703 | 2.9568 | 2.4425 | 0.59557 | -0.53272 | -1.1159 | -1.0472 | 3.141 | 2.8584 | 2.5963 | 2.1877 | 2.0273 | 1.6281 | 1.1864 | 0.7295 | 0.21904 | -0.24102 | -1.532 | -2.7029 | -3.5786 | -4.0459 | 5.8505 | 5.568 | 5.3059 | 4.8972 | 4.7368 | 4.3377 | 3.8959 | 3.439 | 2.9286 | 2.4685 | 1.1775 | 0.0066559 | -0.86904 | -1.3363 | 3.0029 | 2.6328 | 2.5216 | 2.1636 | 2.0375 | 1.6679 | 1.2736 | 0.8753 | 0.49671 | 0.045097 | -1.5795 | -2.5412 | -3.0352 | -2.9472 | 5.7125 | 5.3424 | 5.2311 | 4.8732 | 4.747 | 4.3774 | 3.9832 | 3.5848 | 3.2063 | 2.7546 | 1.1301 | 0.16836 | -0.32565 | -0.23765 | 3.0068 | 2.6123 | 2.4745 | 2.0818 | 1.9288 | 1.4998 | 0.99305 | 0.47695 | 0.025419 | -0.44398 | -2.9725 | -7.822 | -11.5075 | -13.8094 | 5.7163 | 5.3218 | 5.184 | 4.7913 | 4.6384 | 4.2093 | 3.7026 | 3.1865 | 2.735 | 2.2656 | -0.26292 | -5.1125 | -8.798 | -11.0999 | 3.0299 | 2.6387 | 2.5177 | 2.153 | 2.0038 | 1.6079 | 1.1687 | 0.73013 | 0.24223 | -1.0069 | -6.6722 | -11.0059 | -13.4775 | -12.6017 | 5.7395 | 5.3483 | 5.3483 | 4.8625 | 4.7133 | 4.3174 | 3.8782 | 3.4397 | 2.9518 | 1.7026 | -3.9627 | -8.2964 | -10.7679 | -9.8922 | 383606 | 402218 | AGECROFT | KEARSLEY
| Chester Rd T11 & T12 | 5.1571 | 3.595 | 3.2006 | 3.1079 | 2.9835 | 2.7607 | 2.614 | 2.4953 | 2.3027 | 2.173 | 1.4294 | 0.74171 | 0.27169 | -0.17599 | 10.1571 | 8.595 | 8.2006 | 8.1079 | 7.9835 | 7.7607 | 7.614 | 7.4953 | 7.3027 | 7.173 | 6.4294 | 5.7417 | 5.2717 | 4.824 | 6.0181 | 5.2934 | 5.0381 | 4.8875 | 4.7299 | 4.5109 | 4.3482 | 4.2048 | 3.9915 | 3.8419 | 3.2679 | 2.7459 | 2.3009 | 1.9662 | 11.0181 | 10.2934 | 10.0381 | 9.8875 | 9.7299 | 9.5109 | 9.3482 | 9.2048 | 8.9915 | 8.8419 | 8.2679 | 7.7459 | 7.3009 | 6.9662 | 5.1596 | 3.6004 | 3.2077 | 3.1174 | 2.9957 | 2.7764 | 2.6329 | 2.5173 | 2.3299 | 2.2106 | 1.5459 | 1.0657 | 0.69548 | 0.4351 | 10.1596 | 8.6004 | 8.2077 | 8.1174 | 7.9957 | 7.7764 | 7.6329 | 7.5173 | 7.3299 | 7.2106 | 6.5459 | 6.0657 | 5.6955 | 5.4351 | 5.1737 | 3.6293 | 3.2514 | 3.1748 | 3.0648 | 2.8486 | 2.6956 | 2.5633 | 2.3564 | 2.2218 | 1.087 | -0.66569 | -1.9084 | -2.7976 | 10.1737 | 8.6293 | 8.2514 | 8.1748 | 8.0648 | 7.8486 | 7.6956 | 7.5633 | 7.3564 | 7.2218 | 6.087 | 4.3343 | 3.0916 | 2.2024 | 5.1675 | 3.6097 | 3.2271 | 3.1514 | 3.0395 | 2.8186 | 2.6531 | 2.5046 | 2.2595 | 1.8953 | -0.070149 | -1.6712 | -2.6613 | -2.379 | 10.1675 | 8.6097 | 8.6097 | 8.1514 | 8.0395 | 7.8186 | 7.6531 | 7.5046 | 7.2595 | 6.8953 | 4.9299 | 3.3288 | 2.3387 | 2.621 | 381030 | 396165 | STRETFORD | SOUTH MANCHESTER
| Chester Rd T13 | 8.6283 | 8.4391 | 8.3473 | 8.3223 | 8.2555 | 8.1662 | 8.0523 | 7.9991 | 7.9143 | 7.813 | 7.4698 | 7.284 | 7.204 | 7.206 | 13.3783 | 13.1891 | 13.0973 | 13.0723 | 13.0055 | 12.9162 | 12.8023 | 12.7491 | 12.6643 | 12.563 | 12.2198 | 12.034 | 11.954 | 11.956 | 8.7672 | 8.6969 | 8.5886 | 8.5371 | 8.4538 | 8.356 | 8.2292 | 8.1568 | 8.0505 | 7.9348 | 7.7 | 7.5245 | 7.411 | 7.3534 | 13.5172 | 13.4469 | 13.3386 | 13.2871 | 13.2038 | 13.106 | 12.9792 | 12.9068 | 12.8005 | 12.6848 | 12.45 | 12.2745 | 12.161 | 12.1034 | 8.6314 | 8.4457 | 8.3582 | 8.3364 | 8.274 | 8.1903 | 8.0803 | 8.0326 | 7.9545 | 7.8637 | 7.5474 | 7.3802 | 7.3075 | 7.3074 | 13.3814 | 13.1957 | 13.1082 | 13.0864 | 13.024 | 12.9403 | 12.8303 | 12.7826 | 12.7045 | 12.6137 | 12.2974 | 12.1302 | 12.0575 | 12.0574 | 8.6338 | 8.4501 | 8.3641 | 8.3435 | 8.2797 | 8.1918 | 8.0698 | 8.0108 | 7.9246 | 7.8326 | 7.4477 | 6.8809 | 6.488 | 6.2335 | 13.3838 | 13.2001 | 13.1141 | 13.0935 | 13.0297 | 12.9418 | 12.8198 | 12.7608 | 12.6746 | 12.5826 | 12.1977 | 11.6309 | 11.238 | 10.9835 | 8.6326 | 8.4439 | 8.3588 | 8.3423 | 8.2789 | 8.1974 | 8.0867 | 8.0424 | 7.9692 | 7.8037 | 7.0986 | 6.609 | 6.3633 | 6.4914 | 13.3826 | 13.1939 | 13.1939 | 13.0923 | 13.0289 | 12.9474 | 12.8367 | 12.7924 | 12.7192 | 12.5537 | 11.8486 | 11.359 | 11.1133 | 11.2414 | 381040 | 396175 | STRETFORD | SOUTH MANCHESTER
| Chorley South | 1.9311 | 1.2 | 0.86494 | 0.29722 | -0.1948 | -0.96212 | -1.6413 | 3.1803 | 2.4332 | 1.569 | -1.5263 | -3.2975 | -3.7745 | -3.692 | 5.4311 | 4.7 | 4.3649 | 3.7972 | 3.3052 | 2.5379 | 1.8587 | 1.1803 | 0.43319 | -0.431 | -3.5263 | -5.2975 | -5.7745 | -5.692 | 2.1846 | 1.6912 | 1.2773 | 0.75171 | 0.326 | -0.35587 | -0.95893 | 3.9311 | 3.2164 | 2.5178 | 0.34539 | -1.3006 | -2.1935 | -2.8433 | 5.6846 | 5.1912 | 4.7773 | 4.2517 | 3.826 | 3.1441 | 2.5411 | 1.9311 | 1.2164 | 0.51775 | -1.6546 | -3.3006 | -4.1935 | -4.8433 | 1.9357 | 1.247 | 0.95256 | 0.4138 | -0.040469 | -0.76527 | -1.4044 | 3.4566 | 2.7604 | 1.981 | -0.79392 | -2.3258 | -2.7058 | -2.5699 | 5.4357 | 4.747 | 4.4526 | 3.9138 | 3.4595 | 2.7347 | 2.0956 | 1.4566 | 0.76042 | -0.018955 | -2.7939 | -4.3258 | -4.7058 | -4.5699 | 1.955 | 1.2283 | 0.89011 | 0.31787 | -0.1434 | -0.89171 | -1.5808 | 3.2213 | 2.5318 | 1.852 | -1.5314 | -7.3619 | -11.4061 | -14.458 | 5.455 | 4.7283 | 4.3901 | 3.8179 | 3.3566 | 2.6083 | 1.9192 | 1.2213 | 0.53175 | -0.14801 | -3.5314 | -9.3619 | -13.4061 | -16.458 | 1.93 | 1.1473 | 0.8016 | 0.23433 | -0.19279 | -0.8704 | -1.4716 | 3.4527 | 2.7762 | 1.308 | -5.3896 | -10.3708 | -13.0035 | -12.3911 | 5.43 | 4.6473 | 4.6473 | 3.7343 | 3.3072 | 2.6296 | 2.0284 | 1.4527 | 0.77618 | -0.692 | -7.3896 | -12.3708 | -15.0035 | -14.3911 | 358658 | 417041 | WRIGHTINGTON | PENWORTHAM
| Chorlton | 4.6458 | 4.4178 | 4.2095 | 3.9885 | 3.6988 | 3.3898 | 3.0162 | 1.6897 | 1.381 | 0.99538 | -0.29924 | -0.84959 | -0.89806 | -0.72538 | 10.6458 | 10.4178 | 10.2095 | 9.9885 | 9.6988 | 9.3898 | 9.0162 | 8.6897 | 8.381 | 7.9954 | 6.7008 | 6.1504 | 6.1019 | 6.2746 | 4.7266 | 4.5684 | 4.3401 | 4.1515 | 3.9102 | 3.6464 | 3.3163 | 3.0266 | 2.7489 | 2.4331 | 1.4602 | 0.82762 | 0.49019 | 0.30731 | 10.7266 | 10.5684 | 10.3401 | 10.1515 | 9.9102 | 9.6464 | 9.3163 | 9.0266 | 8.7489 | 8.4331 | 7.4602 | 6.8276 | 6.4902 | 6.3073 | 4.6521 | 4.4383 | 4.2444 | 4.0333 | 3.757 | 3.4615 | 3.1015 | 2.7872 | 2.496 | 2.1501 | 0.99179 | 0.52581 | 0.48719 | 0.65547 | 10.6521 | 10.4383 | 10.2444 | 10.0333 | 9.757 | 9.4615 | 9.1015 | 8.7872 | 8.496 | 8.1501 | 6.9918 | 6.5258 | 6.4872 | 6.6555 | 4.6553 | 4.4361 | 4.2426 | 4.0364 | 3.7743 | 3.4916 | 3.1357 | 2.8312 | 2.5843 | 2.3037 | 0.77917 | -1.8068 | -3.5633 | -4.627 | 10.6553 | 10.4361 | 10.2426 | 10.0364 | 9.7743 | 9.4916 | 9.1357 | 8.8312 | 8.5843 | 8.3037 | 6.7792 | 4.1932 | 2.4367 | 1.373 | 4.5941 | 4.3194 | 4.1307 | 3.9474 | 3.7045 | 3.4593 | 3.1454 | 2.896 | 2.6442 | 1.9423 | -1.2608 | -3.496 | -4.5474 | -3.8775 | 10.5941 | 10.3194 | 10.3194 | 9.9474 | 9.7045 | 9.4593 | 9.1454 | 8.896 | 8.6442 | 7.9423 | 4.7392 | 2.504 | 1.4526 | 2.1225 | 381411 | 393754 | WEST DIDSBURY | SOUTH MANCHESTER
| Church | 1.1357 | 1.0821 | 1.0437 | 0.97375 | 0.88154 | 0.77138 | 0.65044 | 0.51644 | 0.37185 | 0.20209 | -0.44818 | -1.0242 | -1.3122 | -1.4681 | 12.1357 | 12.0821 | 12.0437 | 11.9738 | 11.8815 | 11.7714 | 11.6504 | 11.5164 | 11.3719 | 11.2021 | 10.5518 | 9.9758 | 9.6878 | 9.5319 | 1.1622 | 1.1254 | 1.0515 | 0.97088 | 0.87591 | 0.76575 | 0.6428 | 0.50364 | 0.35435 | 0.20081 | -0.22111 | -0.53519 | -0.74952 | -0.91678 | 12.1622 | 12.1254 | 12.0515 | 11.9709 | 11.8759 | 11.7657 | 11.6428 | 11.5036 | 11.3544 | 11.2008 | 10.7789 | 10.4648 | 10.2505 | 10.0832 | 1.1391 | 1.0907 | 1.0577 | 0.99247 | 0.9057 | 0.80124 | 0.68606 | 0.56329 | 0.42848 | 0.27489 | -0.31017 | -0.74488 | -0.94354 | -1.0002 | 12.1391 | 12.0907 | 12.0577 | 11.9925 | 11.9057 | 11.8012 | 11.6861 | 11.5633 | 11.4285 | 11.2749 | 10.6898 | 10.2551 | 10.0565 | 9.9998 | 1.1378 | 1.086 | 1.0515 | 0.98667 | 0.9024 | 0.79933 | 0.6814 | 0.55313 | 0.43509 | 0.30895 | -0.90424 | -3.5864 | -5.7348 | -7.0026 | 12.1378 | 12.086 | 12.0515 | 11.9867 | 11.9024 | 11.7993 | 11.6814 | 11.5531 | 11.4351 | 11.3089 | 10.0958 | 7.4136 | 5.2652 | 3.9974 | 1.159 | 1.1175 | 1.0926 | 1.0498 | 0.9884 | 0.91007 | 0.81033 | 0.69999 | 0.50438 | -0.11497 | -3.0341 | -5.483 | -6.866 | -6.4023 | 12.159 | 12.1175 | 12.1175 | 12.0498 | 11.9884 | 11.9101 | 11.8103 | 11.7 | 11.5044 | 10.885 | 7.9659 | 5.517 | 4.134 | 4.5977 | 374687 | 428919 | HUNCOAT | PADIHAM
| Circle Sq | 15.8816 | 12.4489 | 9.0183 | 6.723 | 6.7151 | 6.7091 | 6.6995 | 6.6856 | 6.6802 | 6.6691 | 6.6407 | 6.6107 | 6.6177 | 6.6126 | 20.5216 | 17.0889 | 13.6583 | 11.363 | 11.3551 | 11.3491 | 11.3395 | 11.3256 | 11.3202 | 11.3091 | 11.2807 | 11.2507 | 11.2577 | 11.2526 | 17.0172 | 15.2907 | 13.564 | 12.4072 | 12.3922 | 12.3755 | 12.3551 | 12.3303 | 12.3074 | 12.2793 | 12.2627 | 12.2452 | 12.2463 | 12.2395 | 21.6572 | 19.9307 | 18.204 | 17.0472 | 17.0322 | 17.0155 | 16.9951 | 16.9703 | 16.9474 | 16.9193 | 16.9027 | 16.8852 | 16.8863 | 16.8795 | 15.8356 | 12.4073 | 8.9781 | 6.687 | 6.6777 | 6.6637 | 6.6665 | 6.6578 | 6.6518 | 6.6444 | 6.6174 | 6.587 | 6.5946 | 6.5911 | 20.4756 | 17.0473 | 13.6181 | 11.327 | 11.3177 | 11.3037 | 11.3065 | 11.2978 | 11.2918 | 11.2844 | 11.2574 | 11.227 | 11.2346 | 11.2311 | 15.881 | 12.4461 | 9.0129 | 6.7144 | 6.7007 | 6.6872 | 6.6691 | 6.6455 | 6.6319 | 6.6129 | 6.5433 | 6.3862 | 6.2968 | 6.2098 | 20.521 | 17.0861 | 13.6529 | 11.3544 | 11.3407 | 11.3272 | 11.3091 | 11.2855 | 11.2719 | 11.2529 | 11.1833 | 11.0262 | 10.9368 | 10.8498 | 15.8817 | 12.4483 | 9.018 | 6.7228 | 6.7125 | 6.7029 | 6.6886 | 6.6694 | 6.6634 | 6.625 | 6.446 | 6.2969 | 6.2338 | 6.2514 | 20.5217 | 17.0883 | 17.0883 | 11.3628 | 11.3525 | 11.3429 | 11.3286 | 11.3094 | 11.3034 | 11.265 | 11.086 | 10.9369 | 10.8738 | 10.8914 | 384363 | 397283 | LONGSIGHT | BREDBURY
| Clarendon Rd | 10.7476 | 10.327 | 10.3138 | 9.8659 | 9.7683 | 9.2337 | 8.8646 | 8.5052 | 7.9758 | 7.389 | 5.6236 | 4.7595 | 4.563 | 4.7747 | 15.3846 | 14.964 | 14.9508 | 14.5029 | 14.4053 | 13.8707 | 13.5016 | 13.1422 | 12.6128 | 12.026 | 10.2606 | 9.3965 | 9.2 | 9.4117 | 10.8614 | 10.5319 | 10.4327 | 9.9744 | 9.896 | 9.4103 | 9.0556 | 8.7439 | 8.2578 | 7.7733 | 6.5627 | 5.69 | 5.0848 | 4.8212 | 15.4984 | 15.1689 | 15.0697 | 14.6114 | 14.533 | 14.0473 | 13.6926 | 13.3809 | 12.8948 | 12.4103 | 11.1997 | 10.327 | 9.7218 | 9.4582 | 10.7556 | 10.3528 | 10.3527 | 9.9213 | 9.8304 | 9.3236 | 8.975 | 8.6314 | 8.129 | 7.5977 | 5.9889 | 5.2621 | 5.1038 | 5.3608 | 15.3926 | 14.9898 | 14.9897 | 14.5583 | 14.4674 | 13.9606 | 13.612 | 13.2684 | 12.766 | 12.2347 | 10.6259 | 9.8991 | 9.7408 | 9.9978 | 10.7543 | 10.3387 | 10.3317 | 9.8873 | 9.8057 | 9.2813 | 9.0073 | 8.7372 | 8.3039 | 7.899 | 5.7395 | 1.104 | -2.665 | -5.0034 | 15.3913 | 14.9757 | 14.9687 | 14.5243 | 14.4427 | 13.9183 | 13.6443 | 13.3742 | 12.9409 | 12.536 | 10.3765 | 5.741 | 1.972 | -0.36636 | 10.7632 | 10.3341 | 10.3363 | 9.9269 | 9.8778 | 9.408 | 9.1884 | 8.9984 | 8.4697 | 7.2627 | 2.133 | -2.0058 | -4.5866 | -3.755 | 15.4002 | 14.9711 | 14.9711 | 14.5639 | 14.5148 | 14.045 | 13.8254 | 13.6354 | 13.1067 | 11.8997 | 6.77 | 2.6312 | 0.050352 | 0.88203 | 369051 | 429883 | BLACKBURN | PENWORTHAM
| Claughton | -0.19815 | -0.22697 | -0.26053 | -0.33386 | -0.42894 | -0.49195 | -0.58174 | -0.70928 | -0.76539 | -0.91407 | -1.5959 | -2.0625 | -2.3219 | -2.119 | 3.3019 | 3.273 | 3.2395 | 3.1661 | 3.0711 | 3.0081 | 2.9183 | 2.7907 | 2.7346 | 2.5859 | 1.9041 | 1.4375 | 1.1781 | 1.381 | -0.15596 | -0.14895 | -0.20871 | -0.27414 | -0.3633 | -0.41962 | -0.50563 | -0.6307 | -0.69092 | -0.78758 | -1.0924 | -1.5183 | -1.8748 | -1.9221 | 3.344 | 3.3511 | 3.2913 | 3.2259 | 3.1367 | 3.0804 | 2.9944 | 2.8693 | 2.8091 | 2.7124 | 2.4076 | 1.9817 | 1.6252 | 1.5779 | -0.19559 | -0.21899 | -0.24611 | -0.31293 | -0.40191 | -0.45998 | -0.5447 | -0.66661 | -0.71613 | -0.84877 | -1.4658 | -1.8713 | -2.1484 | -1.8836 | 3.3044 | 3.281 | 3.2539 | 3.1871 | 3.0981 | 3.04 | 2.9553 | 2.8334 | 2.7839 | 2.6512 | 2.0342 | 1.6287 | 1.3516 | 1.6164 | -0.19313 | -0.22622 | -0.26526 | -0.34283 | -0.45335 | -0.54304 | -0.67765 | -0.85673 | -0.9431 | -1.1446 | -1.7453 | -2.7226 | -3.3174 | -3.5246 | 3.3069 | 3.2738 | 3.2347 | 3.1572 | 3.0466 | 2.957 | 2.8224 | 2.6433 | 2.5569 | 2.3554 | 1.7547 | 0.7774 | 0.18264 | -0.024558 | -0.18667 | -0.21562 | -0.24669 | -0.31796 | -0.4293 | -0.60408 | -0.71225 | -0.85981 | -0.92105 | -1.1358 | -2.1822 | -2.9957 | -3.403 | -3.0918 | 3.3133 | 3.2844 | 3.2844 | 3.182 | 3.0707 | 2.8959 | 2.7877 | 2.6402 | 2.5789 | 2.3642 | 1.3178 | 0.50429 | 0.096984 | 0.40823 | 355872 | 466268 | LANCASTER | HEYSHAM
| Cleveleys | 4.6283 | 4.4565 | 4.2023 | 3.8302 | 3.4571 | 3.0229 | 2.5186 | 2.0078 | 1.4919 | 0.88834 | -1.1052 | -2.0706 | -2.2307 | -1.9624 | 8.1283 | 7.9565 | 7.7023 | 7.3302 | 6.9571 | 6.5229 | 6.0186 | 5.5078 | 4.9919 | 4.3883 | 2.3948 | 1.4294 | 1.2693 | 1.5376 | 4.6636 | 4.5144 | 4.2139 | 3.8459 | 3.5461 | 3.1559 | 2.6905 | 2.2148 | 1.7274 | 1.2165 | -0.22758 | -1.2744 | -1.8494 | -2.1991 | 8.1636 | 8.0144 | 7.7139 | 7.3459 | 7.0461 | 6.6559 | 6.1905 | 5.7148 | 5.2274 | 4.7165 | 3.2724 | 2.2256 | 1.6506 | 1.3009 | 4.6358 | 4.4825 | 4.2635 | 3.91 | 3.5596 | 3.1487 | 2.6677 | 2.1793 | 1.6949 | 1.1561 | -0.61323 | -1.429 | -1.5334 | -1.2643 | 8.1358 | 7.9825 | 7.7635 | 7.41 | 7.0596 | 6.6487 | 6.1677 | 5.6793 | 5.1949 | 4.6561 | 2.8868 | 2.071 | 1.9666 | 2.2357 | 4.6392 | 4.4796 | 4.2522 | 3.9036 | 3.5804 | 3.1943 | 2.7191 | 2.2493 | 1.836 | 1.4123 | -1.1501 | -6.3631 | -10.3914 | -13.1659 | 8.1392 | 7.9796 | 7.7522 | 7.4036 | 7.0804 | 6.6943 | 6.2191 | 5.7493 | 5.336 | 4.9123 | 2.3499 | -2.8631 | -6.8914 | -9.6659 | 4.6596 | 4.4667 | 4.2132 | 3.8886 | 3.5813 | 3.2447 | 2.837 | 2.4521 | 1.967 | 0.67796 | -5.2413 | -9.9415 | -12.5906 | -11.8074 | 8.1596 | 7.9667 | 7.9667 | 7.3886 | 7.0813 | 6.7447 | 6.337 | 5.9521 | 5.467 | 4.178 | -1.7413 | -6.4415 | -9.0906 | -8.3074 | 332286 | 443104 | BISPHAM | PENWORTHAM
| Clifton Junction | 7.3105 | 6.9168 | 6.8497 | 6.6847 | 6.561 | 6.3832 | 6.0703 | 5.7905 | 5.5122 | 5.2044 | 3.9006 | 2.9599 | 2.5089 | 2.1765 | 10.8105 | 10.4168 | 10.3497 | 10.1847 | 10.061 | 9.8832 | 9.5703 | 9.2905 | 9.0122 | 8.7044 | 7.4006 | 6.4599 | 6.0089 | 5.6765 | 7.5623 | 7.409 | 7.2631 | 7.0594 | 6.9162 | 6.7436 | 6.4552 | 6.1969 | 5.933 | 5.6606 | 4.6153 | 3.8014 | 3.275 | 2.9035 | 11.0623 | 10.909 | 10.7631 | 10.5594 | 10.4162 | 10.2436 | 9.9552 | 9.6969 | 9.433 | 9.1606 | 8.1153 | 7.3014 | 6.775 | 6.4035 | 7.3031 | 6.9059 | 6.8713 | 6.7118 | 6.5959 | 6.4002 | 6.0773 | 5.8007 | 5.5293 | 5.2421 | 4.048 | 3.2928 | 2.9219 | 2.7178 | 10.8031 | 10.4059 | 10.3713 | 10.2118 | 10.0959 | 9.9002 | 9.5773 | 9.3007 | 9.0293 | 8.7421 | 7.548 | 6.7928 | 6.4219 | 6.2178 | 7.3243 | 6.9472 | 6.8854 | 6.7211 | 6.6046 | 6.4246 | 6.1571 | 5.9075 | 5.6516 | 5.3704 | 3.6721 | 0.77539 | -1.4771 | -3.0083 | 10.8243 | 10.4472 | 10.3854 | 10.2211 | 10.1046 | 9.9246 | 9.6571 | 9.4075 | 9.1516 | 8.8704 | 7.1721 | 4.2754 | 2.0229 | 0.49166 | 7.3281 | 6.9426 | 6.8774 | 6.7151 | 6.6063 | 6.4318 | 6.1628 | 5.8899 | 5.5726 | 4.8906 | 1.6705 | -0.9985 | -2.5724 | -2.4739 | 10.8281 | 10.4426 | 10.4426 | 10.2151 | 10.1063 | 9.9318 | 9.6628 | 9.3899 | 9.0726 | 8.3906 | 5.1705 | 2.5015 | 0.92759 | 1.0261 | 379289 | 403073 | KEARSLEY LOCAL | KEARSLEY
| Clover Hill | 10.0298 | 9.8643 | 9.7449 | 9.5708 | 9.3757 | 9.1357 | 8.8721 | 8.5557 | 8.2034 | 7.8087 | 6.4505 | 5.7634 | 5.6704 | 5.8367 | 18.1298 | 17.9643 | 17.8449 | 17.6708 | 17.4757 | 17.2357 | 16.9721 | 16.6557 | 16.3034 | 15.9087 | 14.5505 | 13.8634 | 13.7704 | 13.9367 | 10.1021 | 9.9905 | 9.823 | 9.6443 | 9.4619 | 9.2413 | 8.9863 | 8.6921 | 8.3827 | 8.0717 | 7.2132 | 6.6433 | 6.3679 | 6.2163 | 18.2021 | 18.0905 | 17.923 | 17.7443 | 17.5619 | 17.3413 | 17.0863 | 16.7921 | 16.4827 | 16.1717 | 15.3132 | 14.7433 | 14.4679 | 14.3163 | 10.0366 | 9.8807 | 9.7709 | 9.6064 | 9.4226 | 9.1943 | 8.9423 | 8.6326 | 8.2983 | 7.9437 | 6.7095 | 6.1223 | 6.063 | 6.2309 | 18.1366 | 17.9807 | 17.8709 | 17.7064 | 17.5226 | 17.2943 | 17.0423 | 16.7326 | 16.3983 | 16.0437 | 14.8095 | 14.2223 | 14.163 | 14.3309 | 10.0343 | 9.8712 | 9.7565 | 9.588 | 9.4052 | 9.1741 | 8.9078 | 8.6253 | 8.3782 | 8.123 | 6.0399 | 1.0814 | -2.7921 | -5.1424 | 18.1343 | 17.9712 | 17.8565 | 17.688 | 17.5052 | 17.2741 | 17.0078 | 16.7253 | 16.4782 | 16.223 | 14.1399 | 9.1814 | 5.3079 | 2.9576 | 10.0558 | 9.8991 | 9.7987 | 9.664 | 9.5104 | 9.3237 | 9.1054 | 8.8788 | 8.4887 | 7.2819 | 1.7121 | -2.7296 | -5.1144 | -4.0089 | 18.1558 | 17.9991 | 17.9991 | 17.764 | 17.6104 | 17.4237 | 17.2054 | 16.9788 | 16.5887 | 15.3819 | 9.8121 | 5.3704 | 2.9856 | 4.0911 | 386638 | 437064 | NELSON | PADIHAM
| Cog Lane | 6.3155 | 5.5434 | 5.2049 | 4.9694 | 4.6912 | 4.3244 | 3.9312 | 3.5121 | 3.1089 | 2.6206 | 0.6217 | -0.68728 | -1.2007 | -1.4086 | 16.7404 | 15.9683 | 15.6298 | 15.3943 | 15.1161 | 14.7493 | 14.3561 | 13.937 | 13.5338 | 13.0455 | 11.0466 | 9.7376 | 9.2242 | 9.0163 | 6.7719 | 6.4041 | 6.0457 | 5.7506 | 5.443 | 5.0724 | 4.6641 | 4.2243 | 3.7648 | 3.2907 | 1.8564 | 0.72867 | 0.019419 | -0.49973 | 17.1968 | 16.829 | 16.4706 | 16.1755 | 15.8679 | 15.4973 | 15.089 | 14.6492 | 14.1897 | 13.7156 | 12.2813 | 11.1536 | 10.4443 | 9.9252 | 6.3305 | 5.5785 | 5.2598 | 5.0396 | 4.7811 | 4.4345 | 4.0616 | 3.6629 | 3.286 | 2.8444 | 1.0852 | 0.066385 | -0.31865 | -0.36501 | 16.7554 | 16.0034 | 15.6847 | 15.4645 | 15.206 | 14.8594 | 14.4865 | 14.0878 | 13.7109 | 13.2693 | 11.5101 | 10.4913 | 10.1062 | 10.0599 | 6.3263 | 5.5637 | 5.2318 | 4.992 | 4.7227 | 4.3516 | 3.9255 | 3.4616 | 3.0597 | 2.6355 | -0.56367 | -8.1218 | -14.0859 | -18.2631 | 16.7512 | 15.9886 | 15.6567 | 15.4169 | 15.1476 | 14.7765 | 14.3504 | 13.8865 | 13.4846 | 13.0604 | 9.8612 | 2.3031 | -3.661 | -7.8382 | 6.3835 | 5.6525 | 5.3476 | 5.1581 | 4.9359 | 4.622 | 4.2494 | 3.8394 | 3.2426 | 1.5 | -6.7327 | -13.6825 | -17.6832 | -16.838 | 16.8084 | 16.0774 | 16.0774 | 15.583 | 15.3608 | 15.0469 | 14.6743 | 14.2643 | 13.6675 | 11.9249 | 3.6922 | -3.2576 | -7.2583 | -6.4131 | 382462 | 432232 | HUNCOAT | PADIHAM
| Coniston | -0.72391 | -0.88482 | -0.91472 | -0.96687 | -1.0949 | -1.2029 | -1.3048 | -1.3571 | -1.4895 | -1.6314 | -2.1165 | -2.3495 | -2.4262 | -2.325 | 1.4761 | 1.3152 | 1.2853 | 1.2331 | 1.1051 | 0.99715 | 0.89524 | 0.84285 | 0.71055 | 0.56859 | 0.083482 | -0.14949 | -0.22616 | -0.12496 | -0.65556 | -0.75666 | -0.82013 | -0.887 | -1.0219 | -1.1443 | -1.2602 | -1.3196 | -1.4707 | -1.6088 | -1.8787 | -2.1459 | -2.3447 | -2.4555 | 1.5444 | 1.4433 | 1.3799 | 1.313 | 1.1781 | 1.0557 | 0.93975 | 0.88037 | 0.72929 | 0.59122 | 0.32133 | 0.054113 | -0.14475 | -0.25552 | -0.72043 | -0.87674 | -0.90353 | -0.96127 | -1.0843 | -1.1845 | -1.2834 | -1.3343 | -1.4602 | -1.5912 | -2.0533 | -2.275 | -2.3524 | -2.2574 | 1.4796 | 1.3233 | 1.2965 | 1.2387 | 1.1157 | 1.0155 | 0.91658 | 0.86568 | 0.7398 | 0.60875 | 0.14673 | -0.075027 | -0.15236 | -0.057396 | -0.72145 | -0.88306 | -0.91228 | -0.96164 | -1.09 | -1.2025 | -1.3088 | -1.3533 | -1.4706 | -1.565 | -2.0242 | -2.7485 | -3.2585 | -3.6076 | 1.4785 | 1.3169 | 1.2877 | 1.2384 | 1.11 | 0.99752 | 0.89125 | 0.84667 | 0.72943 | 0.63502 | 0.17583 | -0.54854 | -1.0585 | -1.4076 | -0.73716 | -0.91112 | -0.93404 | -0.98157 | -1.1111 | -1.209 | -1.3026 | -1.3385 | -1.4418 | -1.6499 | -2.5922 | -3.249 | -3.6082 | -3.4146 | 1.4628 | 1.2889 | 1.2889 | 1.2184 | 1.0889 | 0.991 | 0.89736 | 0.86151 | 0.75819 | 0.55015 | -0.39217 | -1.049 | -1.4082 | -1.2146 | 329874 | 497641 | ULVERSTON | HARKER
| Copse Rd | 6.9646 | 6.5364 | 6.2806 | 5.9637 | 5.7608 | 5.4514 | 5.0744 | 4.6669 | 4.3104 | 3.7501 | 1.4407 | 0.014944 | -0.45851 | -0.49111 | 11.6016 | 11.1734 | 10.9176 | 10.6007 | 10.3978 | 10.0884 | 9.7114 | 9.3039 | 8.9474 | 8.3871 | 6.0777 | 4.6519 | 4.1785 | 4.1459 | 7.2746 | 7.1082 | 6.7402 | 6.3589 | 6.1157 | 5.7906 | 5.384 | 4.865 | 4.1631 | 3.2753 | 2.3594 | 1.1305 | 0.41213 | -0.069502 | 11.9116 | 11.7452 | 11.3772 | 10.9959 | 10.7527 | 10.4276 | 10.021 | 9.502 | 8.8001 | 7.9123 | 6.9964 | 5.7675 | 5.0491 | 4.5675 | 6.9783 | 6.5725 | 6.341 | 6.0443 | 5.8634 | 5.5771 | 5.224 | 4.8413 | 4.515 | 4.0575 | 1.9286 | 0.70045 | 0.32671 | 0.35399 | 11.6153 | 11.2095 | 10.978 | 10.6813 | 10.5004 | 10.2141 | 9.861 | 9.4783 | 9.152 | 8.6945 | 6.5656 | 5.3375 | 4.9637 | 4.991 | 6.9799 | 6.5613 | 6.3071 | 5.9784 | 5.7654 | 5.4288 | 4.9883 | 4.5056 | 4.104 | 3.6252 | 0.85843 | -5.6751 | -10.8026 | -14.2965 | 11.6169 | 11.1983 | 10.9441 | 10.6154 | 10.4024 | 10.0658 | 9.6253 | 9.1426 | 8.741 | 8.2622 | 5.4954 | -1.0381 | -6.1656 | -9.6595 | 6.9927 | 6.5655 | 6.3163 | 6.0043 | 5.8007 | 5.4936 | 5.0974 | 4.6702 | 4.2041 | 2.8775 | -4.4231 | -10.3945 | -13.8368 | -12.9529 | 11.6297 | 11.2025 | 11.2025 | 10.6413 | 10.4377 | 10.1306 | 9.7344 | 9.3072 | 8.8411 | 7.5145 | 0.21385 | -5.7575 | -9.1998 | -8.3159 | 333013 | 446934 | THORNTON | STANAH
| Cox Green | 4.8899 | 4.1993 | 4.2959 | 3.525 | 3.6347 | 3.0591 | 2.5124 | 2.1638 | 1.4947 | 0.75706 | -1.1301 | -1.7239 | -1.6505 | -1.1064 | 9.1899 | 8.4993 | 8.5959 | 7.825 | 7.9347 | 7.3591 | 6.8124 | 6.4638 | 5.7947 | 5.0571 | 3.1699 | 2.5761 | 2.6495 | 3.1936 | 5.0101 | 4.4303 | 4.494 | 3.7817 | 4.0071 | 3.5433 | 3.1127 | 2.8712 | 2.3216 | 1.7759 | 0.46456 | -0.35241 | -0.88457 | -1.0395 | 9.3101 | 8.7303 | 8.794 | 8.0817 | 8.3071 | 7.8433 | 7.4127 | 7.1712 | 6.6216 | 6.0759 | 4.7646 | 3.9476 | 3.4154 | 3.2605 | 4.8923 | 4.2222 | 4.3334 | 3.5763 | 3.6804 | 3.119 | 2.5847 | 2.2447 | 1.5982 | 0.92149 | -0.76038 | -1.2411 | -1.1414 | -0.58031 | 9.1923 | 8.5222 | 8.6334 | 7.8763 | 7.9804 | 7.419 | 6.8847 | 6.5447 | 5.8982 | 5.2215 | 3.5396 | 3.0589 | 3.1586 | 3.7197 | 4.9088 | 4.246 | 4.3868 | 3.6775 | 3.8832 | 3.4179 | 2.9881 | 2.7732 | 2.3193 | 1.8837 | -0.070172 | -3.7366 | -6.4843 | -8.0664 | 9.2088 | 8.546 | 8.6868 | 7.9775 | 8.1832 | 7.7179 | 7.2881 | 7.0732 | 6.6193 | 6.1837 | 4.2298 | 0.56345 | -2.1843 | -3.7664 | 4.8447 | 4.0874 | 4.2245 | 3.5461 | 3.7528 | 3.3487 | 2.9834 | 2.8553 | 2.35 | 1.2501 | -3.1619 | -6.2876 | -8.016 | -6.8591 | 9.1447 | 8.3874 | 8.3874 | 7.8461 | 8.0528 | 7.6487 | 7.2834 | 7.1553 | 6.65 | 5.5501 | 1.1381 | -1.9876 | -3.716 | -2.5591 | 371893 | 413641 | BOLTON | KEARSLEY
| Craggs Row & Bushell St | 5.5866 | 5.2496 | 5.0146 | 4.6859 | 4.4131 | 4.096 | 3.652 | 3.2513 | 2.8655 | 2.3406 | 0.62092 | -0.22515 | -0.50697 | -0.17358 | 9.7266 | 9.3896 | 9.1546 | 8.8259 | 8.5531 | 8.236 | 7.792 | 7.3913 | 7.0055 | 6.4806 | 4.7609 | 3.9149 | 3.633 | 3.9664 | 5.8384 | 5.7074 | 5.3684 | 4.9919 | 4.6975 | 4.369 | 3.9018 | 3.4674 | 2.9995 | 2.4685 | 1.3209 | 0.43282 | -0.1589 | -0.33721 | 9.9784 | 9.8474 | 9.5084 | 9.1319 | 8.8375 | 8.509 | 8.0418 | 7.6074 | 7.1395 | 6.6085 | 5.4609 | 4.5728 | 3.9811 | 3.8028 | 5.5987 | 5.2809 | 5.0671 | 4.7575 | 4.5052 | 4.2085 | 3.7862 | 3.4061 | 3.0482 | 2.5796 | 1.0368 | 0.31308 | 0.085271 | 0.41154 | 9.7387 | 9.4209 | 9.2071 | 8.8975 | 8.6452 | 8.3485 | 7.9262 | 7.5461 | 7.1882 | 6.7196 | 5.1768 | 4.4531 | 4.2253 | 4.5515 | 5.6007 | 5.2788 | 5.0648 | 4.7559 | 4.5101 | 4.2181 | 3.7693 | 3.3679 | 3.0341 | 2.6366 | 0.4902 | -3.7286 | -6.898 | -8.7225 | 9.7407 | 9.4188 | 9.2048 | 8.8959 | 8.6501 | 8.3581 | 7.9093 | 7.5079 | 7.1741 | 6.7766 | 4.6302 | 0.41136 | -2.758 | -4.5825 | 5.6123 | 5.2804 | 5.0846 | 4.8161 | 4.5892 | 4.3435 | 3.9648 | 3.646 | 3.3057 | 2.2028 | -2.7642 | -6.5017 | -8.5512 | -7.4723 | 9.7523 | 9.4204 | 9.4204 | 8.9561 | 8.7292 | 8.4835 | 8.1048 | 7.786 | 7.4457 | 6.3428 | 1.3758 | -2.3617 | -4.4112 | -3.3323 | 353740 | 430080 | RIBBLE | PENWORTHAM
| Crown Lane | 3.4209 | 2.3102 | 2.2132 | 1.5969 | 1.1876 | 0.55842 | -0.085875 | -0.87037 | -1.6721 | -2.4045 | -5.89 | -8.3785 | -9.5763 | -9.5654 | 8.0579 | 6.9472 | 6.8502 | 6.2339 | 5.8246 | 5.1954 | 4.5511 | 3.7666 | 2.9649 | 2.2325 | -1.253 | -3.7415 | -4.9393 | -4.9284 | 3.7854 | 3.0122 | 2.8716 | 2.3179 | 1.9988 | 1.4707 | 0.941 | 0.27154 | -0.4748 | -0.98602 | -2.9038 | -4.2444 | -5.4008 | -5.9202 | 8.4224 | 7.6492 | 7.5086 | 6.9549 | 6.6358 | 6.1077 | 5.578 | 4.9085 | 4.1622 | 3.651 | 1.7332 | 0.39256 | -0.76376 | -1.2832 | 3.43 | 2.3335 | 2.2429 | 1.6393 | 1.2422 | 0.64211 | 0.021995 | -0.74414 | -1.5166 | -2.1896 | -5.2478 | -7.0233 | -7.8977 | -7.6098 | 8.067 | 6.9705 | 6.8799 | 6.2763 | 5.8792 | 5.2791 | 4.659 | 3.8929 | 3.1204 | 2.4474 | -0.61083 | -2.3863 | -3.2607 | -2.9728 | 3.439 | 2.3338 | 2.2545 | 1.6959 | 1.3467 | 0.77702 | 0.16586 | -0.60083 | -1.3187 | -1.7966 | -6.7145 | -14.4171 | -19.9554 | -23.2437 | 8.076 | 6.9708 | 6.8915 | 6.3329 | 5.9837 | 5.414 | 4.8029 | 4.0362 | 3.3183 | 2.8404 | -2.0775 | -9.7801 | -15.3184 | -18.6067 | 3.4247 | 2.27 | 2.189 | 1.6445 | 1.316 | 0.79782 | 0.24968 | -0.41954 | -1.1284 | -2.5227 | -11.1095 | -17.4349 | -21.0129 | -19.9851 | 8.0617 | 6.907 | 6.907 | 6.2815 | 5.953 | 5.4348 | 4.8867 | 4.2175 | 3.5086 | 2.1143 | -6.4725 | -12.7979 | -16.3759 | -15.3481 | 362706 | 410859 | WESTHOUGHTON | KEARSLEY
| Culcheth | 3.2018 | 2.8897 | 2.752 | 2.5189 | 2.3445 | 2.035 | 1.7526 | 1.5586 | 1.2556 | 0.83289 | -0.40197 | -1.1101 | -1.2603 | -1.0578 | 9.2018 | 8.8897 | 8.752 | 8.5189 | 8.3445 | 8.035 | 7.7526 | 7.5586 | 7.2556 | 6.8329 | 5.598 | 4.8899 | 4.7397 | 4.9422 | 3.3196 | 3.1129 | 2.955 | 2.7693 | 2.6494 | 2.4036 | 2.1836 | 2.0467 | 1.771 | 1.4736 | 0.84617 | 0.29883 | -0.047768 | -0.25381 | 9.3196 | 9.1129 | 8.955 | 8.7693 | 8.6494 | 8.4036 | 8.1836 | 8.0467 | 7.771 | 7.4736 | 6.8462 | 6.2988 | 5.9522 | 5.7462 | 3.2052 | 2.9058 | 2.7809 | 2.5601 | 2.3979 | 2.1017 | 1.8315 | 1.6478 | 1.3609 | 0.97148 | -0.14394 | -0.74733 | -0.85486 | -0.62382 | 9.2052 | 8.9058 | 8.7809 | 8.5601 | 8.3979 | 8.1017 | 7.8315 | 7.6478 | 7.3609 | 6.9715 | 5.8561 | 5.2527 | 5.1451 | 5.3762 | 3.2138 | 2.9005 | 2.7636 | 2.5414 | 2.3692 | 2.0449 | 1.7208 | 1.4726 | 1.1539 | 0.8011 | -0.33858 | -2.2878 | -3.4132 | -4.5124 | 9.2138 | 8.9005 | 8.7636 | 8.5414 | 8.3692 | 8.0449 | 7.7208 | 7.4726 | 7.1539 | 6.8011 | 5.6614 | 3.7122 | 2.5868 | 1.4876 | 3.2047 | 2.8692 | 2.7336 | 2.5193 | 2.3625 | 2.0749 | 1.8039 | 1.63 | 1.3985 | 0.87702 | -1.2301 | -2.7177 | -3.4132 | -3.1918 | 9.2047 | 8.8692 | 8.8692 | 8.5193 | 8.3625 | 8.0749 | 7.8039 | 7.63 | 7.3985 | 6.877 | 4.7699 | 3.2823 | 2.5868 | 2.8082 | 365430 | 395366 | GOLBORNE | BOLD
| Cutacre | 19.3601 | 19.0522 | 18.9649 | 18.9519 | 18.9387 | 18.9215 | 18.8717 | 18.8592 | 18.8499 | 18.8201 | 18.6629 | 18.3948 | 18.2014 | 17.9641 | 23.3601 | 23.0522 | 22.9649 | 22.9519 | 22.9387 | 22.9215 | 22.8717 | 22.8592 | 22.8499 | 22.8201 | 22.6629 | 22.3948 | 22.2014 | 21.9641 | 19.5884 | 19.4895 | 19.4216 | 19.3856 | 19.3567 | 19.3338 | 19.2796 | 19.2571 | 19.2357 | 19.1952 | 19.0695 | 18.8907 | 18.728 | 18.609 | 23.5884 | 23.4895 | 23.4216 | 23.3856 | 23.3567 | 23.3338 | 23.2796 | 23.2571 | 23.2357 | 23.1952 | 23.0695 | 22.8907 | 22.728 | 22.609 | 19.3605 | 19.0527 | 18.9655 | 18.9526 | 18.9395 | 18.9234 | 18.874 | 18.8618 | 18.853 | 18.8249 | 18.7061 | 18.5691 | 18.4396 | 18.3262 | 23.3605 | 23.0527 | 22.9655 | 22.9526 | 22.9395 | 22.9234 | 22.874 | 22.8618 | 22.853 | 22.8249 | 22.7061 | 22.5691 | 22.4396 | 22.3262 | 19.3687 | 19.0695 | 18.9906 | 18.9862 | 18.982 | 18.9706 | 18.9223 | 18.9055 | 18.888 | 18.8495 | 18.5068 | 18.0694 | 17.8363 | 17.7999 | 23.3687 | 23.0695 | 22.9906 | 22.9862 | 22.982 | 22.9706 | 22.9223 | 22.9055 | 22.888 | 22.8495 | 22.5068 | 22.0694 | 21.8363 | 21.7999 | 19.3618 | 19.0558 | 18.974 | 18.9671 | 18.9597 | 18.9405 | 18.8785 | 18.8395 | 18.798 | 18.7309 | 18.3097 | 17.9203 | 17.8087 | 17.8681 | 23.3618 | 23.0558 | 23.0558 | 22.9671 | 22.9597 | 22.9405 | 22.8785 | 22.8395 | 22.798 | 22.7309 | 22.3097 | 21.9203 | 21.8087 | 21.8681 | 369848 | 404515 | KEARSLEY LOCAL | KEARSLEY
| Deansgate | 4.6741 | 4.0619 | 4.1065 | 4.0449 | 3.9344 | 3.7084 | 3.5524 | 3.4243 | 3.2403 | 3.1413 | 2.7634 | 2.6537 | 2.7058 | 2.858 | 12.0041 | 11.3919 | 11.4365 | 11.3749 | 11.2644 | 11.0384 | 10.8824 | 10.7543 | 10.5703 | 10.4713 | 10.0934 | 9.9837 | 10.0358 | 10.188 | 5.232 | 5.0922 | 4.9499 | 4.7203 | 4.4754 | 4.1672 | 3.8993 | 3.6391 | 3.3001 | 3.0301 | 2.5583 | 2.291 | 2.23 | 2.339 | 12.562 | 12.4222 | 12.2799 | 12.0503 | 11.8054 | 11.4972 | 11.2293 | 10.9691 | 10.6301 | 10.3601 | 9.8883 | 9.621 | 9.56 | 9.669 | 4.6832 | 4.0808 | 4.1345 | 4.0831 | 3.9834 | 3.7695 | 3.6253 | 3.5093 | 3.3395 | 3.2556 | 2.8853 | 2.7799 | 2.8332 | 2.9854 | 12.0132 | 11.4108 | 11.4645 | 11.4131 | 11.3134 | 11.0995 | 10.9553 | 10.8393 | 10.6695 | 10.5856 | 10.2153 | 10.1099 | 10.1632 | 10.3154 | 4.7084 | 4.1327 | 4.2124 | 4.187 | 4.1106 | 3.9225 | 3.8042 | 3.714 | 3.5698 | 3.5174 | 3.2723 | 2.7552 | 2.4352 | 2.3509 | 12.0384 | 11.4627 | 11.5424 | 11.517 | 11.4406 | 11.2525 | 11.1342 | 11.044 | 10.8998 | 10.8474 | 10.6023 | 10.0852 | 9.7652 | 9.6809 | 4.7193 | 4.1536 | 4.2481 | 4.2402 | 4.1832 | 4.0176 | 3.9223 | 3.8577 | 3.7439 | 3.5734 | 2.7534 | 2.2507 | 2.083 | 2.5713 | 12.0493 | 11.4836 | 11.4836 | 11.5702 | 11.5132 | 11.3476 | 11.2523 | 11.1877 | 11.0739 | 10.9034 | 10.0834 | 9.5807 | 9.413 | 9.9013 | 383463 | 398149 | BLOOM ST | SOUTH MANCHESTER
| Denton East | 10.4938 | 10.1126 | 9.9906 | 9.6661 | 9.3723 | 9.0023 | 8.5556 | 8.1097 | 7.6333 | 7.0692 | 5.1694 | 4.2014 | 3.9646 | 4.1676 | 8.6308 | 8.2496 | 8.1276 | 7.8031 | 7.5093 | 7.1393 | 6.6926 | 6.2467 | 5.7703 | 5.2062 | 3.3064 | 2.3384 | 2.1016 | 2.3046 | 10.5775 | 10.2481 | 10.0466 | 9.7167 | 9.4831 | 9.117 | 8.7043 | 8.2937 | 7.8502 | 7.3809 | 6.0816 | 5.0991 | 4.5274 | 4.202 | 8.7145 | 8.3851 | 8.1836 | 7.8537 | 7.6201 | 7.254 | 6.8413 | 6.4307 | 5.9872 | 5.5179 | 4.2186 | 3.2361 | 2.6644 | 2.339 | 10.5211 | 10.1753 | 10.0327 | 9.7181 | 9.4864 | 9.1378 | 8.695 | 8.2629 | 7.8142 | 7.3081 | 5.5808 | 4.7322 | 4.5683 | 4.7631 | 8.6581 | 8.3123 | 8.1697 | 7.8551 | 7.6234 | 7.2748 | 6.832 | 6.3999 | 5.9512 | 5.4451 | 3.7178 | 2.8692 | 2.7053 | 2.9001 | 10.498 | 10.1152 | 9.9931 | 9.6608 | 9.3984 | 9.0326 | 8.5706 | 8.125 | 7.7075 | 7.2711 | 4.5634 | -1.3688 | -6.0862 | -9.3514 | 8.635 | 8.2522 | 8.1301 | 7.7978 | 7.5354 | 7.1696 | 6.7076 | 6.262 | 5.8445 | 5.4081 | 2.7004 | -3.2318 | -7.9492 | -11.2144 | 10.5277 | 10.1494 | 10.0348 | 9.7576 | 9.5016 | 9.197 | 8.8004 | 8.4364 | 7.9327 | 6.4855 | -0.18745 | -5.5405 | -8.6869 | -7.8389 | 8.6647 | 8.2864 | 8.2864 | 7.8946 | 7.6386 | 7.334 | 6.9374 | 6.5734 | 6.0697 | 4.6225 | -2.0504 | -7.4035 | -10.5499 | -9.7019 | 392394 | 395626 | DROYLSDEN | STALYBRIDGE
| Denton West | 9.2439 | 9.0356 | 8.8395 | 8.5248 | 8.261 | 7.819 | 7.0733 | 6.6374 | 6.1824 | 5.6205 | 3.7563 | 2.6903 | 2.4083 | 2.4338 | 13.8809 | 13.6726 | 13.4765 | 13.1618 | 12.898 | 12.456 | 11.7103 | 11.2744 | 10.8194 | 10.2575 | 8.3933 | 7.3273 | 7.0453 | 7.0708 | 9.346 | 9.2158 | 8.9578 | 8.6493 | 8.4067 | 8.0293 | 7.6223 | 7.2197 | 6.7954 | 6.3274 | 4.9189 | 3.8815 | 3.2968 | 2.9212 | 13.983 | 13.8528 | 13.5948 | 13.2863 | 13.0437 | 12.6663 | 12.2593 | 11.8567 | 11.4324 | 10.9644 | 9.5559 | 8.5185 | 7.9338 | 7.5582 | 9.2512 | 9.0404 | 8.8398 | 8.53 | 8.2797 | 7.8499 | 7.1145 | 6.691 | 6.2545 | 5.7388 | 4.0116 | 3.0783 | 2.8383 | 2.8867 | 13.8882 | 13.6774 | 13.4768 | 13.167 | 12.9167 | 12.4869 | 11.7515 | 11.328 | 10.8915 | 10.3758 | 8.6486 | 7.7153 | 7.4753 | 7.5237 | 9.2568 | 9.063 | 8.8923 | 8.6034 | 8.3911 | 8.0078 | 7.3254 | 6.9478 | 6.5998 | 6.2057 | 3.7592 | -0.96995 | -4.5043 | -6.7015 | 13.8938 | 13.7 | 13.5293 | 13.2404 | 13.0281 | 12.6448 | 11.9624 | 11.5848 | 11.2368 | 10.8427 | 8.3962 | 3.667 | 0.13274 | -2.0645 | 9.2842 | 9.08 | 8.8926 | 8.6242 | 8.4489 | 8.1151 | 7.4908 | 7.1866 | 6.7581 | 5.5855 | 0.15246 | -4.1188 | -6.3462 | -5.3825 | 13.9212 | 13.717 | 13.717 | 13.2612 | 13.0859 | 12.7521 | 12.1278 | 11.8236 | 11.3951 | 10.2225 | 4.7895 | 0.5182 | -1.7092 | -0.74554 | 390380 | 395565 | DROYLSDEN | STALYBRIDGE
| Dickinson St | 3.8052 | 3.2416 | 3.3726 | 3.273 | 3.0843 | 2.751 | 2.261 | 2.2468 | 2.0559 | 1.8192 | 0.92425 | 0.78078 | 0.79964 | 1.0336 | 3.8052 | 3.2416 | 3.3726 | 3.273 | 3.0843 | 2.751 | 2.261 | 2.2468 | 2.0559 | 1.8192 | 0.92425 | 0.78078 | 0.79964 | 1.0336 | 4.7114 | 4.9036 | 4.7547 | 4.4421 | 4.1035 | 3.7131 | 3.1359 | 3.0013 | 2.6744 | 2.3005 | 1.2869 | 0.87653 | 0.68844 | 0.79634 | 4.7114 | 4.9036 | 4.7547 | 4.4421 | 4.1035 | 3.7131 | 3.1359 | 3.0013 | 2.6744 | 2.3005 | 1.2869 | 0.87653 | 0.68844 | 0.79634 | 3.8119 | 3.2576 | 3.399 | 3.3074 | 3.1268 | 2.8019 | 2.3215 | 2.3145 | 2.1333 | 1.9115 | 1.0441 | 0.91774 | 0.94482 | 1.1795 | 3.8119 | 3.2576 | 3.399 | 3.3074 | 3.1268 | 2.8019 | 2.3215 | 2.3145 | 2.1333 | 1.9115 | 1.0441 | 0.91774 | 0.94482 | 1.1795 | 3.8674 | 3.3687 | 3.5639 | 3.5235 | 3.3859 | 3.1027 | 2.6596 | 2.6855 | 2.5431 | 2.3753 | 1.6963 | 0.83948 | 0.33982 | 0.23559 | 3.8674 | 3.3687 | 3.5639 | 3.5235 | 3.3859 | 3.1027 | 2.6596 | 2.6855 | 2.5431 | 2.3753 | 1.6963 | 0.83948 | 0.33982 | 0.23559 | 3.8711 | 3.3746 | 3.5803 | 3.5563 | 3.4327 | 3.1692 | 2.7494 | 2.8009 | 2.6927 | 2.3062 | 0.64818 | -0.13858 | -0.35219 | 0.5508 | 3.8711 | 3.3746 | 3.3746 | 3.5563 | 3.4327 | 3.1692 | 2.7494 | 2.8009 | 2.6927 | 2.3062 | 0.64818 | -0.13858 | -0.35219 | 0.5508 | 384109 | 397722 | BLOOM ST | SOUTH MANCHESTER
| Didsbury | 7.7141 | 7.146 | 7.0048 | 6.775 | 6.3565 | 5.8116 | 5.2855 | 4.723 | 4.1751 | 3.6474 | 1.6352 | 0.80463 | 0.78608 | 1.1319 | 12.3511 | 11.783 | 11.6418 | 11.412 | 10.9935 | 10.4486 | 9.9225 | 9.36 | 8.8121 | 8.2844 | 6.2722 | 5.4416 | 5.4231 | 5.7689 | 7.9093 | 7.5117 | 7.2841 | 7.048 | 6.659 | 6.1509 | 5.6499 | 5.1393 | 4.5814 | 4.132 | 2.5835 | 1.6296 | 1.1897 | 0.97399 | 12.5463 | 12.1487 | 11.9211 | 11.685 | 11.296 | 10.7879 | 10.2869 | 9.7763 | 9.2184 | 8.769 | 7.2205 | 6.2666 | 5.8267 | 5.611 | 7.7214 | 7.1629 | 7.0288 | 6.8064 | 6.3988 | 5.8672 | 5.3536 | 4.7879 | 4.2589 | 3.7769 | 1.8913 | 1.1202 | 1.0981 | 1.411 | 12.3584 | 11.7999 | 11.6658 | 11.4434 | 11.0358 | 10.5042 | 9.9906 | 9.4249 | 8.8959 | 8.4139 | 6.5283 | 5.7572 | 5.7351 | 6.048 | 7.7337 | 7.1932 | 7.0916 | 6.8973 | 6.5367 | 6.0613 | 5.6084 | 5.1641 | 4.7477 | 4.4498 | 2.3512 | -2.0148 | -5.6715 | -8.2028 | 12.3707 | 11.8302 | 11.7286 | 11.5343 | 11.1737 | 10.6983 | 10.2454 | 9.8011 | 9.3847 | 9.0868 | 6.9882 | 2.6222 | -1.0345 | -3.5658 | 7.7068 | 7.1123 | 7.0164 | 6.8706 | 6.5714 | 6.1809 | 5.8029 | 5.4434 | 5.0522 | 4.1302 | -0.82809 | -5.3149 | -7.7103 | -6.7953 | 12.3438 | 11.7493 | 11.7493 | 11.5076 | 11.2084 | 10.8179 | 10.4399 | 10.0804 | 9.6892 | 8.7672 | 3.8089 | -0.67788 | -3.0733 | -2.1583 | 384792 | 391153 | WEST DIDSBURY | SOUTH MANCHESTER
| Dodgson Rd | 15.1118 | 14.8526 | 14.8287 | 14.5843 | 14.5708 | 14.2929 | 14.1586 | 14.0171 | 13.7887 | 13.464 | 12.3827 | 11.283 | 10.6008 | 10.1243 | 19.2488 | 18.9896 | 18.9657 | 18.7213 | 18.7078 | 18.4299 | 18.2956 | 18.1541 | 17.9257 | 17.601 | 16.5197 | 15.42 | 14.7378 | 14.2613 | 15.1979 | 14.9812 | 14.9166 | 14.664 | 14.6189 | 14.342 | 14.1635 | 13.9714 | 13.7456 | 13.4161 | 12.6091 | 11.9915 | 11.4634 | 11.1672 | 19.3349 | 19.1182 | 19.0536 | 18.801 | 18.7559 | 18.479 | 18.3005 | 18.1084 | 17.8826 | 17.5531 | 16.7461 | 16.1285 | 15.6004 | 15.3042 | 15.103 | 14.8823 | 14.8435 | 14.6009 | 14.6347 | 14.3725 | 14.2464 | 14.0974 | 13.9036 | 13.6077 | 12.6164 | 11.8038 | 11.3483 | 11.2092 | 19.24 | 19.0193 | 18.9805 | 18.7379 | 18.7717 | 18.5095 | 18.3834 | 18.2344 | 18.0406 | 17.7447 | 16.7534 | 15.9408 | 15.4853 | 15.3462 | 15.1129 | 14.8474 | 14.8141 | 14.5609 | 14.5229 | 14.2174 | 14.0377 | 13.859 | 13.5807 | 13.269 | 11.5172 | 7.6623 | 4.3406 | 2.2851 | 19.2499 | 18.9844 | 18.9511 | 18.6979 | 18.6599 | 18.3544 | 18.1747 | 17.996 | 17.7177 | 17.406 | 15.6542 | 11.7993 | 8.4776 | 6.4221 | 15.135 | 14.8893 | 14.8719 | 14.6367 | 14.6312 | 14.3579 | 14.2068 | 14.0572 | 13.7172 | 12.8154 | 8.8813 | 5.4472 | 3.2225 | 3.1976 | 19.272 | 19.0263 | 19.0263 | 18.7737 | 18.7682 | 18.4949 | 18.3438 | 18.1942 | 17.8542 | 16.9524 | 13.0183 | 9.5842 | 7.3595 | 7.3346 | 355190 | 430397 | PRESTON EAST | PENWORTHAM
| Douglas St | 8.5455 | 8.3108 | 8.189 | 7.9323 | 7.8723 | 7.7458 | 7.4469 | 7.2129 | 7.0628 | 6.6823 | 5.6182 | 4.9341 | 4.4382 | 4.2222 | 15.2055 | 14.9708 | 14.849 | 14.5923 | 14.5323 | 14.4058 | 14.1069 | 13.8729 | 13.7228 | 13.3423 | 12.2782 | 11.5941 | 11.0982 | 10.8822 | 8.8278 | 8.8083 | 8.6059 | 8.2917 | 8.1947 | 7.9432 | 7.6947 | 7.4121 | 7.0747 | 6.4927 | 5.9961 | 5.6917 | 5.3095 | 5.1418 | 15.4878 | 15.4683 | 15.2659 | 14.9517 | 14.8547 | 14.6032 | 14.3547 | 14.0721 | 13.7347 | 13.1527 | 12.6561 | 12.3517 | 11.9695 | 11.8018 | 8.5702 | 8.351 | 8.2386 | 7.9917 | 7.9048 | 7.7822 | 7.4923 | 7.2667 | 7.1275 | 6.7741 | 5.8454 | 5.3863 | 5.0049 | 4.9494 | 15.2302 | 15.011 | 14.8986 | 14.6517 | 14.5648 | 14.4422 | 14.1523 | 13.9267 | 13.7875 | 13.4341 | 12.5054 | 12.0463 | 11.6649 | 11.6094 | 8.5609 | 8.3406 | 8.2325 | 7.9842 | 7.9261 | 7.7892 | 7.4666 | 7.1983 | 7.0184 | 6.6229 | 4.9666 | 2.278 | 0.13325 | -1.0063 | 15.2209 | 15.0006 | 14.8925 | 14.6442 | 14.5861 | 14.4492 | 14.1266 | 13.8583 | 13.6784 | 13.2829 | 11.6266 | 8.938 | 6.7933 | 5.6537 | 8.5614 | 8.3288 | 8.218 | 7.9782 | 7.9071 | 7.7746 | 7.4525 | 7.1867 | 6.9633 | 6.1533 | 2.9639 | 0.58434 | -0.81181 | -0.26066 | 15.2214 | 14.9888 | 14.9888 | 14.6382 | 14.5671 | 14.4346 | 14.1125 | 13.8467 | 13.6233 | 12.8133 | 9.6239 | 7.2443 | 5.8482 | 6.3993 | 352220 | 429932 | RIBBLE | PENWORTHAM
| Droylsden East | 7.0562 | 6.6417 | 6.3329 | 5.9657 | 5.6319 | 5.2094 | 4.6951 | 4.2164 | 3.706 | 3.0856 | 1.0112 | -0.11537 | -0.42589 | -0.2376 | 11.6932 | 11.2787 | 10.9699 | 10.6027 | 10.2689 | 9.8464 | 9.3321 | 8.8534 | 8.343 | 7.7226 | 5.6482 | 4.5216 | 4.2111 | 4.3994 | 7.2222 | 6.9536 | 6.6049 | 6.2464 | 5.9493 | 5.5665 | 5.089 | 4.6437 | 4.1613 | 3.6466 | 2.1598 | 1.065 | 0.40631 | 0.026328 | 11.8592 | 11.5906 | 11.2419 | 10.8834 | 10.5863 | 10.2035 | 9.726 | 9.2807 | 8.7983 | 8.2836 | 6.7968 | 5.702 | 5.0433 | 4.6633 | 7.0681 | 6.6766 | 6.3913 | 6.0425 | 5.7311 | 5.3319 | 4.8414 | 4.385 | 3.9062 | 3.3511 | 1.5128 | 0.48192 | 0.23286 | 0.43624 | 11.7051 | 11.3136 | 11.0283 | 10.6795 | 10.3681 | 9.9689 | 9.4784 | 9.022 | 8.5432 | 7.9881 | 6.1498 | 5.1189 | 4.8699 | 5.0732 | 7.0674 | 6.6638 | 6.372 | 6.0221 | 5.7303 | 5.3469 | 4.8492 | 4.3902 | 3.9727 | 3.5274 | 0.52051 | -6.3227 | -11.8467 | -15.5725 | 11.7044 | 11.3008 | 11.009 | 10.6591 | 10.3673 | 9.9839 | 9.4862 | 9.0272 | 8.6097 | 8.1644 | 5.1575 | -1.6857 | -7.2097 | -10.9355 | 7.0994 | 6.6894 | 6.4008 | 6.0877 | 5.8258 | 5.5025 | 5.0779 | 4.7056 | 4.1458 | 2.5088 | -5.0709 | -11.278 | -14.9546 | -13.9706 | 11.7364 | 11.3264 | 11.3264 | 10.7247 | 10.4628 | 10.1395 | 9.7149 | 9.3426 | 8.7828 | 7.1458 | -0.43385 | -6.641 | -10.3176 | -9.3336 | 390532 | 398053 | DROYLSDEN | STALYBRIDGE
| Dukinfield | 10.7415 | 10.4461 | 10.5053 | 10.4007 | 10.4075 | 10.2163 | 10.1221 | 10.0202 | 9.8357 | 9.6801 | 9.0893 | 8.6118 | 8.4101 | 8.2767 | 15.3785 | 15.0831 | 15.1423 | 15.0377 | 15.0445 | 14.8533 | 14.7591 | 14.6572 | 14.4727 | 14.3171 | 13.7263 | 13.2488 | 13.0471 | 12.9137 | 10.9304 | 10.7877 | 10.7701 | 10.6276 | 10.6166 | 10.4253 | 10.3264 | 10.2177 | 10.0244 | 9.8769 | 9.4655 | 9.0756 | 8.8552 | 8.729 | 15.5674 | 15.4247 | 15.4071 | 15.2646 | 15.2536 | 15.0623 | 14.9634 | 14.8547 | 14.6614 | 14.5139 | 14.1025 | 13.7126 | 13.4922 | 13.366 | 10.7459 | 10.4569 | 10.5214 | 10.4217 | 10.4295 | 10.2485 | 10.1596 | 10.0585 | 9.8864 | 9.7461 | 9.2218 | 8.8409 | 8.6765 | 8.6224 | 15.3829 | 15.0939 | 15.1584 | 15.0587 | 15.0665 | 14.8855 | 14.7966 | 14.6955 | 14.5234 | 14.3831 | 13.8588 | 13.4779 | 13.3135 | 13.2594 | 10.757 | 10.4766 | 10.5482 | 10.4535 | 10.4657 | 10.2809 | 10.1739 | 10.0497 | 9.8622 | 9.7199 | 8.7415 | 6.4715 | 4.6178 | 3.3821 | 15.394 | 15.1136 | 15.1852 | 15.0905 | 15.1027 | 14.9179 | 14.8109 | 14.6867 | 14.4992 | 14.3569 | 13.3785 | 11.1085 | 9.2548 | 8.0191 | 10.7644 | 10.481 | 10.5515 | 10.464 | 10.4792 | 10.3086 | 10.2042 | 10.0887 | 9.8659 | 9.4205 | 6.979 | 4.8394 | 3.6466 | 3.9762 | 15.4014 | 15.118 | 15.118 | 15.101 | 15.1162 | 14.9456 | 14.8412 | 14.7257 | 14.5029 | 14.0575 | 11.616 | 9.4764 | 8.2836 | 8.6132 | 394372 | 396438 | HYDE | STALYBRIDGE
| Dumers Lane | 8.4341 | 7.9408 | 7.9549 | 7.7304 | 7.6817 | 7.4701 | 7.2423 | 7.1107 | 6.8382 | 6.5796 | 5.6092 | 4.7506 | 4.1533 | 3.7102 | 14.9341 | 14.4408 | 14.4549 | 14.2304 | 14.1817 | 13.9701 | 13.7423 | 13.6107 | 13.3382 | 13.0796 | 12.1092 | 11.2506 | 10.6533 | 10.2102 | 8.7676 | 8.5612 | 8.5022 | 8.2294 | 8.1523 | 7.9451 | 7.7145 | 7.5723 | 7.2884 | 7.0333 | 6.3857 | 5.8269 | 5.2949 | 4.9938 | 15.2676 | 15.0612 | 15.0022 | 14.7294 | 14.6523 | 14.4451 | 14.2145 | 14.0723 | 13.7884 | 13.5333 | 12.8857 | 12.3269 | 11.7949 | 11.4938 | 8.437 | 7.9519 | 7.9728 | 7.7541 | 7.711 | 7.5062 | 7.2853 | 7.1596 | 6.8971 | 6.658 | 5.7962 | 5.1962 | 4.7274 | 4.4816 | 14.937 | 14.4519 | 14.4728 | 14.2541 | 14.211 | 14.0062 | 13.7853 | 13.6596 | 13.3971 | 13.158 | 12.2962 | 11.6962 | 11.2274 | 10.9816 | 8.4504 | 7.9745 | 8.0044 | 7.7932 | 7.7564 | 7.549 | 7.3134 | 7.1643 | 6.8782 | 6.6185 | 4.9104 | 1.8958 | -0.57634 | -2.0773 | 14.9504 | 14.4745 | 14.5044 | 14.2932 | 14.2564 | 14.049 | 13.8134 | 13.6643 | 13.3782 | 13.1185 | 11.4104 | 8.3958 | 5.9237 | 4.4227 | 8.4498 | 7.9594 | 7.9839 | 7.7795 | 7.7512 | 7.5509 | 7.3098 | 7.153 | 6.7908 | 6.1226 | 2.7499 | -0.028256 | -1.7103 | -1.3345 | 14.9498 | 14.4594 | 14.4594 | 14.2795 | 14.2512 | 14.0509 | 13.8098 | 13.653 | 13.2908 | 12.6226 | 9.2499 | 6.4717 | 4.7897 | 5.1655 | 380057 | 408141 | BURY | KEARSLEY
| Dumplington | 12.7457 | 11.3147 | 10.9504 | 10.84 | 10.6435 | 10.5468 | 10.2169 | 9.9635 | 9.8779 | 9.4678 | 8.8844 | 8.6061 | 7.9956 | 8.1498 | 23.7457 | 22.3147 | 21.9504 | 21.84 | 21.6435 | 21.5468 | 21.2169 | 20.9635 | 20.8779 | 20.4678 | 19.8844 | 19.6061 | 18.9956 | 19.1498 | 13.8015 | 13.3432 | 12.9222 | 12.6247 | 12.3086 | 12.1306 | 11.7244 | 11.3525 | 11.1261 | 10.6029 | 10.0084 | 9.6438 | 8.9048 | 9.1135 | 24.8015 | 24.3432 | 23.9222 | 23.6247 | 23.3086 | 23.1306 | 22.7244 | 22.3525 | 22.1261 | 21.6029 | 21.0084 | 20.6438 | 19.9048 | 20.1135 | 12.7545 | 11.3373 | 10.9762 | 10.8809 | 10.688 | 10.6003 | 10.282 | 10.0471 | 9.9738 | 9.5788 | 9.0543 | 8.901 | 8.3585 | 8.6135 | 23.7545 | 22.3373 | 21.9762 | 21.8809 | 21.688 | 21.6003 | 21.282 | 21.0471 | 20.9738 | 20.5788 | 20.0543 | 19.901 | 19.3585 | 19.6135 | 12.7953 | 11.4171 | 11.1031 | 11.0464 | 10.9004 | 10.8509 | 10.5686 | 10.3654 | 10.3203 | 9.9573 | 9.4537 | 9.0089 | 7.7524 | 6.644 | 23.7953 | 22.4171 | 22.1031 | 22.0464 | 21.9004 | 21.8509 | 21.5686 | 21.3654 | 21.3203 | 20.9573 | 20.4537 | 20.0089 | 18.7524 | 17.644 | 12.7871 | 11.397 | 11.0808 | 11.0394 | 10.9002 | 10.8641 | 10.5884 | 10.4003 | 10.3646 | 9.9292 | 9.1359 | 7.7893 | 6.3123 | 6.7162 | 23.7871 | 22.397 | 22.397 | 22.0394 | 21.9002 | 21.8641 | 21.5884 | 21.4003 | 21.3646 | 20.9292 | 20.1359 | 18.7893 | 17.3123 | 17.7162 | 376770 | 397157 | BARTON | CARRINGTON
| Eastlands | 10.8994 | 9.4643 | 6.6971 | 2.083 | -2.3939 | -6.9874 | -11.6381 | 7.386 | 7.2173 | 7.024 | 6.3637 | 5.9684 | 5.8475 | 5.9753 | 15.5364 | 14.1013 | 11.3341 | 6.72 | 2.2431 | -2.3504 | -7.0011 | -7.114 | -7.2827 | -7.476 | -8.1363 | -8.5316 | -8.6525 | -8.5247 | 11.733 | 11.0881 | 8.4658 | 3.7915 | -0.74061 | -5.3637 | -10.0547 | 8.9171 | 8.6885 | 8.4568 | 7.903 | 7.4643 | 7.2366 | 7.2132 | 16.37 | 15.7251 | 13.1028 | 8.4285 | 3.8964 | -0.72673 | -5.4177 | -5.5829 | -5.8115 | -6.0432 | -6.597 | -7.0357 | -7.2634 | -7.2868 | 10.9046 | 9.4783 | 6.7206 | 2.1144 | -2.3549 | -6.9403 | -11.5827 | 7.4493 | 7.2909 | 7.1156 | 6.5055 | 6.152 | 6.0491 | 6.1842 | 15.5416 | 14.1153 | 11.3576 | 6.7514 | 2.2821 | -2.3033 | -6.9457 | -7.0507 | -7.2091 | -7.3844 | -7.9945 | -8.348 | -8.4509 | -8.3158 | 10.9217 | 9.5099 | 6.7677 | 2.1753 | -2.2839 | -6.8598 | -11.5041 | 7.5242 | 7.3807 | 7.2335 | 6.5185 | 5.1632 | 4.2536 | 3.7135 | 15.5587 | 14.1469 | 11.4047 | 6.8123 | 2.3531 | -2.2228 | -6.8671 | -6.9758 | -7.1193 | -7.2665 | -7.9815 | -9.3368 | -10.2464 | -10.7865 | 10.9293 | 9.5182 | 6.7882 | 2.2174 | -2.2248 | -6.7768 | -11.3933 | 7.6659 | 7.5423 | 7.2046 | 5.63 | 4.4203 | 3.8475 | 4.2577 | 15.5663 | 14.1552 | 14.1552 | 6.8544 | 2.4122 | -2.1398 | -6.7563 | -6.8341 | -6.9577 | -7.2954 | -8.87 | -10.0797 | -10.6525 | -10.2423 | 386458 | 398693 | STUART ST | STALYBRIDGE
| Easton | -0.062535 | -0.10733 | -0.15646 | -0.23455 | -0.20574 | -0.27711 | -0.3554 | -0.38108 | -0.4397 | -0.57606 | -0.9879 | -1.1775 | -1.3313 | -1.2279 | 0.23747 | 0.19267 | 0.14354 | 0.065454 | 0.094257 | 0.022891 | -0.055403 | -0.081081 | -0.1397 | -0.27606 | -0.6879 | -0.87754 | -1.0313 | -0.92787 | -0.022706 | -0.034478 | -0.097617 | -0.17138 | -0.14562 | -0.21803 | -0.29894 | -0.33122 | -0.38393 | -0.4769 | -0.65676 | -0.94444 | -1.2536 | -1.425 | 0.27729 | 0.26552 | 0.20238 | 0.12862 | 0.15438 | 0.081973 | 0.001058 | -0.03122 | -0.08393 | -0.1769 | -0.35676 | -0.64444 | -0.95364 | -1.125 | -0.061048 | -0.1028 | -0.14782 | -0.2213 | -0.19143 | -0.25954 | -0.3347 | -0.36184 | -0.41873 | -0.53796 | -0.91922 | -1.0866 | -1.2249 | -1.1215 | 0.23895 | 0.1972 | 0.15218 | 0.078695 | 0.10857 | 0.040456 | -0.034699 | -0.061837 | -0.11873 | -0.23796 | -0.61922 | -0.7866 | -0.9249 | -0.82149 | -0.059355 | -0.10896 | -0.16412 | -0.24843 | -0.23541 | -0.32939 | -0.43945 | -0.49044 | -0.55504 | -0.65827 | -0.96135 | -1.0946 | -1.1025 | -1.032 | 0.24065 | 0.19104 | 0.13588 | 0.051575 | 0.064588 | -0.029395 | -0.13945 | -0.19044 | -0.25504 | -0.35827 | -0.66135 | -0.79461 | -0.80249 | -0.732 | -0.066302 | -0.12316 | -0.17707 | -0.2616 | -0.26147 | -0.36116 | -0.46552 | -0.50739 | -0.56165 | -0.66845 | -0.99742 | -1.089 | -1.0661 | -0.94888 | 0.2337 | 0.17684 | 0.17684 | 0.038395 | 0.038526 | -0.061162 | -0.16552 | -0.20739 | -0.26165 | -0.36845 | -0.69742 | -0.78899 | -0.76612 | -0.64888 | 343201 | 571738 | - | HARKER
| Egremont | 2.7877 | 2.6517 | 2.2933 | 1.6921 | 1.4647 | 0.9802 | 0.38307 | -0.20323 | -0.70198 | -1.4892 | -4.2525 | -5.5311 | -5.6005 | -4.8104 | 5.2877 | 5.1517 | 4.7933 | 4.1921 | 3.9647 | 3.4802 | 2.8831 | 2.2968 | 1.798 | 1.0108 | -1.7525 | -3.0311 | -3.1005 | -2.3104 | 2.8951 | 2.9107 | 2.4594 | 1.9991 | 1.9799 | 1.6463 | 1.1941 | 0.77009 | 0.35532 | -0.1414 | -1.422 | -2.3199 | -2.762 | -2.8349 | 5.3951 | 5.4107 | 4.9594 | 4.4991 | 4.4799 | 4.1463 | 3.6941 | 3.2701 | 2.8553 | 2.3586 | 1.078 | 0.18013 | -0.26204 | -0.33486 | 2.7947 | 2.6725 | 2.3526 | 1.7894 | 1.5783 | 1.1264 | 0.56354 | 0.0104 | -0.45207 | -1.1653 | -3.6435 | -4.6986 | -4.6575 | -3.8484 | 5.2947 | 5.1725 | 4.8526 | 4.2894 | 4.0783 | 3.6264 | 3.0635 | 2.5104 | 2.0479 | 1.3347 | -1.1435 | -2.1986 | -2.1575 | -1.3484 | 2.7924 | 2.6213 | 2.2122 | 1.6006 | 1.3626 | 0.81082 | 0.087767 | -0.65034 | -1.2092 | -1.877 | -4.7787 | -10.0524 | -13.3657 | -15.8777 | 5.2924 | 5.1213 | 4.7122 | 4.1006 | 3.8626 | 3.3108 | 2.5878 | 1.8497 | 1.2908 | 0.62296 | -2.2787 | -7.5524 | -10.8657 | -13.3777 | 2.8128 | 2.5981 | 2.1973 | 1.6024 | 1.3485 | 0.86727 | 0.25414 | -0.32515 | -0.7692 | -2.1153 | -8.152 | -12.3032 | -14.3157 | -13.2478 | 5.3128 | 5.0981 | 5.0981 | 4.1024 | 3.8485 | 3.3673 | 2.7541 | 2.1749 | 1.7308 | 0.38472 | -5.652 | -9.8032 | -11.8157 | -10.7478 | 301070 | 513074 | EGREMONT | HARKER
| Embleton | 3.7041 | 3.3177 | 3.1533 | 2.7864 | 2.6763 | 2.2414 | 1.7602 | 2.2119 | 1.8777 | 1.3678 | -0.43056 | -1.3798 | -1.6391 | -1.3522 | 15.4621 | 15.0757 | 14.9113 | 14.5444 | 14.4343 | 13.9994 | 13.5182 | 13.2119 | 12.8777 | 12.3678 | 10.5694 | 9.6202 | 9.3609 | 9.6478 | 3.8357 | 3.6099 | 3.3499 | 3.0119 | 2.9292 | 2.5277 | 2.0745 | 2.5425 | 2.1988 | 1.7718 | 0.83534 | 0.042871 | -0.55596 | -0.8391 | 15.5937 | 15.3679 | 15.1079 | 14.7699 | 14.6872 | 14.2857 | 13.8325 | 13.5425 | 13.1988 | 12.7718 | 11.8353 | 11.0429 | 10.444 | 10.1609 | 3.7136 | 3.339 | 3.1982 | 2.8574 | 2.768 | 2.3605 | 1.9076 | 2.383 | 2.0783 | 1.6248 | 0.044569 | -0.72565 | -0.96185 | -0.65216 | 15.4716 | 15.097 | 14.9562 | 14.6154 | 14.526 | 14.1185 | 13.6656 | 13.383 | 13.0783 | 12.6248 | 11.0446 | 10.2744 | 10.0381 | 10.3478 | 3.7127 | 3.3129 | 3.1292 | 2.7542 | 2.6234 | 2.1444 | 1.5838 | 1.9458 | 1.5898 | 1.1572 | -0.6929 | -3.8536 | -5.909 | -7.4043 | 15.4707 | 15.0709 | 14.8872 | 14.5122 | 14.3814 | 13.9024 | 13.3418 | 12.9458 | 12.5898 | 12.1572 | 10.3071 | 7.1464 | 5.091 | 3.5957 | 3.7445 | 3.3522 | 3.1793 | 2.8283 | 2.7249 | 2.3031 | 1.8219 | 2.2846 | 2.0025 | 1.2117 | -2.4738 | -5.026 | -6.3517 | -5.7764 | 15.5025 | 15.1102 | 15.1102 | 14.5863 | 14.4829 | 14.0611 | 13.5799 | 13.2846 | 13.0025 | 12.2117 | 8.5262 | 5.974 | 4.6483 | 5.2236 | 315767 | 529389 | STAINBURN & SIDDICK | HARKER
| Exchange St | 6.6523 | 6.1981 | 5.8714 | 5.5631 | 5.4706 | 5.1472 | 4.7947 | 4.4989 | 4.2222 | 3.7431 | 2.3519 | 1.6418 | 1.2983 | 1.3691 | 10.1523 | 9.6981 | 9.3714 | 9.0631 | 8.9706 | 8.6472 | 8.2947 | 7.9989 | 7.7222 | 7.2431 | 5.8519 | 5.1418 | 4.7983 | 4.8691 | 6.8935 | 6.645 | 6.3294 | 6.0127 | 5.9268 | 5.6174 | 5.2744 | 4.9823 | 4.7021 | 4.2754 | 3.3309 | 2.69 | 2.1507 | 1.9145 | 10.3935 | 10.145 | 9.8294 | 9.5127 | 9.4268 | 9.1174 | 8.7744 | 8.4823 | 8.2021 | 7.7754 | 6.8309 | 6.19 | 5.6507 | 5.4145 | 6.6611 | 6.2061 | 5.889 | 5.5921 | 5.5089 | 5.1982 | 4.8583 | 4.5738 | 4.3137 | 3.875 | 2.6268 | 2.0751 | 1.7997 | 1.9365 | 10.1611 | 9.7061 | 9.389 | 9.0921 | 9.0089 | 8.6982 | 8.3583 | 8.0738 | 7.8137 | 7.375 | 6.1268 | 5.5751 | 5.2997 | 5.4365 | 6.653 | 6.2005 | 5.8779 | 5.5678 | 5.5062 | 5.201 | 4.8517 | 4.5599 | 4.3296 | 3.9532 | 1.8335 | -2.5994 | -6.1538 | -8.1527 | 10.153 | 9.7005 | 9.3779 | 9.0678 | 9.0062 | 8.701 | 8.3517 | 8.0599 | 7.8296 | 7.4532 | 5.3335 | 0.9006 | -2.6538 | -4.6527 | 6.6828 | 6.2199 | 5.9119 | 5.6514 | 5.6066 | 5.3472 | 5.0455 | 4.8062 | 4.4897 | 3.3168 | -1.8054 | -5.7449 | -8.0546 | -7.0804 | 10.1828 | 9.7199 | 9.7199 | 9.1514 | 9.1066 | 8.8472 | 8.5455 | 8.3062 | 7.9897 | 6.8168 | 1.6946 | -2.2449 | -4.5546 | -3.5804 | 369100 | 423028 | LOWER DARWEN | ROCHDALE
| Failsworth | 9.6373 | 9.2611 | 9.1892 | 8.9136 | 8.701 | 8.3527 | 8.0723 | 7.7089 | 7.2915 | 6.8525 | 5.3363 | 4.4991 | 4.2089 | 4.1803 | 14.2743 | 13.8981 | 13.8262 | 13.5506 | 13.338 | 12.9897 | 12.7093 | 12.3459 | 11.9285 | 11.4895 | 9.9733 | 9.1361 | 8.8459 | 8.8173 | 9.7797 | 9.5196 | 9.3585 | 9.0548 | 8.8382 | 8.4985 | 8.2202 | 7.858 | 7.4325 | 7.0296 | 5.8907 | 5.0787 | 4.5814 | 4.2464 | 14.4167 | 14.1566 | 13.9955 | 13.6918 | 13.4752 | 13.1355 | 12.8572 | 12.495 | 12.0695 | 11.6666 | 10.5277 | 9.7157 | 9.2184 | 8.8834 | 9.649 | 9.2864 | 9.2259 | 8.9629 | 8.7645 | 8.432 | 8.1658 | 7.8172 | 7.4206 | 7.0202 | 5.6597 | 4.9313 | 4.6787 | 4.675 | 14.286 | 13.9234 | 13.8629 | 13.5999 | 13.4015 | 13.069 | 12.8028 | 12.4542 | 12.0576 | 11.6572 | 10.2967 | 9.5683 | 9.3157 | 9.312 | 9.6456 | 9.2779 | 9.2149 | 8.9479 | 8.7558 | 8.4194 | 8.1614 | 7.8045 | 7.3934 | 7.021 | 4.8358 | -0.16337 | -4.274 | -7.0821 | 14.2826 | 13.9149 | 13.8519 | 13.5849 | 13.3928 | 13.0564 | 12.7984 | 12.4415 | 12.0304 | 11.658 | 9.4728 | 4.4736 | 0.363 | -2.4451 | 9.6823 | 9.328 | 9.284 | 9.0642 | 8.9209 | 8.6331 | 8.4383 | 8.1348 | 7.6312 | 6.3833 | 0.83832 | -3.6819 | -6.4411 | -5.8241 | 14.3193 | 13.965 | 13.965 | 13.7012 | 13.5579 | 13.2701 | 13.0753 | 12.7718 | 12.2682 | 11.0203 | 5.4753 | 0.95508 | -1.8041 | -1.1871 | 389631 | 401496 | CHADDERTON | WHITEGATE
| Fallowfield | 6.9342 | 6.6767 | 6.4194 | 6.1611 | 5.7827 | 5.3515 | 4.8511 | 4.4202 | 3.9746 | 3.4093 | 1.3188 | 0.071037 | -0.44005 | -0.47741 | 11.5712 | 11.3137 | 11.0564 | 10.7981 | 10.4197 | 9.9885 | 9.4881 | 9.0572 | 8.6116 | 8.0463 | 5.9558 | 4.708 | 4.1969 | 4.1596 | 7.0425 | 6.8622 | 6.512 | 6.2437 | 5.8711 | 5.4426 | 4.9298 | 4.4762 | 3.9991 | 3.4798 | 1.9436 | 0.71569 | -0.071724 | -0.64096 | 11.6795 | 11.4992 | 11.149 | 10.8807 | 10.5081 | 10.0796 | 9.5668 | 9.1132 | 8.6361 | 8.1168 | 6.5806 | 5.3527 | 4.5653 | 3.996 | 6.947 | 6.7064 | 6.4677 | 6.2246 | 5.8647 | 5.4525 | 4.9717 | 4.5588 | 4.1384 | 3.6253 | 1.694 | 0.55644 | 0.085844 | 0.041659 | 11.584 | 11.3434 | 11.1047 | 10.8616 | 10.5017 | 10.0895 | 9.6087 | 9.1958 | 8.7754 | 8.2623 | 6.331 | 5.1934 | 4.7228 | 4.6787 | 6.9431 | 6.6882 | 6.4324 | 6.163 | 5.783 | 5.3299 | 4.7564 | 4.2439 | 3.7871 | 3.2894 | 0.42342 | -5.1619 | -9.3683 | -12.2851 | 11.5801 | 11.3252 | 11.0694 | 10.8 | 10.42 | 9.9669 | 9.3934 | 8.8809 | 8.4241 | 7.9264 | 5.0604 | -0.52492 | -4.7313 | -7.6481 | 6.9485 | 6.6937 | 6.4683 | 6.2478 | 5.896 | 5.4999 | 5.0095 | 4.591 | 4.1177 | 2.7486 | -3.6901 | -8.7241 | -11.5199 | -10.7236 | 11.5855 | 11.3307 | 11.3307 | 10.8848 | 10.533 | 10.1369 | 9.6465 | 9.228 | 8.7547 | 7.3856 | 0.94694 | -4.0871 | -6.8829 | -6.0866 | 385608 | 393881 | WEST DIDSBURY | SOUTH MANCHESTER
| Farnworth | 7.7158 | 7.5732 | 7.409 | 7.1402 | 6.9097 | 6.5552 | 6.1226 | 5.7514 | 5.344 | 4.8394 | 2.9387 | 1.8216 | 1.4343 | 1.4601 | 11.7158 | 11.5732 | 11.409 | 11.1402 | 10.9097 | 10.5552 | 10.1226 | 9.7514 | 9.344 | 8.8394 | 6.9387 | 5.8216 | 5.4343 | 5.4601 | 7.8152 | 7.7472 | 7.4907 | 7.1982 | 6.9778 | 6.6422 | 6.2211 | 5.8569 | 5.4485 | 5.0021 | 3.7989 | 2.8917 | 2.2861 | 1.9327 | 11.8152 | 11.7472 | 11.4907 | 11.1982 | 10.9778 | 10.6422 | 10.2211 | 9.8569 | 9.4485 | 9.0021 | 7.7989 | 6.8917 | 6.2861 | 5.9327 | 7.7307 | 7.5995 | 7.4484 | 7.1923 | 6.995 | 6.6343 | 6.217 | 5.9167 | 5.5354 | 5.0828 | 3.3368 | 2.4521 | 2.1874 | 2.3126 | 11.7307 | 11.5995 | 11.4484 | 11.1923 | 10.995 | 10.6343 | 10.217 | 9.9167 | 9.5354 | 9.0828 | 7.3368 | 6.4521 | 6.1874 | 6.3126 | 7.7182 | 7.5747 | 7.4074 | 7.1292 | 6.9118 | 6.5127 | 6.0269 | 5.6728 | 5.3276 | 4.9504 | 2.4318 | -2.9722 | -7.1369 | -9.9575 | 11.7182 | 11.5747 | 11.4074 | 11.1292 | 10.9118 | 10.5127 | 10.0269 | 9.6728 | 9.3276 | 8.9504 | 6.4318 | 1.0278 | -3.1369 | -5.9575 | 7.7612 | 7.6313 | 7.4817 | 7.2513 | 7.077 | 6.7381 | 6.312 | 6.0213 | 5.6101 | 4.3643 | -1.5367 | -6.3517 | -9.1439 | -8.3901 | 11.7612 | 11.6313 | 11.6313 | 11.2513 | 11.077 | 10.7381 | 10.312 | 10.0213 | 9.6101 | 8.3643 | 2.4633 | -2.3517 | -5.1439 | -4.3901 | 373726 | 405532 | KEARSLEY LOCAL | KEARSLEY
| Feniscowles | 8.8874 | 8.7722 | 8.7569 | 8.7104 | 8.6129 | 8.555 | 8.512 | 8.4284 | 8.3379 | 8.2709 | 7.9201 | 7.7212 | 7.7024 | 7.8272 | 14.8874 | 14.7722 | 14.7569 | 14.7104 | 14.6129 | 14.555 | 14.512 | 14.4284 | 14.3379 | 14.2709 | 13.9201 | 13.7212 | 13.7024 | 13.8272 | 8.9831 | 8.9473 | 8.9093 | 8.8513 | 8.7541 | 8.7028 | 8.6636 | 8.584 | 8.4972 | 8.4419 | 8.261 | 8.0783 | 7.935 | 7.8957 | 14.9831 | 14.9473 | 14.9093 | 14.8513 | 14.7541 | 14.7028 | 14.6636 | 14.584 | 14.4972 | 14.4419 | 14.261 | 14.0783 | 13.935 | 13.8957 | 8.8884 | 8.7744 | 8.7601 | 8.7149 | 8.6193 | 8.563 | 8.5216 | 8.4397 | 8.3522 | 8.2918 | 8.0153 | 7.8592 | 7.8519 | 7.9762 | 14.8884 | 14.7744 | 14.7601 | 14.7149 | 14.6193 | 14.563 | 14.5216 | 14.4397 | 14.3522 | 14.2918 | 14.0153 | 13.8592 | 13.8519 | 13.9762 | 8.8943 | 8.787 | 8.7814 | 8.7467 | 8.6656 | 8.6238 | 8.594 | 8.5273 | 8.4623 | 8.433 | 7.9622 | 6.7319 | 5.764 | 5.1962 | 14.8943 | 14.787 | 14.7814 | 14.7467 | 14.6656 | 14.6238 | 14.594 | 14.5273 | 14.4623 | 14.433 | 13.9622 | 12.7319 | 11.764 | 11.1962 | 8.8877 | 8.7671 | 8.7565 | 8.7209 | 8.6361 | 8.5961 | 8.5718 | 8.513 | 8.4367 | 8.2168 | 6.8266 | 5.7294 | 5.1121 | 5.3984 | 14.8877 | 14.7671 | 14.7671 | 14.7209 | 14.6361 | 14.5961 | 14.5718 | 14.513 | 14.4367 | 14.2168 | 12.8266 | 11.7294 | 11.1121 | 11.3984 | 364660 | 425120 | LOWER DARWEN | ROCHDALE
| Ferodo | 5.5372 | 5.28 | 5.1692 | 4.972 | 4.8443 | 4.5498 | 4.2589 | 3.9902 | 3.5748 | 3.1718 | 1.7828 | 0.89612 | 0.58567 | 0.62497 | 16.4972 | 16.24 | 16.1292 | 15.932 | 15.8043 | 15.5098 | 15.2189 | 14.9502 | 14.5348 | 14.1318 | 12.7428 | 11.8561 | 11.5457 | 11.585 | 5.7838 | 5.6541 | 5.441 | 5.2162 | 5.125 | 4.8705 | 4.6136 | 4.3747 | 4.111 | 3.7998 | 2.9889 | 2.2685 | 1.7742 | 1.4583 | 16.7438 | 16.6141 | 16.401 | 16.1762 | 16.085 | 15.8305 | 15.5736 | 15.3347 | 15.071 | 14.7598 | 13.9489 | 13.2285 | 12.7342 | 12.4183 | 5.5407 | 5.2936 | 5.1957 | 5.0102 | 4.8956 | 4.6159 | 4.3395 | 4.0849 | 3.6842 | 3.3189 | 2.0845 | 1.3692 | 1.1268 | 1.2312 | 16.5007 | 16.2536 | 16.1557 | 15.9702 | 15.8556 | 15.5759 | 15.2995 | 15.0449 | 14.6442 | 14.2789 | 13.0445 | 12.3292 | 12.0868 | 12.1912 | 5.5561 | 5.3015 | 5.1871 | 4.9929 | 4.858 | 4.3654 | 4.0247 | 3.6906 | 3.4018 | 3.0491 | -1.5011 | -4.2049 | -5.8594 | -7.0981 | 16.5161 | 16.2615 | 16.1471 | 15.9529 | 15.818 | 15.3254 | 14.9847 | 14.6506 | 14.3618 | 14.0091 | 9.4589 | 6.7551 | 5.1006 | 3.8619 | 5.563 | 5.3091 | 5.203 | 5.0195 | 4.7269 | 4.4511 | 4.1603 | 0.34549 | 0.27485 | -0.19856 | -2.8707 | -5.1997 | -6.2541 | -5.9143 | 16.523 | 16.2691 | 16.2691 | 15.9795 | 15.6869 | 15.4111 | 15.1203 | 11.3055 | 11.2349 | 10.7614 | 8.0893 | 5.7603 | 4.7059 | 5.0457 | 405720 | 381338 | NEW MILLS | STALYBRIDGE
| Flat Lane | -0.0050124 | -0.19151 | -0.32136 | -0.45492 | -0.60042 | -0.76033 | -0.93384 | -1.117 | -1.3082 | -1.5625 | -2.4509 | -2.8814 | -3.0065 | -2.8377 | 5.495 | 5.3085 | 5.1786 | 5.0451 | 4.8996 | 4.7397 | 4.5662 | 4.383 | 4.1918 | 3.9375 | 3.0491 | 2.6186 | 2.4935 | 2.6623 | 0.075374 | -0.03722 | -0.17684 | -0.29246 | -0.41767 | -0.55842 | -0.72004 | -0.89315 | -1.074 | -1.2623 | -1.7766 | -2.2781 | -2.6338 | -2.85 | 5.5754 | 5.4628 | 5.3232 | 5.2075 | 5.0823 | 4.9416 | 4.78 | 4.6068 | 4.426 | 4.2377 | 3.7234 | 3.2219 | 2.8662 | 2.65 | -0.00086641 | -0.17791 | -0.3061 | -0.43219 | -0.56897 | -0.72061 | -0.88632 | -1.0618 | -1.2405 | -1.4665 | -2.2617 | -2.6344 | -2.7138 | -2.5449 | 5.4991 | 5.3221 | 5.1939 | 5.0678 | 4.931 | 4.7794 | 4.6137 | 4.4382 | 4.2595 | 4.0335 | 3.2383 | 2.8656 | 2.7862 | 2.9551 | -0.002753 | -0.19953 | -0.34102 | -0.48314 | -0.64944 | -0.83705 | -1.0489 | -1.2664 | -1.4607 | -1.6552 | -2.5213 | -3.6288 | -4.25 | -4.6789 | 5.4972 | 5.3005 | 5.159 | 5.0169 | 4.8506 | 4.663 | 4.4511 | 4.2336 | 4.0393 | 3.8448 | 2.9787 | 1.8712 | 1.25 | 0.82113 | -0.015059 | -0.23283 | -0.38342 | -0.52967 | -0.70552 | -0.88841 | -1.0825 | -1.2729 | -1.4435 | -1.7822 | -3.2928 | -4.2361 | -4.6134 | -4.3457 | 5.4849 | 5.2672 | 5.2672 | 4.9703 | 4.7945 | 4.6116 | 4.4175 | 4.2271 | 4.0565 | 3.7178 | 2.2072 | 1.2639 | 0.88663 | 1.1543 | 383248 | 456995 | NELSON | PADIHAM
| Frederick Rd | 5.1189 | 4.0424 | 3.8451 | 3.4756 | 3.1571 | 2.8047 | 2.4814 | 2.0518 | 1.6282 | 1.1075 | -0.93701 | -2.397 | -3.2597 | -3.6585 | 12.1189 | 11.0424 | 10.8451 | 10.4756 | 10.1571 | 9.8047 | 9.4814 | 9.0518 | 8.6282 | 8.1075 | 6.063 | 4.603 | 3.7403 | 3.3415 | 5.5147 | 4.828 | 4.6478 | 4.244 | 3.9037 | 3.5359 | 3.2241 | 2.815 | 2.3663 | 1.9195 | 0.36478 | -0.99801 | -2.0725 | -2.852 | 12.5147 | 11.828 | 11.6478 | 11.244 | 10.9037 | 10.5359 | 10.2241 | 9.815 | 9.3663 | 8.9195 | 7.3648 | 6.002 | 4.9275 | 4.148 | 5.1279 | 4.0615 | 3.8698 | 3.5093 | 3.1999 | 2.8576 | 2.5839 | 2.2109 | 1.814 | 1.3444 | -0.48272 | -1.6875 | -2.4269 | -2.6925 | 12.1279 | 11.0615 | 10.8698 | 10.5093 | 10.1999 | 9.8576 | 9.5839 | 9.2109 | 8.814 | 8.3444 | 6.5173 | 5.3125 | 4.5731 | 4.3075 | 5.128 | 4.0654 | 3.8849 | 3.5206 | 3.2225 | 2.8833 | 2.4643 | 1.9841 | 1.5663 | 1.1215 | -1.4243 | -5.8302 | -9.1269 | -11.4027 | 12.128 | 11.0654 | 10.8849 | 10.5206 | 10.2225 | 9.8833 | 9.4643 | 8.9841 | 8.5663 | 8.1215 | 5.5757 | 1.1698 | -2.1269 | -4.4027 | 5.1438 | 4.0794 | 3.9158 | 3.5781 | 3.31 | 3.007 | 2.588 | 2.1584 | 1.7337 | 0.70745 | -4.2318 | -8.2034 | -10.5412 | -10.2833 | 12.1438 | 11.0794 | 11.0794 | 10.5781 | 10.31 | 10.007 | 9.588 | 9.1584 | 8.7337 | 7.7074 | 2.7682 | -1.2034 | -3.5412 | -3.2833 | 381697 | 399348 | FREDERICK RD | KEARSLEY
| Fusehill | 2.2351 | 1.4808 | 1.5451 | 1.2455 | 1.2885 | 0.8407 | 0.48436 | 0.42093 | 0.004988 | -0.38737 | -1.5479 | -2.1995 | -2.3812 | -2.1087 | 8.7351 | 7.9808 | 8.0451 | 7.7455 | 7.7885 | 7.3407 | 6.9844 | 6.9209 | 6.505 | 6.1126 | 4.9521 | 4.3005 | 4.1188 | 4.3913 | 2.6366 | 2.2216 | 2.1112 | 1.7177 | 1.6859 | 1.2014 | 0.78647 | 0.64853 | 0.13765 | -0.28821 | -1.071 | -1.7128 | -2.0826 | -2.123 | 9.1366 | 8.7216 | 8.6112 | 8.2177 | 8.1859 | 7.7014 | 7.2865 | 7.1485 | 6.6376 | 6.2118 | 5.429 | 4.7872 | 4.4174 | 4.377 | 2.2456 | 1.5155 | 1.5996 | 1.3216 | 1.3835 | 0.96075 | 0.62821 | 0.5837 | 0.19766 | -0.14984 | -1.1726 | -1.7086 | -1.8332 | -1.531 | 8.7456 | 8.0155 | 8.0996 | 7.8216 | 7.8835 | 7.4608 | 7.1282 | 7.0837 | 6.6977 | 6.3502 | 5.3274 | 4.7914 | 4.6668 | 4.969 | 2.2626 | 1.5281 | 1.606 | 1.3157 | 1.3666 | 0.92375 | 0.54944 | 0.45784 | 0.057883 | -0.26045 | -1.8129 | -5.387 | -8.0438 | -9.7068 | 8.7626 | 8.0281 | 8.106 | 7.8157 | 7.8666 | 7.4237 | 7.0494 | 6.9578 | 6.5579 | 6.2395 | 4.6871 | 1.113 | -1.5438 | -3.2068 | 2.3032 | 1.596 | 1.6977 | 1.4444 | 1.5341 | 1.1489 | 0.83793 | 0.81569 | 0.41873 | -0.50766 | -4.5763 | -7.7153 | -9.4145 | -8.4875 | 8.8032 | 8.096 | 8.096 | 7.9444 | 8.0341 | 7.6489 | 7.3379 | 7.3157 | 6.9187 | 5.9923 | 1.9237 | -1.2153 | -2.9145 | -1.9875 | 341042 | 555452 | CARLISLE | HARKER
| Gale | 12.9836 | 12.7739 | 12.6383 | 12.5269 | 12.326 | 11.966 | 11.6099 | 11.4138 | 11.0413 | 10.6868 | 9.4766 | 8.7098 | 8.4379 | 8.32 | 17.6206 | 17.4109 | 17.2753 | 17.1639 | 16.963 | 16.603 | 16.2469 | 16.0508 | 15.6783 | 15.3238 | 14.1136 | 13.3468 | 13.0749 | 12.957 | 12.9987 | 12.8305 | 12.6424 | 12.5275 | 12.3298 | 11.9844 | 11.6398 | 11.4541 | 11.0856 | 10.7821 | 9.9426 | 9.2203 | 8.7672 | 8.336 | 17.6357 | 17.4675 | 17.2794 | 17.1645 | 16.9668 | 16.6214 | 16.2768 | 16.0911 | 15.7226 | 15.4191 | 14.5796 | 13.8573 | 13.4042 | 12.973 | 12.9841 | 12.7954 | 12.6731 | 12.5714 | 12.3928 | 12.0494 | 11.7096 | 11.5263 | 11.1744 | 10.8541 | 9.7235 | 9.0306 | 8.7824 | 8.721 | 17.6211 | 17.4324 | 17.3101 | 17.2084 | 17.0298 | 16.6864 | 16.3466 | 16.1633 | 15.8114 | 15.4911 | 14.3605 | 13.6676 | 13.4194 | 13.358 | 12.9857 | 12.7782 | 12.6425 | 12.5276 | 12.3381 | 11.9869 | 11.6268 | 11.4245 | 11.0888 | 10.8185 | 9.0316 | 4.721 | 1.2484 | -1.3181 | 17.6227 | 17.4152 | 17.2795 | 17.1646 | 16.9751 | 16.6239 | 16.2638 | 16.0615 | 15.7258 | 15.4555 | 13.6686 | 9.358 | 5.8854 | 3.3189 | 13.0219 | 12.8249 | 12.7035 | 12.6189 | 12.4611 | 12.1607 | 11.8548 | 11.7101 | 11.2952 | 10.2804 | 5.6592 | 1.759 | -0.57219 | -0.23693 | 17.6589 | 17.4619 | 17.4619 | 17.2559 | 17.0981 | 16.7977 | 16.4918 | 16.3471 | 15.9322 | 14.9174 | 10.2962 | 6.396 | 4.0648 | 4.4001 | 389570 | 414943 | BELFIELD | ROCHDALE
| Garstang | 6.6983 | 6.0654 | 5.6975 | 5.1773 | 4.7749 | 4.2101 | 3.6251 | 3.0378 | 2.4228 | 1.6178 | -1.1865 | -2.6497 | -2.9981 | -2.559 | 0.79833 | 0.16544 | -0.20251 | -0.72275 | -1.1251 | -1.6899 | -2.2749 | -2.8622 | -3.4772 | -4.2822 | -7.0865 | -8.5497 | -8.8981 | -8.459 | 6.9436 | 6.5344 | 6.1497 | 5.7198 | 5.4062 | 4.9317 | 4.4338 | 3.9213 | 3.3671 | 2.8014 | 1.2023 | -0.29886 | -1.3119 | -1.9605 | 1.0436 | 0.63441 | 0.24972 | -0.18019 | -0.49376 | -0.96832 | -1.4662 | -1.9787 | -2.5329 | -3.0986 | -4.6977 | -6.1989 | -7.2119 | -7.8605 | 6.7062 | 6.0995 | 5.7573 | 5.264 | 4.8836 | 4.3422 | 3.7785 | 3.2111 | 2.6306 | 1.9073 | -0.64587 | -1.8755 | -2.101 | -1.5896 | 0.80617 | 0.19946 | -0.14274 | -0.63603 | -1.0164 | -1.5578 | -2.1215 | -2.6889 | -3.2694 | -3.9927 | -6.5459 | -7.7755 | -8.001 | -7.4896 | 6.7158 | 6.0636 | 5.6773 | 5.1521 | 4.7144 | 4.0887 | 3.4039 | 2.7153 | 2.0894 | 1.4562 | -1.1607 | -4.2836 | -5.7755 | -6.9721 | 0.81583 | 0.16363 | -0.22273 | -0.74786 | -1.1856 | -1.8113 | -2.4961 | -3.1847 | -3.8106 | -4.4438 | -7.0607 | -10.1836 | -11.6755 | -12.8721 | 6.621 | 5.8857 | 5.5004 | 4.9859 | 4.5419 | 3.9525 | 3.3377 | 2.7547 | 2.2578 | 1.3443 | -2.746 | -5.2281 | -6.0466 | -5.3689 | 0.72103 | -0.014297 | -0.014297 | -0.91406 | -1.3581 | -1.9475 | -2.5623 | -3.1453 | -3.6422 | -4.5557 | -8.646 | -11.1281 | -11.9466 | -11.2689 | 348319 | 445221 | THORNTON | STANAH
| Gatley | 1.427 | 1.2312 | 1.1487 | 1.069 | 0.89007 | 0.66973 | 0.3887 | 0.23255 | 0.005878 | -0.24298 | -1.0964 | -1.5148 | -1.5812 | -1.5075 | 11.927 | 11.7312 | 11.6487 | 11.569 | 11.3901 | 11.1697 | 10.8887 | 10.7325 | 10.5059 | 10.257 | 9.4036 | 8.9852 | 8.9188 | 8.9925 | 1.5172 | 1.3944 | 1.2612 | 1.174 | 1.0053 | 0.80263 | 0.53635 | 0.38626 | 0.17162 | -0.048027 | -0.735 | -1.1976 | -1.4337 | -1.5731 | 12.0172 | 11.8944 | 11.7612 | 11.674 | 11.5053 | 11.3026 | 11.0363 | 10.8863 | 10.6716 | 10.452 | 9.765 | 9.3024 | 9.0663 | 8.9269 | 1.4368 | 1.2502 | 1.1762 | 1.1026 | 0.93293 | 0.72213 | 0.451 | 0.30261 | 0.088047 | -0.13736 | -0.90704 | -1.2633 | -1.3109 | -1.2251 | 11.9368 | 11.7502 | 11.6762 | 11.6026 | 11.4329 | 11.2221 | 10.951 | 10.8026 | 10.588 | 10.3626 | 9.593 | 9.2367 | 9.1891 | 9.2749 | 1.4357 | 1.2503 | 1.1789 | 1.1082 | 0.94903 | 0.74951 | 0.48356 | 0.33985 | 0.15787 | -0.025215 | -1.1208 | -3.4079 | -5.1669 | -6.4294 | 11.9357 | 11.7503 | 11.6789 | 11.6082 | 11.449 | 11.2495 | 10.9836 | 10.8399 | 10.6579 | 10.4748 | 9.3792 | 7.0921 | 5.3331 | 4.0706 | 1.4408 | 1.2453 | 1.1812 | 1.1365 | 1.0082 | 0.84849 | 0.6186 | 0.51463 | 0.31541 | -0.24057 | -2.8519 | -4.9144 | -6.0765 | -5.7248 | 11.9408 | 11.7453 | 11.7453 | 11.6365 | 11.5082 | 11.3485 | 11.1186 | 11.0146 | 10.8154 | 10.2594 | 7.6481 | 5.5856 | 4.4235 | 4.7752 | 384242 | 388388 | MOSS NOOK | SOUTH MANCHESTER
| Gidlow | 6.4746 | 6.1319 | 5.8141 | 5.4156 | 4.9144 | 4.3441 | 3.7483 | 3.1195 | 2.4861 | 1.7435 | -0.75561 | -1.9974 | -2.2909 | -2.0565 | 11.1116 | 10.7689 | 10.4511 | 10.0526 | 9.5514 | 8.9811 | 8.3853 | 7.7565 | 7.1231 | 6.3805 | 3.8814 | 2.6396 | 2.3461 | 2.5805 | 6.554 | 6.2734 | 5.8932 | 5.5151 | 5.0689 | 4.555 | 4.0133 | 3.4374 | 2.8472 | 2.235 | 0.49498 | -0.78378 | -1.5529 | -2.0525 | 11.191 | 10.9104 | 10.5302 | 10.1521 | 9.7059 | 9.192 | 8.6503 | 8.0744 | 7.4842 | 6.872 | 5.132 | 3.8532 | 3.0841 | 2.5845 | 6.4858 | 6.168 | 5.8708 | 5.4879 | 5.0063 | 4.4571 | 3.8816 | 3.2727 | 2.6694 | 1.997 | -0.3288 | -1.4349 | -1.6318 | -1.4297 | 11.1228 | 10.805 | 10.5078 | 10.1249 | 9.6433 | 9.0941 | 8.5186 | 7.9097 | 7.3064 | 6.634 | 4.3082 | 3.2021 | 3.0052 | 3.2073 | 6.4771 | 6.1377 | 5.8333 | 5.4523 | 4.9944 | 4.4711 | 3.8998 | 3.3056 | 2.7867 | 2.2565 | -0.91516 | -7.4117 | -12.4132 | -15.7766 | 11.1141 | 10.7747 | 10.4703 | 10.0893 | 9.6314 | 9.1081 | 8.5368 | 7.9426 | 7.4237 | 6.8935 | 3.7218 | -2.7747 | -7.7762 | -11.1396 | 6.5106 | 6.1527 | 5.8588 | 5.5339 | 5.1217 | 4.6836 | 4.2129 | 3.7403 | 3.153 | 1.5449 | -5.82 | -11.6265 | -14.8939 | -13.8629 | 11.1476 | 10.7897 | 10.7897 | 10.1709 | 9.7587 | 9.3206 | 8.8499 | 8.3773 | 7.79 | 6.1819 | -1.183 | -6.9895 | -10.2569 | -9.2259 | 357620 | 406662 | WIGAN | KIRKBY
| Gillsrow | 0.53134 | 0.38269 | 0.3018 | 0.19828 | 0.029915 | -0.089466 | -0.21713 | -0.37499 | -0.54867 | -0.73646 | -1.4301 | -1.9577 | -2.3029 | -2.1454 | 2.7313 | 2.5827 | 2.5018 | 2.3983 | 2.2299 | 2.1105 | 1.9829 | 1.825 | 1.6513 | 1.4635 | 0.76993 | 0.24229 | -0.10293 | 0.054604 | 0.59048 | 0.49108 | 0.39286 | 0.28501 | 0.11687 | -0.0034512 | -0.13107 | -0.29321 | -0.4692 | -0.62907 | -1.0646 | -1.478 | -2.1549 | -2.5834 | 2.7905 | 2.6911 | 2.5929 | 2.485 | 2.3169 | 2.1965 | 2.0689 | 1.9068 | 1.7308 | 1.5709 | 1.1354 | 0.72202 | 0.0451 | -0.38344 | 0.53512 | 0.39054 | 0.31333 | 0.21398 | 0.051756 | -0.062236 | -0.18487 | -0.33719 | -0.50261 | -0.67374 | -1.3241 | -1.6393 | -1.8926 | -1.7388 | 2.7351 | 2.5905 | 2.5133 | 2.414 | 2.2518 | 2.1378 | 2.0151 | 1.8628 | 1.6974 | 1.5263 | 0.87592 | 0.56065 | 0.30738 | 0.46118 | 0.53811 | 0.39635 | 0.32843 | 0.23499 | 0.073552 | -0.036873 | -0.15414 | -0.29255 | -0.42559 | -0.61387 | -1.4014 | -2.026 | -2.295 | -2.3799 | 2.7381 | 2.5964 | 2.5284 | 2.435 | 2.2736 | 2.1631 | 2.0459 | 1.9074 | 1.7744 | 1.5861 | 0.7986 | 0.174 | -0.095011 | -0.17987 | 0.50595 | 0.3412 | 0.27834 | 0.19687 | 0.037942 | -0.05909 | -0.16327 | -0.27137 | -0.3979 | -0.64332 | -1.6617 | -2.1874 | -2.3421 | -2.149 | 2.7059 | 2.5412 | 2.5412 | 2.3969 | 2.2379 | 2.1409 | 2.0367 | 1.9286 | 1.8021 | 1.5567 | 0.53831 | 0.012629 | -0.1421 | 0.051005 | 337117 | 526444 | PENRITH & SHAP | HUTTON
| Glaxo | 6.559 | 6.4637 | 6.4476 | 6.4135 | 6.441 | 6.3999 | 6.3447 | 6.2437 | 6.2586 | 6.1723 | 4.6477 | 3.0906 | -0.328 | -0.19998 | 18.509 | 18.4137 | 18.3976 | 18.3635 | 18.391 | 18.3499 | 18.2947 | 18.1937 | 18.2086 | 18.1223 | 16.5977 | 15.0406 | 11.622 | 11.75 | 6.7326 | 6.7785 | 6.7085 | 6.6342 | 6.6318 | 6.5823 | 6.5131 | 6.3966 | 6.3901 | 6.2825 | 6.2124 | 6.1562 | 6.1171 | 6.2016 | 18.6826 | 18.7285 | 18.6585 | 18.5842 | 18.5818 | 18.5323 | 18.4631 | 18.3466 | 18.3401 | 18.2325 | 18.1624 | 18.1062 | 18.0671 | 18.1516 | 6.5598 | 6.4657 | 6.4502 | 6.417 | 6.4459 | 6.4053 | 6.3519 | 6.2523 | 6.2679 | 6.1852 | 4.6696 | 3.1259 | -0.28507 | -0.14841 | 18.5098 | 18.4157 | 18.4002 | 18.367 | 18.3959 | 18.3553 | 18.3019 | 18.2023 | 18.2179 | 18.1352 | 16.6196 | 15.0759 | 11.6649 | 11.8016 | 6.5721 | 6.4905 | 6.488 | 6.4679 | 6.5088 | 6.4818 | 6.4404 | 6.3545 | 6.383 | 6.3143 | -0.1275 | -1.0793 | -1.1547 | -1.0181 | 18.5221 | 18.4405 | 18.438 | 18.4179 | 18.4588 | 18.4318 | 18.3904 | 18.3045 | 18.333 | 18.2643 | 11.8225 | 10.8707 | 10.7953 | 10.9319 | 6.5721 | 6.489 | 6.486 | 6.4664 | 6.5082 | 6.4826 | 6.4423 | 5.5167 | 4.0556 | 0.26875 | -1.2617 | -1.1845 | -1.2302 | -0.98781 | 18.5221 | 18.439 | 18.439 | 18.4164 | 18.4582 | 18.4326 | 18.3923 | 17.4667 | 16.0056 | 12.2187 | 10.6883 | 10.7655 | 10.7198 | 10.9622 | 330458 | 477825 | ULVERSTON | HARKER
| Glossop | 8.8339 | 8.528 | 8.2811 | 7.9498 | 7.7097 | 7.3591 | 6.8942 | 6.5169 | 6.0909 | 5.5825 | 3.8442 | 2.871 | 2.5302 | 2.5714 | 13.4709 | 13.165 | 12.9181 | 12.5868 | 12.3467 | 11.9961 | 11.5312 | 11.1539 | 10.7279 | 10.2195 | 8.4812 | 7.508 | 7.1672 | 7.2084 | 8.9611 | 8.7582 | 8.4273 | 8.0846 | 7.8559 | 7.5257 | 7.076 | 6.7107 | 6.2859 | 5.8343 | 4.5549 | 3.6249 | 3.0558 | 2.7457 | 13.5981 | 13.3952 | 13.0643 | 12.7216 | 12.4929 | 12.1627 | 11.713 | 11.3477 | 10.9229 | 10.4713 | 9.1919 | 8.2619 | 7.6928 | 7.3827 | 8.8409 | 8.5487 | 8.3162 | 7.9991 | 7.7753 | 7.4421 | 6.9955 | 6.6349 | 6.2323 | 5.7713 | 4.2036 | 3.3804 | 3.0999 | 3.1821 | 13.4779 | 13.1857 | 12.9532 | 12.6361 | 12.4123 | 12.0791 | 11.6325 | 11.2719 | 10.8693 | 10.4083 | 8.8406 | 8.0174 | 7.7369 | 7.8191 | 8.8437 | 8.5455 | 8.3101 | 7.9913 | 7.779 | 7.4586 | 7.0173 | 6.6645 | 6.314 | 5.9377 | 3.4676 | -1.7844 | -5.9523 | -8.6116 | 13.4807 | 13.1825 | 12.9471 | 12.6283 | 12.416 | 12.0956 | 11.6543 | 11.3015 | 10.951 | 10.5747 | 8.1046 | 2.8526 | -1.3153 | -3.9746 | 8.8728 | 8.575 | 8.3604 | 8.0952 | 7.9389 | 7.6908 | 7.3173 | 7.0391 | 6.5948 | 5.3306 | -0.5373 | -5.271 | -8.0145 | -7.1761 | 13.5098 | 13.212 | 13.212 | 12.7322 | 12.5759 | 12.3278 | 11.9543 | 11.6761 | 11.2318 | 9.9676 | 4.0997 | -0.63396 | -3.3775 | -2.5391 | 402300 | 394074 | HYDE | STALYBRIDGE
| Golborne | 3.1311 | 1.4765 | 0.82021 | -0.12023 | -0.72892 | -2.3873 | -3.946 | -0.45589 | -1.9838 | -3.4178 | -7.1438 | -9.5306 | -10.2911 | -10.4311 | 8.6311 | 6.9765 | 6.3202 | 5.3798 | 4.7711 | 3.1127 | 1.554 | 0.54411 | -0.98385 | -2.4178 | -6.1438 | -8.5306 | -9.2911 | -9.4311 | 3.9658 | 3.0769 | 2.4402 | 1.6885 | 1.3043 | 0.27791 | -0.66089 | 3.2401 | 2.2004 | 1.1995 | -1.4932 | -3.5595 | -4.8495 | -5.4894 | 9.4658 | 8.5769 | 7.9402 | 7.1885 | 6.8043 | 5.7779 | 4.8391 | 4.2401 | 3.2004 | 2.1995 | -0.4932 | -2.5595 | -3.8495 | -4.4894 | 3.1404 | 1.5082 | 0.87246 | -0.050281 | -0.61826 | -2.2463 | -3.7768 | -0.32841 | -1.817 | -3.1558 | -6.4681 | -8.282 | -8.8057 | -8.6036 | 8.6404 | 7.0082 | 6.3725 | 5.4497 | 4.8817 | 3.2537 | 1.7232 | 0.67159 | -0.817 | -2.1558 | -5.4681 | -7.282 | -7.8057 | -7.6036 | 3.1665 | 1.5597 | 0.96556 | 0.056642 | -0.38154 | -1.8919 | -3.3038 | 0.37341 | -0.81384 | -1.8585 | -6.7275 | -15.3522 | -21.672 | -25.5623 | 8.6665 | 7.0597 | 6.4656 | 5.5566 | 5.1185 | 3.6081 | 2.1962 | 1.3734 | 0.18616 | -0.85854 | -5.7275 | -14.3522 | -20.672 | -24.5623 | 3.1707 | 1.5086 | 0.91155 | 0.071472 | -0.32126 | -1.7272 | -3.0633 | 0.7016 | -0.71602 | -3.1119 | -12.7288 | -20.4964 | -24.7365 | -23.1408 | 8.6707 | 7.0086 | 7.0086 | 5.5715 | 5.1787 | 3.7728 | 2.4367 | 1.7016 | 0.28398 | -2.1119 | -11.7288 | -19.4964 | -23.7365 | -22.1408 | 360621 | 397766 | GOLBORNE | BOLD
| Gowhole | 5.2542 | 4.6867 | 4.0919 | 3.4029 | 2.7701 | 2.0006 | 1.0814 | 0.20959 | -0.67079 | -1.7892 | -5.6348 | -7.47 | -7.7559 | -7.1882 | 9.8912 | 9.3237 | 8.7289 | 8.0399 | 7.4071 | 6.6376 | 5.7184 | 4.8466 | 3.9662 | 2.8478 | -0.99775 | -2.833 | -3.1189 | -2.5512 | 5.3877 | 4.9461 | 4.3401 | 3.8099 | 3.3583 | 2.7698 | 2.0438 | 1.362 | 0.61593 | -0.15707 | -2.4731 | -4.1267 | -5.1094 | -5.6362 | 10.0247 | 9.5831 | 8.9771 | 8.4469 | 7.9953 | 7.4068 | 6.6808 | 5.999 | 5.2529 | 4.4799 | 2.1639 | 0.51027 | -0.47242 | -0.99916 | 5.2559 | 4.7117 | 4.1435 | 3.485 | 2.8847 | 2.1494 | 1.265 | 0.42524 | -0.41263 | -1.4252 | -4.8823 | -6.4378 | -6.6417 | -6.0703 | 9.8929 | 9.3487 | 8.7805 | 8.122 | 7.5217 | 6.7864 | 5.902 | 5.0622 | 4.2244 | 3.2118 | -0.2453 | -1.8008 | -2.0047 | -1.4333 | 5.2647 | 4.6797 | 4.0818 | 3.4225 | 2.8144 | 2.0528 | 1.1105 | 0.21388 | -0.58062 | -1.4062 | -5.3149 | -11.6334 | -15.6361 | -18.4269 | 9.9017 | 9.3167 | 8.7188 | 8.0595 | 7.4514 | 6.6898 | 5.7475 | 4.8509 | 4.0564 | 3.2308 | -0.67785 | -6.9964 | -10.9991 | -13.7899 | 5.1976 | 4.5099 | 3.9249 | 3.3258 | 2.7868 | 2.147 | 1.3488 | 0.64767 | -0.039436 | -1.6723 | -9.1111 | -14.2369 | -16.6539 | -15.389 | 9.8346 | 9.1469 | 9.1469 | 7.9628 | 7.4238 | 6.784 | 5.9858 | 5.2847 | 4.5976 | 2.9647 | -4.4741 | -9.5999 | -12.0169 | -10.752 | 401104 | 383846 | NEW MILLS | STALYBRIDGE
| Grane Rd & Prinny Hill | 9.2062 | 8.9753 | 8.8769 | 8.7203 | 8.5234 | 8.2916 | 8.0387 | 7.7814 | 7.5122 | 7.2222 | 6.3347 | 6.0553 | 6.176 | 6.4312 | 14.3062 | 14.0753 | 13.9769 | 13.8203 | 13.6234 | 13.3916 | 13.1387 | 12.8814 | 12.6122 | 12.3222 | 11.4347 | 11.1553 | 11.276 | 11.5312 | 9.4005 | 9.3322 | 9.1722 | 8.988 | 8.7968 | 8.5849 | 8.3496 | 8.1072 | 7.8583 | 7.6124 | 6.9346 | 6.5062 | 6.3482 | 6.3511 | 14.5005 | 14.4322 | 14.2722 | 14.088 | 13.8968 | 13.6849 | 13.4496 | 13.2072 | 12.9583 | 12.7124 | 12.0346 | 11.6062 | 11.4482 | 11.4511 | 9.2091 | 8.982 | 8.8876 | 8.7346 | 8.5476 | 8.3217 | 8.0745 | 7.8202 | 7.5544 | 7.2892 | 6.48 | 6.2418 | 6.3787 | 6.6465 | 14.3091 | 14.082 | 13.9876 | 13.8346 | 13.6476 | 13.4217 | 13.1745 | 12.9202 | 12.6544 | 12.3892 | 11.58 | 11.3418 | 11.4787 | 11.7465 | 9.2233 | 9.0159 | 8.9487 | 8.8288 | 8.6862 | 8.5198 | 8.3408 | 8.1699 | 8.0198 | 7.8791 | 7.1856 | 6.0655 | 5.372 | 4.9798 | 14.3233 | 14.1159 | 14.0487 | 13.9288 | 13.7862 | 13.6198 | 13.4408 | 13.2699 | 13.1198 | 12.9791 | 12.2856 | 11.1655 | 10.472 | 10.0798 | 9.206 | 8.9643 | 8.8888 | 8.7765 | 8.6365 | 8.4941 | 8.3383 | 8.2007 | 8.0627 | 7.7422 | 6.3485 | 5.48 | 5.1451 | 5.5275 | 14.306 | 14.0643 | 14.0643 | 13.8765 | 13.7365 | 13.5941 | 13.4383 | 13.3007 | 13.1627 | 12.8422 | 11.4485 | 10.58 | 10.2451 | 10.6275 | 378312 | 422726 | ROSSENDALE | PADIHAM
| Grange | 4.9337 | 4.7952 | 4.5957 | 4.3237 | 4.1363 | 3.817 | 3.4641 | 3.1913 | 2.872 | 2.4157 | 0.87639 | 0.1272 | -0.035418 | 0.23075 | 10.9337 | 10.7952 | 10.5957 | 10.3237 | 10.1363 | 9.817 | 9.4641 | 9.1913 | 8.872 | 8.4157 | 6.8764 | 6.1272 | 5.9646 | 6.2308 | 4.9382 | 4.8029 | 4.5758 | 4.3535 | 4.2133 | 3.9348 | 3.6228 | 3.403 | 3.1179 | 2.7847 | 1.9665 | 1.2936 | 0.85619 | 0.5733 | 10.9382 | 10.8029 | 10.5758 | 10.3535 | 10.2133 | 9.9348 | 9.6228 | 9.403 | 9.1179 | 8.7847 | 7.9665 | 7.2936 | 6.8562 | 6.5733 | 4.9397 | 4.8126 | 4.627 | 4.3723 | 4.2002 | 3.8989 | 3.5532 | 3.2845 | 2.9828 | 2.5698 | 1.1715 | 0.50451 | 0.362 | 0.59945 | 10.9397 | 10.8126 | 10.627 | 10.3723 | 10.2002 | 9.8989 | 9.5532 | 9.2845 | 8.9828 | 8.5698 | 7.1715 | 6.5045 | 6.362 | 6.5994 | 4.9327 | 4.7739 | 4.5553 | 4.2704 | 4.055 | 3.6913 | 3.2692 | 2.9416 | 2.6243 | 2.2594 | 0.65571 | -2.2406 | -4.1992 | -5.7339 | 10.9327 | 10.7739 | 10.5553 | 10.2704 | 10.055 | 9.6913 | 9.2692 | 8.9416 | 8.6243 | 8.2594 | 6.6557 | 3.7594 | 1.8008 | 0.26612 | 4.9349 | 4.7626 | 4.5513 | 4.2838 | 4.0861 | 3.7648 | 3.4048 | 3.1586 | 2.8957 | 2.1518 | -1.2186 | -3.6567 | -4.9563 | -4.5429 | 10.9349 | 10.7626 | 10.7626 | 10.2838 | 10.0861 | 9.7648 | 9.4048 | 9.1586 | 8.8957 | 8.1518 | 4.7814 | 2.3433 | 1.0437 | 1.4571 | 340240 | 478314 | ULVERSTON | HARKER
| Great Harwood | 9.8388 | 9.704 | 9.586 | 9.4189 | 9.2207 | 8.9966 | 8.7449 | 8.4729 | 8.2049 | 7.8627 | 6.6863 | 5.9877 | 5.7682 | 5.8671 | 17.9588 | 17.824 | 17.706 | 17.5389 | 17.3407 | 17.1166 | 16.8649 | 16.5929 | 16.3249 | 15.9827 | 14.8063 | 14.1077 | 13.8882 | 13.9871 | 9.8761 | 9.7676 | 9.6054 | 9.4345 | 9.2444 | 9.028 | 8.7808 | 8.5108 | 8.2235 | 7.7583 | 7.2192 | 6.6049 | 6.2189 | 5.9566 | 17.9961 | 17.8876 | 17.7254 | 17.5545 | 17.3644 | 17.148 | 16.9008 | 16.6308 | 16.3435 | 15.8783 | 15.3392 | 14.7249 | 14.3389 | 14.0766 | 9.8456 | 9.7225 | 9.6167 | 9.4603 | 9.274 | 9.062 | 8.8225 | 8.5625 | 8.3117 | 8.0048 | 6.9274 | 6.3335 | 6.166 | 6.2841 | 17.9656 | 17.8425 | 17.7367 | 17.5803 | 17.394 | 17.182 | 16.9425 | 16.6825 | 16.4317 | 16.1248 | 15.0474 | 14.4535 | 14.286 | 14.4041 | 9.8395 | 9.7028 | 9.5878 | 9.4292 | 9.2413 | 9.0217 | 8.7504 | 8.458 | 8.2118 | 7.9533 | 6.185 | 2.1295 | -0.92673 | -2.8349 | 17.9595 | 17.8228 | 17.7078 | 17.5492 | 17.3613 | 17.1417 | 16.8704 | 16.578 | 16.3318 | 16.0733 | 14.305 | 10.2495 | 7.1933 | 5.2851 | 9.8702 | 9.7423 | 9.6419 | 9.5155 | 9.3439 | 9.1592 | 8.9382 | 8.7046 | 8.3852 | 7.426 | 2.9699 | -0.62187 | -2.5508 | -1.7779 | 17.9902 | 17.8623 | 17.8623 | 17.6355 | 17.4639 | 17.2792 | 17.0582 | 16.8246 | 16.5052 | 15.546 | 11.0899 | 7.4981 | 5.5692 | 6.3421 | 373765 | 431955 | HUNCOAT | PADIHAM
| Green Lane (Altrincham) | 6.3801 | 6.0071 | 5.3917 | 4.9094 | 4.6954 | 4.0716 | 3.3732 | 2.7576 | 2.0458 | 1.3699 | -0.87672 | -1.9451 | -1.8972 | -1.6435 | 11.0171 | 10.6441 | 10.0287 | 9.5464 | 9.3324 | 8.7086 | 8.0102 | 7.3946 | 6.6828 | 6.0069 | 3.7603 | 2.6919 | 2.7398 | 2.9935 | 6.5355 | 6.2906 | 5.6367 | 5.2148 | 5.0942 | 4.5697 | 3.9663 | 3.4399 | 2.8079 | 2.2752 | 0.60359 | -0.61407 | -1.0952 | -1.4988 | 11.1725 | 10.9276 | 10.2737 | 9.8518 | 9.7312 | 9.2067 | 8.6033 | 8.0769 | 7.4449 | 6.9122 | 5.2406 | 4.0229 | 3.5418 | 3.1382 | 6.3882 | 6.0287 | 5.4295 | 4.9586 | 4.757 | 4.1503 | 3.4685 | 2.8671 | 2.1816 | 1.5722 | -0.45856 | -1.4018 | -1.3692 | -1.1508 | 11.0252 | 10.6657 | 10.0665 | 9.5956 | 9.394 | 8.7873 | 8.1055 | 7.5041 | 6.8186 | 6.2092 | 4.1784 | 3.2352 | 3.2678 | 3.4862 | 6.3999 | 6.057 | 5.4919 | 5.066 | 4.937 | 4.4141 | 3.8174 | 3.317 | 2.8013 | 2.3945 | -0.46778 | -6.814 | -11.5693 | -15.0254 | 11.0369 | 10.694 | 10.1289 | 9.703 | 9.574 | 9.0511 | 8.4544 | 7.954 | 7.4383 | 7.0315 | 4.1692 | -2.177 | -6.9323 | -10.3884 | 6.3078 | 5.8395 | 5.2797 | 4.921 | 4.8644 | 4.441 | 3.9356 | 3.5481 | 2.9418 | 1.4491 | -5.578 | -11.2968 | -14.313 | -13.3459 | 10.9448 | 10.4765 | 10.4765 | 9.558 | 9.5014 | 9.078 | 8.5726 | 8.1851 | 7.5788 | 6.0861 | -0.94105 | -6.6598 | -9.676 | -8.7089 | 378744 | 387772 | ALTRINCHAM | CARRINGTON
| Green Lane (Hazel Grove) | 4.0855 | 3.8925 | 3.4826 | 3.0426 | 2.635 | 2.0586 | 1.2318 | 0.72876 | 0.19968 | -0.57942 | -2.96 | -3.9654 | -4.1589 | -3.7524 | 8.7225 | 8.5295 | 8.1196 | 7.6796 | 7.272 | 6.6956 | 5.8688 | 5.3658 | 4.8367 | 4.0576 | 1.677 | 0.67163 | 0.47811 | 0.88462 | 4.2137 | 4.1185 | 3.6279 | 3.211 | 2.8727 | 2.3739 | 1.6257 | 1.1949 | 0.72179 | 0.06571 | -1.7034 | -2.7958 | -3.4924 | -3.7489 | 8.8507 | 8.7555 | 8.2649 | 7.848 | 7.5097 | 7.0109 | 6.2627 | 5.8319 | 5.3588 | 4.7027 | 2.9336 | 1.8412 | 1.1446 | 0.88811 | 4.0962 | 3.9159 | 3.5215 | 3.0941 | 2.701 | 2.1416 | 1.3337 | 0.84444 | 0.33951 | -0.37366 | -2.5369 | -3.3922 | -3.5446 | -3.1424 | 8.7332 | 8.5529 | 8.1585 | 7.7311 | 7.338 | 6.7786 | 5.9707 | 5.4814 | 4.9765 | 4.2633 | 2.1001 | 1.2448 | 1.0924 | 1.4946 | 4.1007 | 3.9269 | 3.551 | 3.1526 | 2.813 | 2.316 | 1.5707 | 1.1551 | 0.79389 | 0.25707 | -2.9019 | -9.6254 | -15.0207 | -18.5431 | 8.7377 | 8.5639 | 8.188 | 7.7896 | 7.45 | 6.953 | 6.2077 | 5.7921 | 5.4309 | 4.8941 | 1.7351 | -4.9884 | -10.3837 | -13.9061 | 4.1294 | 3.9171 | 3.5287 | 3.1822 | 2.9054 | 2.5063 | 1.8538 | 1.548 | 1.0805 | -0.63281 | -8.3254 | -14.3425 | -17.9223 | -16.6018 | 8.7664 | 8.5541 | 8.5541 | 7.8192 | 7.5424 | 7.1433 | 6.4908 | 6.185 | 5.7175 | 4.0042 | -3.6884 | -9.7055 | -13.2853 | -11.9648 | 391570 | 387132 | HAZEL GROVE | BREDBURY
| Green St T11 | 0.91844 | 0.6235 | 0.57279 | 0.46209 | 0.29587 | 0.095596 | -0.11707 | -0.32472 | -0.52954 | -0.75273 | -1.5423 | -1.9921 | -2.1333 | -2.0846 | 5.6684 | 5.3735 | 5.3228 | 5.2121 | 5.0459 | 4.8456 | 4.6329 | 4.4253 | 4.2205 | 3.9973 | 3.2077 | 2.7579 | 2.6167 | 2.6654 | 1.2039 | 1.1414 | 0.98177 | 0.80163 | 0.59312 | 0.37818 | 0.13977 | -0.12425 | -0.39636 | -0.68184 | -1.3346 | -1.8049 | -2.0498 | -2.1431 | 5.9539 | 5.8914 | 5.7318 | 5.5516 | 5.3431 | 5.1282 | 4.8898 | 4.6258 | 4.3536 | 4.0682 | 3.4154 | 2.9451 | 2.7002 | 2.6069 | 0.92577 | 0.64021 | 0.59933 | 0.4975 | 0.34159 | 0.15176 | -0.050316 | -0.24737 | -0.43851 | -0.63646 | -1.3462 | -1.7216 | -1.8289 | -1.7591 | 5.6758 | 5.3902 | 5.3493 | 5.2475 | 5.0916 | 4.9018 | 4.6997 | 4.5026 | 4.3115 | 4.1135 | 3.4038 | 3.0284 | 2.9211 | 2.9909 | 0.937 | 0.65978 | 0.62463 | 0.52603 | 0.36951 | 0.17429 | -0.04309 | -0.25943 | -0.46262 | -0.6654 | -1.6785 | -3.6425 | -5.2814 | -6.3204 | 5.687 | 5.4098 | 5.3746 | 5.276 | 5.1195 | 4.9243 | 4.7069 | 4.4906 | 4.2874 | 4.0846 | 3.0715 | 1.1075 | -0.53141 | -1.5704 | 0.9425 | 0.65854 | 0.6265 | 0.5429 | 0.40203 | 0.23161 | 0.039382 | -0.14476 | -0.34638 | -0.84041 | -3.1293 | -5.1092 | -6.1542 | -5.617 | 5.6925 | 5.4085 | 5.4085 | 5.2929 | 5.152 | 4.9816 | 4.7894 | 4.6052 | 4.4036 | 3.9096 | 1.6207 | -0.35922 | -1.4042 | -0.86699 | 358235 | 404898 | WIGAN | KIRKBY
| Green St T12 & T13 | 3.4648 | 3.1324 | 2.9886 | 2.7545 | 2.4418 | 2.0972 | 1.7063 | 1.3249 | 0.92659 | 0.45287 | -1.2247 | -2.3303 | -2.7396 | -2.8258 | 9.0048 | 8.6724 | 8.5286 | 8.2945 | 7.9818 | 7.6372 | 7.2463 | 6.8649 | 6.4666 | 5.9929 | 4.3153 | 3.2097 | 2.8004 | 2.7142 | 3.6319 | 3.3997 | 3.0147 | 2.5595 | 2.0335 | 1.4753 | 0.82682 | 0.13848 | -0.62908 | -1.4563 | -2.2647 | -2.8591 | -3.2616 | -3.4704 | 9.1719 | 8.9397 | 8.5547 | 8.0995 | 7.5735 | 7.0153 | 6.3668 | 5.6785 | 4.9109 | 4.0837 | 3.2753 | 2.6809 | 2.2784 | 2.0696 | 3.5003 | 3.2202 | 3.1219 | 2.931 | 2.6702 | 2.3719 | 1.9738 | 1.549 | 1.1095 | 0.65651 | -0.92071 | -1.8439 | -2.1795 | -2.159 | 9.0403 | 8.7602 | 8.6619 | 8.471 | 8.2102 | 7.9119 | 7.5138 | 7.089 | 6.6495 | 6.1965 | 4.6193 | 3.6961 | 3.3605 | 3.381 | 3.4878 | 3.1812 | 3.0636 | 2.8537 | 2.5665 | 2.2415 | 1.8648 | 1.4935 | 1.1059 | 0.72021 | -1.588 | -7.4797 | -12.8343 | -16.6071 | 9.0278 | 8.7212 | 8.6036 | 8.3937 | 8.1065 | 7.7815 | 7.4048 | 7.0335 | 6.6459 | 6.2602 | 3.952 | -1.9397 | -7.2943 | -11.0671 | 3.5225 | 3.2345 | 3.1594 | 3.0188 | 2.8096 | 2.5714 | 2.2716 | 1.9523 | 1.5755 | 0.45847 | -6.0292 | -12.1301 | -15.7894 | -15.1823 | 9.0625 | 8.7745 | 8.7745 | 8.5588 | 8.3496 | 8.1114 | 7.8116 | 7.4923 | 7.1155 | 5.9985 | -0.48916 | -6.5901 | -10.2494 | -9.6423 | 358225 | 404888 | WIGAN | KIRKBY
| Greenfield | 12.3494 | 12.0009 | 11.6658 | 11.2647 | 10.9444 | 10.4714 | 9.9763 | 9.4813 | 8.9578 | 8.3089 | 6.1457 | 5.1949 | 5.1031 | 5.4781 | 16.8494 | 16.5009 | 16.1658 | 15.7647 | 15.4444 | 14.9714 | 14.4763 | 13.9813 | 13.4578 | 12.8089 | 10.6457 | 9.6949 | 9.6031 | 9.9781 | 12.4337 | 12.1657 | 11.8242 | 11.5025 | 11.2749 | 10.8956 | 10.496 | 10.1001 | 9.6752 | 9.2198 | 7.9437 | 7.0268 | 6.5179 | 6.2262 | 16.9337 | 16.6657 | 16.3242 | 16.0025 | 15.7749 | 15.3956 | 14.996 | 14.6001 | 14.1752 | 13.7198 | 12.4437 | 11.5268 | 11.0179 | 10.7262 | 12.3551 | 12.0183 | 11.6967 | 11.3129 | 11.0092 | 10.5554 | 10.079 | 9.58 | 9.078 | 8.4889 | 6.5145 | 5.6798 | 5.6125 | 5.9605 | 16.8551 | 16.5183 | 16.1967 | 15.8129 | 15.5092 | 15.0554 | 14.579 | 14.08 | 13.578 | 12.9889 | 11.0145 | 10.1798 | 10.1125 | 10.4605 | 12.354 | 11.995 | 11.6584 | 11.2734 | 10.965 | 10.4983 | 9.9953 | 9.4997 | 9.0686 | 8.6082 | 6.4217 | 2.6861 | 0.24544 | -1.5138 | 16.854 | 16.495 | 16.1584 | 15.7734 | 15.465 | 14.9983 | 14.4953 | 13.9997 | 13.5686 | 13.1082 | 10.9217 | 7.1861 | 4.7454 | 2.9862 | 12.3398 | 11.9328 | 11.591 | 11.2321 | 10.9583 | 10.5575 | 10.1309 | 9.739 | 9.3539 | 8.3637 | 3.9169 | 0.79986 | -0.70307 | 0.062153 | 16.8398 | 16.4328 | 16.4328 | 15.7321 | 15.4583 | 15.0575 | 14.6309 | 14.239 | 13.8539 | 12.8637 | 8.4169 | 5.2999 | 3.7969 | 4.5622 | 399322 | 404583 | HARTSHEAD-HEYROD | STALYBRIDGE
| Greenhill | 15.6008 | 14.9507 | 14.4775 | 13.9791 | 13.7283 | 13.076 | 12.6869 | 12.0925 | 11.3044 | 10.6344 | 8.2809 | 6.8017 | 6.146 | 6.0063 | 29.6008 | 28.9507 | 28.4775 | 27.9791 | 27.7283 | 27.076 | 26.6869 | 26.0925 | 25.3044 | 24.6344 | 22.2809 | 20.8017 | 20.146 | 20.0063 | 16.1873 | 16.0276 | 15.3363 | 14.6957 | 14.3513 | 13.6664 | 13.2121 | 12.5361 | 11.6487 | 10.9355 | 9.1536 | 7.7275 | 6.8064 | 6.2711 | 30.1873 | 30.0276 | 29.3363 | 28.6957 | 28.3513 | 27.6664 | 27.2121 | 26.5361 | 25.6487 | 24.9355 | 23.1536 | 21.7275 | 20.8064 | 20.2711 | 15.6202 | 14.9909 | 14.5441 | 14.0712 | 13.8449 | 13.2227 | 12.8598 | 12.2951 | 11.5491 | 10.9471 | 8.8057 | 7.5725 | 7.0495 | 7.0195 | 29.6202 | 28.9909 | 28.5441 | 28.0712 | 27.8449 | 27.2227 | 26.8598 | 26.2951 | 25.5491 | 24.9471 | 22.8057 | 21.5725 | 21.0495 | 21.0195 | 15.6341 | 15.0161 | 14.5761 | 14.1101 | 13.8979 | 13.2741 | 12.8833 | 12.2811 | 11.5376 | 10.9904 | 7.6453 | 0.58939 | -4.8844 | -8.2844 | 29.6341 | 29.0161 | 28.5761 | 28.1101 | 27.8979 | 27.2741 | 26.8833 | 26.2811 | 25.5376 | 24.9904 | 21.6453 | 14.5894 | 9.1156 | 5.7156 | 15.6613 | 15.0549 | 14.6519 | 14.2546 | 14.102 | 13.5593 | 13.2468 | 12.7341 | 11.8789 | 10.1286 | 2.195 | -4.1262 | -7.6925 | -6.4447 | 29.6613 | 29.0549 | 29.0549 | 28.2546 | 28.102 | 27.5593 | 27.2468 | 26.7341 | 25.8789 | 24.1286 | 16.195 | 9.8738 | 6.3075 | 7.5553 | 393262 | 404755 | GREENHILL | WHITEGATE
| Griffin | 8.4085 | 7.6127 | 7.2235 | 6.573 | 6.5906 | 5.9676 | 5.5509 | 5.0608 | 4.5018 | 3.7526 | 1.1669 | -0.12297 | -0.63596 | -0.37209 | 13.0485 | 12.2527 | 11.8635 | 11.213 | 11.2306 | 10.6076 | 10.1909 | 9.7008 | 9.1418 | 8.3926 | 5.8069 | 4.517 | 4.004 | 4.2679 | 8.6053 | 8.0957 | 7.6736 | 7.1125 | 7.1408 | 6.5725 | 6.1813 | 5.7107 | 5.2535 | 4.6627 | 3.0392 | 1.8142 | 0.88119 | 0.37243 | 13.2453 | 12.7357 | 12.3136 | 11.7525 | 11.7808 | 11.2125 | 10.8213 | 10.3507 | 9.8935 | 9.3027 | 7.6792 | 6.4542 | 5.5212 | 5.0124 | 8.4118 | 7.6575 | 7.2644 | 6.6658 | 6.6973 | 6.1032 | 5.7092 | 5.2347 | 4.7114 | 4.0428 | 1.7477 | 0.67207 | 0.27341 | 0.5765 | 13.0518 | 12.2975 | 11.9044 | 11.3058 | 11.3373 | 10.7432 | 10.3492 | 9.8747 | 9.3514 | 8.6828 | 6.3877 | 5.3121 | 4.9134 | 5.2165 | 8.4055 | 7.602 | 7.2035 | 6.546 | 6.5823 | 5.9152 | 5.4761 | 4.9759 | 4.4711 | 3.8707 | 0.65445 | -5.5735 | -10.2793 | -13.0912 | 13.0455 | 12.242 | 11.8435 | 11.186 | 11.2223 | 10.5552 | 10.1161 | 9.6159 | 9.1111 | 8.5107 | 5.2945 | -0.93352 | -5.6393 | -8.4512 | 8.4404 | 7.6266 | 7.2642 | 6.6433 | 6.7155 | 6.1047 | 5.7488 | 5.4094 | 4.7687 | 3.1496 | -3.9753 | -9.4065 | -12.4161 | -11.2087 | 13.0804 | 12.2666 | 12.2666 | 11.2833 | 11.3555 | 10.7447 | 10.3888 | 10.0494 | 9.4087 | 7.7896 | 0.66465 | -4.7665 | -7.7761 | -6.5687 | 367171 | 427130 | LOWER DARWEN | ROCHDALE
| Hadfield | 11.8014 | 11.2482 | 10.882 | 10.4415 | 9.9474 | 9.3662 | 8.7408 | 8.1368 | 7.4896 | 6.8072 | 4.3314 | 3.1532 | 2.9835 | 3.2069 | 16.4384 | 15.8852 | 15.519 | 15.0785 | 14.5844 | 14.0032 | 13.3778 | 12.7738 | 12.1266 | 11.4442 | 8.9684 | 7.7902 | 7.6205 | 7.8439 | 12.0557 | 11.7286 | 11.3508 | 10.96 | 10.5618 | 10.0904 | 9.5798 | 9.088 | 8.5469 | 8.0234 | 6.3335 | 5.2957 | 4.8244 | 4.6379 | 16.6927 | 16.3656 | 15.9878 | 15.597 | 15.1988 | 14.7274 | 14.2168 | 13.725 | 13.1839 | 12.6604 | 10.9705 | 9.9327 | 9.4614 | 9.2749 | 11.8122 | 11.2697 | 10.9135 | 10.4826 | 10.0024 | 9.4372 | 8.8271 | 8.2366 | 7.6134 | 6.9904 | 4.7418 | 3.7493 | 3.6396 | 3.9033 | 16.4492 | 15.9067 | 15.5505 | 15.1196 | 14.6394 | 14.0742 | 13.4641 | 12.8736 | 12.2504 | 11.6274 | 9.3788 | 8.3863 | 8.2766 | 8.5403 | 11.815 | 11.2773 | 10.9344 | 10.5235 | 10.0818 | 9.5629 | 8.9981 | 8.4636 | 7.9458 | 7.4472 | 4.5362 | -0.021617 | -3.2074 | -5.1691 | 16.452 | 15.9143 | 15.5714 | 15.1605 | 14.7188 | 14.1999 | 13.6351 | 13.1006 | 12.5828 | 12.0842 | 9.1732 | 4.6154 | 1.4296 | -0.53214 | 11.7761 | 11.1349 | 10.7448 | 10.3399 | 9.9171 | 9.451 | 8.9332 | 8.4719 | 7.9175 | 6.7501 | 1.32 | -2.5818 | -4.4693 | -3.5202 | 16.4131 | 15.7719 | 15.7719 | 14.9769 | 14.5541 | 14.088 | 13.5702 | 13.1089 | 12.5545 | 11.3871 | 5.957 | 2.0552 | 0.1677 | 1.1168 | 401790 | 395876 | HYDE | STALYBRIDGE
| Hall Cross | 3.3564 | 2.5404 | 2.333 | 1.7415 | 1.2987 | 0.56542 | -0.10393 | -0.81136 | -1.5849 | -2.4698 | -5.4452 | -7.0994 | -7.5103 | -7.3195 | 7.9934 | 7.1774 | 6.97 | 6.3785 | 5.9357 | 5.2024 | 4.5331 | 3.8256 | 3.0521 | 2.1672 | -0.80816 | -2.4624 | -2.8733 | -2.6825 | 3.6799 | 3.1517 | 2.7848 | 2.1822 | 1.765 | 1.0854 | 0.45678 | -0.17805 | -0.91699 | -1.6448 | -3.6687 | -5.3718 | -6.3571 | -7.0255 | 8.3169 | 7.7887 | 7.4218 | 6.8192 | 6.402 | 5.7224 | 5.0938 | 4.4589 | 3.72 | 2.9922 | 0.96829 | -0.73484 | -1.7201 | -2.3885 | 3.3648 | 2.5722 | 2.3948 | 1.8193 | 1.415 | 0.71131 | 0.043815 | -0.64355 | -1.3793 | -2.1869 | -4.9299 | -6.368 | -6.6839 | -6.4414 | 8.0018 | 7.2092 | 7.0318 | 6.4563 | 6.052 | 5.3483 | 4.6808 | 3.9935 | 3.2577 | 2.4501 | -0.29287 | -1.731 | -2.0469 | -1.8044 | 3.3842 | 2.5898 | 2.4098 | 1.8572 | 1.4721 | 0.79486 | 0.14691 | -0.49527 | -1.1469 | -1.7789 | -4.8302 | -9.9384 | -13.3938 | -15.8848 | 8.0212 | 7.2268 | 7.0468 | 6.4942 | 6.1091 | 5.4319 | 4.7839 | 4.1417 | 3.4901 | 2.8581 | -0.19322 | -5.3014 | -8.7568 | -11.2478 | 3.3906 | 2.5711 | 2.386 | 1.8713 | 1.5132 | 0.90535 | 0.3559 | -0.18346 | -0.80613 | -2.1106 | -7.9673 | -12.355 | -14.5517 | -13.84 | 8.0276 | 7.2081 | 7.2081 | 6.5083 | 6.1502 | 5.5423 | 4.9929 | 4.4535 | 3.8309 | 2.5264 | -3.3303 | -7.718 | -9.9147 | -9.203 | 342288 | 430650 | PEEL | PENWORTHAM
| Handforth | 10.1593 | 9.6004 | 9.1571 | 8.8781 | 8.4496 | 7.9786 | 7.408 | 6.9652 | 6.47 | 5.8976 | 3.8261 | 2.7792 | 2.5044 | 2.5403 | 14.7963 | 14.2374 | 13.7941 | 13.5151 | 13.0866 | 12.6156 | 12.045 | 11.6022 | 11.107 | 10.5346 | 8.4631 | 7.4162 | 7.1414 | 7.1773 | 10.4206 | 10.1048 | 9.6723 | 9.4204 | 9.0509 | 8.6424 | 8.1333 | 7.7424 | 7.2947 | 6.8296 | 5.2836 | 4.1927 | 3.5319 | 3.0883 | 15.0576 | 14.7418 | 14.3093 | 14.0574 | 13.6879 | 13.2794 | 12.7703 | 12.3794 | 11.9317 | 11.4666 | 9.9206 | 8.8297 | 8.1689 | 7.7253 | 10.1678 | 9.6227 | 9.1941 | 8.9249 | 8.511 | 8.0552 | 7.5001 | 7.0703 | 6.5969 | 6.077 | 4.1684 | 3.281 | 3.0669 | 3.2003 | 14.8048 | 14.2597 | 13.8311 | 13.5619 | 13.148 | 12.6922 | 12.1371 | 11.7073 | 11.2339 | 10.714 | 8.8054 | 7.918 | 7.7039 | 7.8373 | 10.1746 | 9.6361 | 9.2209 | 8.9638 | 8.5857 | 8.1648 | 7.6308 | 7.2284 | 6.8292 | 6.4151 | 4.1203 | 0.39861 | -2.2761 | -4.1787 | 14.8116 | 14.2731 | 13.8579 | 13.6008 | 13.2227 | 12.8018 | 12.2678 | 11.8654 | 11.4662 | 11.0521 | 8.7573 | 5.0356 | 2.3609 | 0.45831 | 10.114 | 9.5054 | 9.0936 | 8.8706 | 8.525 | 8.1591 | 7.6818 | 7.3503 | 6.9398 | 5.9993 | 1.5893 | -1.684 | -3.4017 | -2.8649 | 14.751 | 14.1424 | 14.1424 | 13.5076 | 13.162 | 12.7961 | 12.3188 | 11.9873 | 11.5768 | 10.6363 | 6.2263 | 2.953 | 1.2353 | 1.7721 | 385958 | 383397 | MOSS NOOK | SOUTH MANCHESTER
| Hanging Bridge | 1.8397 | 1.5624 | 1.4732 | 1.2381 | 1.0568 | 0.75784 | 0.44336 | 0.12261 | -0.21778 | -0.60954 | -2.0685 | -3.1945 | -3.673 | -3.9144 | 5.8397 | 5.5624 | 5.4732 | 5.2381 | 5.0568 | 4.7578 | 4.4434 | 4.1226 | 3.7822 | 3.3905 | 1.9315 | 0.80554 | 0.32702 | 0.085603 | 1.9866 | 1.8337 | 1.6932 | 1.466 | 1.341 | 1.0912 | 0.82757 | 0.55692 | 0.25905 | -0.031854 | -1.0446 | -1.8921 | -2.4335 | -2.7875 | 5.9866 | 5.8337 | 5.6932 | 5.466 | 5.341 | 5.0912 | 4.8276 | 4.5569 | 4.2591 | 3.9681 | 2.9554 | 2.1079 | 1.5665 | 1.2125 | 1.8416 | 1.5734 | 1.4928 | 1.2519 | 1.0755 | 0.78557 | 0.48011 | 0.1683 | -0.15684 | -0.5137 | -1.8036 | -2.6055 | -2.9041 | -2.9318 | 5.8416 | 5.5734 | 5.4928 | 5.2519 | 5.0755 | 4.7856 | 4.4801 | 4.1683 | 3.8432 | 3.4863 | 2.1964 | 1.3945 | 1.0959 | 1.0682 | 1.8545 | 1.5861 | 1.509 | 1.2917 | 1.1439 | 0.86746 | 0.56793 | 0.26501 | -0.026659 | -0.31312 | -2.0975 | -4.1363 | -5.2656 | -5.9842 | 5.8545 | 5.5861 | 5.509 | 5.2917 | 5.1439 | 4.8675 | 4.5679 | 4.265 | 3.9733 | 3.6869 | 1.9025 | -0.13627 | -1.2656 | -1.9842 | 1.835 | 1.5294 | 1.4418 | 1.2032 | 1.0457 | 0.77709 | 0.48204 | 0.19087 | -0.10122 | -0.54902 | -2.8482 | -4.495 | -5.1262 | -5.0707 | 5.835 | 5.5294 | 5.5294 | 5.2032 | 5.0457 | 4.7771 | 4.482 | 4.1909 | 3.8988 | 3.451 | 1.1518 | -0.49505 | -1.1262 | -1.0707 | 346186 | 417486 | WRIGHTINGTON | PENWORTHAM
| Hareholme | 5.3082 | 4.6535 | 4.421 | 4.1403 | 3.8021 | 3.3561 | 2.8703 | 2.356 | 1.8356 | 1.2189 | -1.5285 | -3.5742 | -4.7587 | -5.4743 | 9.9452 | 9.2905 | 9.058 | 8.7773 | 8.4391 | 7.9931 | 7.5073 | 6.993 | 6.4726 | 5.8559 | 3.1085 | 1.0628 | -0.12168 | -0.83729 | 5.7858 | 5.543 | 5.264 | 4.9647 | 4.666 | 4.3197 | 3.9461 | 3.5587 | 3.1774 | 2.6279 | 0.79737 | -0.43179 | -1.0264 | -1.3432 | 10.4228 | 10.18 | 9.901 | 9.6017 | 9.303 | 8.9567 | 8.5831 | 8.1957 | 7.8144 | 7.2649 | 5.4344 | 4.2052 | 3.6106 | 3.2938 | 5.3159 | 4.6953 | 4.4514 | 4.1809 | 3.8564 | 3.4251 | 2.9539 | 2.4538 | 1.9547 | 1.39 | -1.1191 | -2.9239 | -3.9732 | -4.6028 | 9.9529 | 9.3323 | 9.0884 | 8.8179 | 8.4934 | 8.0621 | 7.5909 | 7.0908 | 6.5917 | 6.027 | 3.5179 | 1.7131 | 0.66384 | 0.034218 | 5.3412 | 4.7056 | 4.4348 | 4.0826 | 3.6322 | 3.0149 | 2.2793 | 1.4483 | 0.58046 | -0.41848 | -4.7404 | -10.0404 | -13.6564 | -15.8844 | 9.9782 | 9.3426 | 9.0718 | 8.7196 | 8.2692 | 7.6519 | 6.9163 | 6.0853 | 5.2175 | 4.2185 | -0.10344 | -5.4034 | -9.0194 | -11.2474 | 5.3092 | 4.6087 | 4.2764 | 3.9072 | 3.4478 | 2.8498 | 2.1277 | 1.3452 | 0.4324 | -1.0985 | -7.1427 | -12.1327 | -15.4969 | -14.5382 | 9.9462 | 9.2457 | 9.2457 | 8.5442 | 8.0848 | 7.4868 | 6.7647 | 5.9822 | 5.0694 | 3.5385 | -2.5057 | -7.4957 | -10.8599 | -9.9012 | 382535 | 422283 | ROSSENDALE | PADIHAM
| Harpurhey | 9.268 | 8.9923 | 8.8218 | 8.4867 | 8.1567 | 7.7221 | 7.3015 | 6.8149 | 6.2994 | 5.7355 | 3.6112 | 2.4192 | 2.0265 | 2.0284 | 13.908 | 13.6323 | 13.4618 | 13.1267 | 12.7967 | 12.3621 | 11.9415 | 11.4549 | 10.9394 | 10.3755 | 8.2512 | 7.0592 | 6.6665 | 6.6684 | 9.321 | 9.1228 | 8.8669 | 8.5461 | 8.2932 | 7.8987 | 7.5327 | 7.0905 | 6.6144 | 6.1594 | 4.575 | 3.4289 | 2.7725 | 2.3006 | 13.961 | 13.7628 | 13.5069 | 13.1861 | 12.9332 | 12.5387 | 12.1727 | 11.7305 | 11.2544 | 10.7994 | 9.215 | 8.0689 | 7.4125 | 6.9406 | 9.261 | 9.0016 | 8.8484 | 8.537 | 8.2192 | 7.8066 | 7.4071 | 6.942 | 6.4558 | 5.9483 | 4.0375 | 2.9995 | 2.6561 | 2.654 | 13.901 | 13.6416 | 13.4884 | 13.177 | 12.8592 | 12.4466 | 12.0471 | 11.582 | 11.0958 | 10.5883 | 8.6775 | 7.6395 | 7.2961 | 7.294 | 9.2678 | 8.9916 | 8.8117 | 8.4494 | 8.1446 | 7.7127 | 7.2651 | 6.7453 | 6.2706 | 5.8141 | 3.0379 | -2.5009 | -6.8179 | -9.9433 | 13.9078 | 13.6316 | 13.4517 | 13.0894 | 12.7846 | 12.3527 | 11.9051 | 11.3853 | 10.9106 | 10.4541 | 7.6779 | 2.1391 | -2.1779 | -5.3033 | 9.313 | 9.0335 | 8.8621 | 8.5564 | 8.2711 | 7.9072 | 7.5331 | 7.0997 | 6.5782 | 5.2642 | -0.99694 | -5.992 | -8.881 | -8.3033 | 13.953 | 13.6735 | 13.6735 | 13.1964 | 12.9111 | 12.5472 | 12.1731 | 11.7397 | 11.2182 | 9.9042 | 3.6431 | -1.352 | -4.241 | -3.6633 | 385907 | 402469 | RED BANK | WHITEGATE
| Harwood | 2.3022 | 1.9127 | 1.7398 | 1.1929 | 1.0196 | 0.24348 | -0.20397 | -0.74904 | -1.4038 | -2.1446 | -4.6853 | -5.7078 | -5.7951 | -5.2515 | 6.6022 | 6.2127 | 6.0398 | 5.4929 | 5.3196 | 4.5435 | 4.096 | 3.551 | 2.8962 | 2.1554 | -0.38531 | -1.4078 | -1.4951 | -0.95151 | 2.4118 | 2.1131 | 1.8894 | 1.3914 | 1.296 | 0.61279 | 0.2522 | -0.20157 | -0.57946 | -1.1735 | -2.7836 | -3.9156 | -4.6605 | -4.9157 | 6.7118 | 6.4131 | 6.1894 | 5.6914 | 5.596 | 4.9128 | 4.5522 | 4.0984 | 3.7205 | 3.1265 | 1.5164 | 0.38444 | -0.36052 | -0.61567 | 2.3157 | 1.9381 | 1.7756 | 1.2417 | 1.0793 | 0.32109 | -0.11344 | -0.64559 | -1.217 | -1.8816 | -4.1711 | -5.0252 | -5.0837 | -4.5689 | 6.6157 | 6.2381 | 6.0756 | 5.5417 | 5.3793 | 4.6211 | 4.1866 | 3.6544 | 3.083 | 2.4184 | 0.12885 | -0.72515 | -0.78366 | -0.26885 | 2.309 | 1.9269 | 1.7686 | 1.2421 | 1.107 | 0.36759 | -0.080642 | -0.62418 | -1.0025 | -1.5587 | -4.5714 | -10.8079 | -15.7621 | -18.9514 | 6.609 | 6.2269 | 6.0686 | 5.5421 | 5.407 | 4.6676 | 4.2194 | 3.6758 | 3.2975 | 2.7413 | -0.27137 | -6.5079 | -11.4621 | -14.6514 | 2.2979 | 1.8673 | 1.7135 | 1.2312 | 1.1235 | 0.44872 | 0.081285 | -0.36148 | -0.87604 | -2.4558 | -9.7187 | -15.2371 | -18.4961 | -17.2327 | 6.5979 | 6.1673 | 6.1673 | 5.5312 | 5.4235 | 4.7487 | 4.3813 | 3.9385 | 3.424 | 1.8442 | -5.4187 | -10.9371 | -14.1961 | -12.9327 | 374043 | 410941 | BOLTON | KEARSLEY
| Hattersley | 5.9807 | 5.6733 | 5.3825 | 3.0256 | -1.2949 | -1.774 | -2.2431 | 2.8002 | 2.3152 | 1.7297 | -0.25014 | -1.2211 | -1.377 | -1.1275 | 9.4807 | 9.1733 | 8.8825 | 6.5256 | 2.2051 | 1.726 | 1.2569 | 0.80018 | 0.31523 | -0.27027 | -2.2501 | -3.2211 | -3.377 | -3.1275 | 6.1229 | 5.9371 | 5.6241 | 3.8238 | 0.58595 | 0.20699 | -0.16283 | 4.9777 | 4.5867 | 4.1645 | 2.8932 | 2.0299 | 1.6108 | 1.4391 | 9.6229 | 9.4371 | 9.1241 | 7.3238 | 4.0859 | 3.707 | 3.3372 | 2.9777 | 2.5867 | 2.1645 | 0.8932 | 0.029875 | -0.3892 | -0.56094 | 5.9849 | 5.6813 | 5.3949 | 3.0431 | -1.2707 | -1.741 | -2.2019 | 2.8485 | 2.3779 | 1.8381 | 0.023508 | -0.83613 | -0.96301 | -0.72654 | 9.4849 | 9.1813 | 8.8949 | 6.5431 | 2.2293 | 1.759 | 1.2981 | 0.84851 | 0.37791 | -0.16189 | -1.9765 | -2.8361 | -2.963 | -2.7265 | 5.9921 | 5.6933 | 5.4143 | 3.0735 | -1.2202 | -1.6735 | -2.1319 | 2.9225 | 2.5059 | 2.0481 | -0.29765 | -4.196 | -6.9431 | -8.7585 | 9.4921 | 9.1933 | 8.9143 | 6.5735 | 2.2798 | 1.8265 | 1.3681 | 0.9225 | 0.5059 | 0.04813 | -2.2976 | -6.196 | -8.9431 | -10.7585 | 5.9617 | 5.5865 | 5.2743 | 2.9401 | -1.3413 | -1.7518 | -2.1641 | 2.9599 | 2.5243 | 1.5015 | -3.0485 | -6.3771 | -8.0359 | -7.2887 | 9.4617 | 9.0865 | 9.0865 | 6.4401 | 2.1587 | 1.7482 | 1.3359 | 0.95986 | 0.52434 | -0.49855 | -5.0485 | -8.3771 | -10.0359 | -9.2887 | 398419 | 395120 | HYDE | STALYBRIDGE
| Haverthwaite | 3.3214 | 3.0136 | 2.9189 | 2.7074 | 2.6913 | 2.5503 | 2.3429 | 2.1716 | 1.9941 | 1.7795 | 0.9816 | 0.59635 | 0.48117 | 0.68066 | 5.8214 | 5.5136 | 5.4189 | 5.2074 | 5.1913 | 5.0503 | 4.8429 | 4.6716 | 4.4941 | 4.2795 | 3.4816 | 3.0964 | 2.9812 | 3.1807 | 3.5221 | 3.3863 | 3.2271 | 2.9837 | 2.9356 | 2.7752 | 2.5416 | 2.3324 | 2.1104 | 1.8946 | 1.4089 | 0.96593 | 0.63912 | 0.50534 | 6.0221 | 5.8863 | 5.7271 | 5.4837 | 5.4356 | 5.2752 | 5.0416 | 4.8324 | 4.6104 | 4.3946 | 3.9089 | 3.4659 | 3.1391 | 3.0053 | 3.3271 | 3.0259 | 2.9375 | 2.7344 | 2.7233 | 2.5901 | 2.3916 | 2.2287 | 2.062 | 1.8661 | 1.111 | 0.75364 | 0.64119 | 0.84837 | 5.8271 | 5.5259 | 5.4375 | 5.2344 | 5.2233 | 5.0901 | 4.8916 | 4.7287 | 4.562 | 4.3661 | 3.611 | 3.2536 | 3.1412 | 3.3484 | 3.3362 | 3.0375 | 2.9531 | 2.7575 | 2.747 | 2.6122 | 2.4045 | 2.2362 | 2.0825 | 1.9436 | 1.1928 | 0.071786 | -0.62589 | -0.98667 | 5.8362 | 5.5375 | 5.4531 | 5.2575 | 5.247 | 5.1122 | 4.9045 | 4.7362 | 4.5825 | 4.4436 | 3.6928 | 2.5718 | 1.8741 | 1.5133 | 3.3007 | 2.9758 | 2.9018 | 2.7168 | 2.7085 | 2.5851 | 2.3961 | 2.2547 | 2.1217 | 1.8188 | 0.3159 | -0.67299 | -1.1017 | -0.7011 | 5.8007 | 5.4758 | 5.4758 | 5.2168 | 5.2085 | 5.0851 | 4.8961 | 4.7547 | 4.6217 | 4.3188 | 2.8159 | 1.827 | 1.3983 | 1.7989 | 334234 | 483827 | ULVERSTON | HARKER
| Hawk Green | 11.4144 | 11.1668 | 10.807 | 10.5158 | 10.2082 | 9.8008 | 9.2139 | 8.8114 | 8.4525 | 7.8211 | 5.7761 | 4.7582 | 4.5036 | 4.9542 | 15.9144 | 15.6668 | 15.307 | 15.0158 | 14.7082 | 14.3008 | 13.7139 | 13.3114 | 12.9525 | 12.3211 | 10.2761 | 9.2582 | 9.0036 | 9.4542 | 11.5805 | 11.4795 | 11.0454 | 10.8008 | 10.5709 | 10.2392 | 9.7292 | 9.392 | 9.074 | 8.6165 | 7.3938 | 6.3917 | 5.6906 | 5.3905 | 16.0805 | 15.9795 | 15.5454 | 15.3008 | 15.0709 | 14.7392 | 14.2292 | 13.892 | 13.574 | 13.1165 | 11.8938 | 10.8917 | 10.1906 | 9.8905 | 11.4218 | 11.1714 | 10.8257 | 10.5496 | 10.2589 | 9.87 | 9.3037 | 8.9183 | 8.5807 | 8.0089 | 6.1364 | 5.2369 | 5.0399 | 5.4759 | 15.9218 | 15.6714 | 15.3257 | 15.0496 | 14.7589 | 14.37 | 13.8037 | 13.4183 | 13.0807 | 12.5089 | 10.6364 | 9.7369 | 9.5399 | 9.9759 | 11.4311 | 11.1929 | 10.8481 | 10.5908 | 10.3233 | 9.9431 | 9.3396 | 8.9155 | 8.6011 | 8.1394 | 5.9204 | 1.6627 | -1.3735 | -3.3204 | 15.9311 | 15.6929 | 15.3481 | 15.0908 | 14.8233 | 14.4431 | 13.8396 | 13.4155 | 13.1011 | 12.6394 | 10.4204 | 6.1627 | 3.1265 | 1.1796 | 11.4089 | 11.1072 | 10.7636 | 10.5201 | 10.2489 | 9.9032 | 9.3755 | 9.0542 | 8.7374 | 7.6407 | 2.8121 | -0.75936 | -2.6776 | -1.7832 | 15.9089 | 15.6072 | 15.6072 | 15.0201 | 14.7489 | 14.4032 | 13.8755 | 13.5542 | 13.2374 | 12.1407 | 7.3121 | 3.7406 | 1.8224 | 2.7168 | 395915 | 387138 | HAZEL GROVE | BREDBURY
| Haydock | 7.4357 | 6.7141 | 6.3225 | 5.8415 | 5.6851 | 5.5704 | 5.0357 | 4.5467 | 4.3609 | 3.665 | 1.8078 | -0.68833 | -2.3428 | -3.9329 | 12.9357 | 12.2141 | 11.8225 | 11.3415 | 11.1851 | 11.0704 | 10.5357 | 10.0467 | 9.8609 | 9.165 | 7.3078 | 4.8117 | 3.1572 | 1.5671 | 8.0316 | 7.8155 | 7.1225 | 6.4435 | 6.1102 | 5.8998 | 5.1361 | 4.4283 | 3.9779 | 2.9705 | 1.5736 | 0.6153 | -0.6377 | -1.3644 | 13.5316 | 13.3155 | 12.6225 | 11.9435 | 11.6102 | 11.3998 | 10.6361 | 9.9283 | 9.4779 | 8.4705 | 7.0736 | 6.1153 | 4.8623 | 4.1356 | 7.1851 | 6.4731 | 6.392 | 5.8858 | 5.6939 | 5.3758 | 5.1528 | 4.697 | 4.232 | 4.0747 | 2.1714 | 0.45222 | -0.73609 | -1.5699 | 12.6851 | 11.9731 | 11.892 | 11.3858 | 11.1939 | 10.8758 | 10.6528 | 10.197 | 9.732 | 9.5747 | 7.6714 | 5.9522 | 4.7639 | 3.9301 | 7.4712 | 6.7876 | 6.4412 | 6.0046 | 5.8939 | 5.7911 | 5.2638 | 4.7538 | 4.5282 | 3.7878 | 0.56222 | -7.8756 | -15.1166 | -19.6223 | 12.9712 | 12.2876 | 11.9412 | 11.5046 | 11.3939 | 11.2911 | 10.7638 | 10.2538 | 10.0282 | 9.2878 | 6.0622 | -2.3756 | -9.6166 | -14.1223 | 7.4673 | 6.7488 | 6.4627 | 6.0683 | 6.0041 | 5.7627 | 5.3934 | 4.8604 | 4.3144 | 3.7003 | -5.2007 | -13.4913 | -18.4496 | -18.1203 | 12.9673 | 12.2488 | 12.2488 | 11.5683 | 11.5041 | 11.2627 | 10.8934 | 10.3604 | 9.8144 | 9.2003 | 0.2993 | -7.9913 | -12.9496 | -12.6203 | 357489 | 397336 | GOLBORNE | BOLD
| HDA No1 & HDA No2 | 13.069 | 12.7827 | 12.666 | 12.3838 | 12.5439 | 12.2383 | 12.0293 | 11.7434 | 11.3995 | 11.0257 | 9.8631 | 9.4 | 9.5079 | 9.4287 | 19.289 | 19.0027 | 18.886 | 18.6038 | 18.7639 | 18.4583 | 18.2493 | 17.9634 | 17.6195 | 17.2457 | 16.0831 | 15.62 | 15.7279 | 15.6487 | 13.4238 | 13.4186 | 13.1889 | 12.8442 | 12.9555 | 12.6522 | 12.5276 | 12.2691 | 11.9317 | 11.5933 | 10.725 | 10.1893 | 9.9827 | 10.0618 | 19.6438 | 19.6386 | 19.4089 | 19.0642 | 19.1755 | 18.8722 | 18.7476 | 18.4891 | 18.1517 | 17.8133 | 16.945 | 16.4093 | 16.2027 | 16.2818 | 13.0732 | 12.7914 | 12.6804 | 12.4049 | 12.5678 | 12.2701 | 12.0869 | 11.8105 | 11.4828 | 11.145 | 10.1101 | 9.8299 | 10.0349 | 10.5106 | 19.2932 | 19.0114 | 18.9004 | 18.6249 | 18.7878 | 18.4901 | 18.3069 | 18.0305 | 17.7028 | 17.365 | 16.3301 | 16.0499 | 16.2549 | 16.7306 | 13.0943 | 12.8343 | 12.7457 | 12.4961 | 12.6852 | 12.4115 | 12.328 | 12.1542 | 11.9871 | 11.8994 | 10.9696 | 7.5684 | 5.2349 | 3.6403 | 19.3143 | 19.0543 | 18.9657 | 18.7161 | 18.9052 | 18.6315 | 18.548 | 18.3742 | 18.2071 | 18.1194 | 17.1896 | 13.7884 | 11.4549 | 9.8603 | 13.0803 | 12.7906 | 12.6853 | 12.4313 | 12.6222 | 12.3529 | 12.2679 | 12.0969 | 11.9307 | 11.6924 | 9.8836 | 7.1364 | 5.6396 | 5.2798 | 19.3003 | 19.0106 | 19.0106 | 18.6513 | 18.8422 | 18.5729 | 18.4879 | 18.3169 | 18.1507 | 17.9124 | 16.1036 | 13.3564 | 11.8596 | 11.4998 | 301743 | 524532 | STAINBURN & SIDDICK | HARKER
| Heady Hill | 5.4245 | 5.0729 | 4.7454 | 4.6788 | 4.4551 | 4.1058 | 3.7076 | 3.4129 | 2.628 | 2.2084 | 0.63303 | -1.3956 | -2.3314 | -3.3336 | 8.9245 | 8.5729 | 8.2454 | 8.1788 | 7.9551 | 7.6058 | 7.2076 | 6.9129 | 6.128 | 5.7084 | 4.133 | 2.1044 | 1.1686 | 0.1664 | 5.6668 | 5.5343 | 5.1574 | 5.0651 | 4.8463 | 4.505 | 4.1099 | 3.813 | 3.5277 | 3.1152 | 1.8909 | 0.70086 | -0.31619 | -1.187 | 9.1668 | 9.0343 | 8.6574 | 8.5651 | 8.3463 | 8.005 | 7.6099 | 7.313 | 7.0277 | 6.6152 | 5.3909 | 4.2009 | 3.1838 | 2.313 | 5.4329 | 5.0838 | 4.7672 | 4.7021 | 4.486 | 4.1459 | 3.7573 | 3.4713 | 2.6993 | 2.3109 | 0.94121 | -0.62231 | -1.3258 | -1.8774 | 8.9329 | 8.5838 | 8.2672 | 8.2021 | 7.986 | 7.6459 | 7.2573 | 6.9713 | 6.1993 | 5.8109 | 4.4412 | 2.8777 | 2.1742 | 1.6226 | 5.4311 | 5.0866 | 4.7604 | 4.6997 | 4.4888 | 4.1372 | 3.7062 | 3.3612 | 2.5911 | 2.1786 | -1.0239 | -6.728 | -10.7746 | -13.6501 | 8.9311 | 8.5866 | 8.2604 | 8.1997 | 7.9888 | 7.6372 | 7.2062 | 6.8612 | 6.0911 | 5.6786 | 2.4761 | -3.228 | -7.2746 | -10.1501 | 5.4567 | 5.1041 | 4.8078 | 4.7408 | 4.5464 | 3.6256 | 2.632 | 1.8295 | 1.5024 | 0.40885 | -5.0343 | -10.0975 | -13.0674 | -12.9563 | 8.9567 | 8.6041 | 8.6041 | 8.2408 | 8.0464 | 7.1256 | 6.132 | 5.3295 | 5.0024 | 3.9089 | -1.5343 | -6.5975 | -9.5674 | -9.4563 | 384370 | 410583 | CASTLETON | ROCHDALE
| Heap Bridge | 7.4152 | 7.0129 | 6.9233 | 6.7983 | 6.7611 | 6.5382 | 6.3315 | 6.2089 | 5.9879 | 5.7435 | 4.8093 | 3.978 | 3.347 | 2.888 | 4.3652 | 3.9629 | 3.8733 | 3.7483 | 3.7111 | 3.4882 | 3.2815 | 3.1589 | 2.9379 | 2.6935 | 1.7593 | 0.92799 | 0.29701 | -0.16202 | 7.7057 | 7.5563 | 7.4227 | 7.2659 | 7.2075 | 6.9993 | 6.8009 | 6.6795 | 6.4961 | 6.3088 | 5.6712 | 5.0949 | 4.5215 | 4.1792 | 4.6557 | 4.5063 | 4.3727 | 4.2159 | 4.1575 | 3.9493 | 3.7509 | 3.6295 | 3.4461 | 3.2588 | 2.6212 | 2.0449 | 1.4715 | 1.1292 | 7.4195 | 7.0199 | 6.9423 | 6.81 | 6.7862 | 6.5676 | 6.3652 | 6.2413 | 6.0188 | 5.7908 | 4.9771 | 4.4079 | 3.9077 | 3.6647 | 4.3695 | 3.9699 | 3.8923 | 3.76 | 3.7362 | 3.5176 | 3.3152 | 3.1913 | 2.9688 | 2.7408 | 1.9271 | 1.3579 | 0.85772 | 0.61465 | 7.427 | 7.0356 | 6.9555 | 6.8327 | 6.8012 | 6.5687 | 6.3324 | 6.1662 | 5.8876 | 5.6094 | 4.0708 | 1.654 | -0.20021 | -1.3139 | 4.377 | 3.9856 | 3.9055 | 3.7827 | 3.7512 | 3.5187 | 3.2824 | 3.1162 | 2.8376 | 2.5594 | 1.0208 | -1.396 | -3.2502 | -4.3639 | 7.414 | 6.9978 | 6.913 | 6.7789 | 6.7504 | 6.5092 | 6.2558 | 6.0628 | 5.7245 | 5.1213 | 2.4255 | 0.20436 | -1.0318 | -0.80418 | 4.364 | 3.9478 | 3.9478 | 3.7289 | 3.7004 | 3.4592 | 3.2058 | 3.0128 | 2.6745 | 2.0713 | -0.62451 | -2.8456 | -4.0818 | -3.8542 | 382793 | 410428 | BURY | KEARSLEY
| Heasandford | 9.2157 | 8.8483 | 8.8355 | 8.8789 | 8.6883 | 8.569 | 8.4605 | 13.0305 | 12.829 | 12.7288 | 12.5433 | 12.3819 | 12.4146 | 12.4834 | 18.4257 | 18.0583 | 18.0455 | 18.0889 | 17.8983 | 17.779 | 17.6705 | 17.6305 | 17.429 | 17.3288 | 17.1433 | 16.9819 | 17.0146 | 17.0834 | 9.4988 | 9.368 | 9.2786 | 9.258 | 9.0346 | 8.9058 | 8.7788 | 13.3231 | 13.094 | 12.9648 | 12.8106 | 12.6174 | 12.5873 | 12.6107 | 18.7088 | 18.578 | 18.4886 | 18.468 | 18.2446 | 18.1158 | 17.9888 | 17.9231 | 17.694 | 17.5648 | 17.4106 | 17.2174 | 17.1873 | 17.2107 | 9.2176 | 8.8529 | 8.8425 | 8.8879 | 8.7008 | 8.5848 | 8.4797 | 13.0525 | 12.8563 | 12.7645 | 12.5974 | 12.4485 | 12.4843 | 12.5518 | 18.4276 | 18.0629 | 18.0525 | 18.0979 | 17.9108 | 17.7948 | 17.6897 | 17.6525 | 17.4563 | 17.3645 | 17.1974 | 17.0485 | 17.0843 | 17.1518 | 9.2336 | 8.8853 | 8.8908 | 8.9516 | 8.7798 | 8.6799 | 8.5909 | 13.1796 | 13.0022 | 12.9327 | 12.7565 | 11.862 | 10.8444 | 10.2589 | 18.4436 | 18.0953 | 18.1008 | 18.1616 | 17.9898 | 17.8899 | 17.8009 | 17.7796 | 17.6022 | 17.5327 | 17.3565 | 16.462 | 15.4444 | 14.8589 | 9.2377 | 8.8867 | 8.8935 | 8.9631 | 8.8024 | 8.7181 | 8.6427 | 13.2482 | 13.077 | 12.8923 | 11.9613 | 10.8167 | 10.1499 | 10.6062 | 18.4477 | 18.0967 | 18.0967 | 18.1731 | 18.0124 | 17.9281 | 17.8527 | 17.8482 | 17.677 | 17.4923 | 16.5613 | 15.4167 | 14.7499 | 15.2062 | 385349 | 433821 | BURNLEY | ROCHDALE
| Heaton Moor | 4.7909 | 4.3492 | 3.9936 | 3.5714 | 3.4169 | 2.9758 | 2.4119 | 2.0214 | 1.5369 | 0.97301 | -1.0459 | -2.1882 | -2.74 | -2.7483 | 14.7909 | 14.3492 | 13.9936 | 13.5714 | 13.4169 | 12.9758 | 12.4119 | 12.0214 | 11.5369 | 10.973 | 8.9541 | 7.8118 | 7.26 | 7.2517 | 4.9404 | 4.654 | 4.2797 | 3.904 | 3.7808 | 3.4339 | 2.9012 | 2.6124 | 2.2349 | 1.7746 | 0.33329 | -0.67631 | -1.3658 | -1.6499 | 14.9404 | 14.654 | 14.2797 | 13.904 | 13.7808 | 13.4339 | 12.9012 | 12.6124 | 12.2349 | 11.7746 | 10.3333 | 9.3237 | 8.6342 | 8.3501 | 4.7919 | 4.3866 | 4.036 | 3.659 | 3.4869 | 3.054 | 2.4687 | 2.091 | 1.675 | 1.1587 | -0.71316 | -1.6154 | -1.908 | -1.7232 | 14.7919 | 14.3866 | 14.036 | 13.659 | 13.4869 | 13.054 | 12.4687 | 12.091 | 11.675 | 11.1587 | 9.2868 | 8.3846 | 8.092 | 8.2768 | 4.8006 | 4.3717 | 4.0389 | 3.6445 | 3.5248 | 3.1588 | 2.6214 | 2.2991 | 1.8755 | 1.4852 | -1.2834 | -6.2127 | -10.1158 | -12.3675 | 14.8006 | 14.3717 | 14.0389 | 13.6445 | 13.5248 | 13.1588 | 12.6214 | 12.2991 | 11.8755 | 11.4852 | 8.7166 | 3.7873 | -0.1158 | -2.3675 | 4.778 | 4.293 | 3.965 | 3.6011 | 3.5251 | 3.1502 | 2.6435 | 2.3505 | 1.8717 | 0.72516 | -4.9703 | -9.4428 | -12.0586 | -11.1545 | 14.778 | 14.293 | 14.293 | 13.6011 | 13.5251 | 13.1502 | 12.6435 | 12.3505 | 11.8717 | 10.7252 | 5.0297 | 0.55722 | -2.0586 | -1.1545 | 387623 | 391345 | VERNON PARK | BREDBURY
| Heaton Norris | 2.87 | 2.0417 | 1.9956 | 1.5249 | 1.6542 | 1.2515 | 0.69878 | -2.1354 | -2.5015 | -2.963 | -8.3311 | -9.3464 | -9.7454 | -9.2998 | 9.87 | 9.0417 | 8.9956 | 8.5249 | 8.6542 | 8.2515 | 7.6988 | 4.8646 | 4.4985 | 4.037 | -1.3311 | -2.3464 | -2.7454 | -2.2998 | 3.2458 | 2.7421 | 2.6504 | 2.1326 | 2.1306 | 1.7329 | 1.2185 | 0.99375 | 0.55822 | 0.093176 | -1.0486 | -1.9706 | -2.6886 | -2.9957 | 10.2458 | 9.7421 | 9.6504 | 9.1326 | 9.1306 | 8.7329 | 8.2185 | 7.9938 | 7.5582 | 7.0932 | 5.9514 | 5.0294 | 4.3114 | 4.0043 | 2.8768 | 2.0517 | 2.0109 | 1.5537 | 1.6925 | 1.3028 | 0.74917 | -2.011 | -2.3556 | -2.7682 | -7.9643 | -8.8313 | -9.2241 | -8.7259 | 9.8768 | 9.0517 | 9.0109 | 8.5537 | 8.6925 | 8.3028 | 7.7492 | 4.989 | 4.6444 | 4.2318 | -0.96435 | -1.8313 | -2.2241 | -1.7259 | 2.8941 | 2.0879 | 2.0573 | 1.5949 | 1.7205 | 1.2956 | 0.67109 | -1.9416 | -2.3925 | -2.8029 | -9.1294 | -13.4115 | -17.1907 | -18.9173 | 9.8941 | 9.0879 | 9.0573 | 8.5949 | 8.7205 | 8.2956 | 7.6711 | 5.0584 | 4.6075 | 4.1971 | -2.1294 | -6.4115 | -10.1907 | -11.9173 | 2.904 | 2.0711 | 2.0265 | 1.5831 | 1.7175 | 1.3207 | 0.70561 | -1.8599 | -2.3448 | -6.2646 | -12.606 | -16.4334 | -18.9222 | -17.5536 | 9.904 | 9.0711 | 9.0711 | 8.5831 | 8.7175 | 8.3207 | 7.7056 | 5.1401 | 4.6552 | 0.73538 | -5.606 | -9.4334 | -11.9222 | -10.5536 | 388860 | 391967 | VERNON PARK | BREDBURY
| Helwith Bridge | 0.82087 | 0.70322 | 0.64022 | 0.58552 | 0.52408 | 0.4521 | 0.37346 | 0.29167 | 0.20437 | 0.089695 | -0.43166 | -0.65891 | -0.77745 | -0.78318 | 8.8209 | 8.7032 | 8.6402 | 8.5855 | 8.5241 | 8.4521 | 8.3735 | 8.2917 | 8.2044 | 8.0897 | 7.5683 | 7.3411 | 7.2225 | 7.2168 | 0.89688 | 0.84679 | 0.78596 | 0.74014 | 0.69069 | 0.63451 | 0.57256 | 0.50813 | 0.44238 | 0.37568 | 0.093332 | -0.12372 | -0.27312 | -0.38405 | 8.8969 | 8.8468 | 8.786 | 8.7401 | 8.6907 | 8.6345 | 8.5726 | 8.5081 | 8.4424 | 8.3757 | 8.0933 | 7.8763 | 7.7269 | 7.616 | 0.82144 | 0.70617 | 0.64578 | 0.59362 | 0.53449 | 0.46463 | 0.38797 | 0.30802 | 0.22444 | 0.12035 | -0.33925 | -0.53282 | -0.63331 | -0.62915 | 8.8214 | 8.7062 | 8.6458 | 8.5936 | 8.5345 | 8.4646 | 8.388 | 8.308 | 8.2244 | 8.1203 | 7.6607 | 7.4672 | 7.3667 | 7.3708 | 0.82184 | 0.69976 | 0.63027 | 0.56798 | 0.49179 | 0.39948 | 0.29157 | 0.1777 | 0.064859 | -0.054634 | -0.58805 | -1.2696 | -1.7099 | -1.9993 | 8.8218 | 8.6998 | 8.6303 | 8.568 | 8.4918 | 8.3995 | 8.2916 | 8.1777 | 8.0649 | 7.9454 | 7.412 | 6.7304 | 6.2901 | 6.0007 | 0.81357 | 0.67872 | 0.60352 | 0.53629 | 0.4513 | 0.356 | 0.2499 | 0.14202 | 0.033391 | -0.17033 | -1.0271 | -1.6088 | -1.8859 | -1.7804 | 8.8136 | 8.6787 | 8.6787 | 8.5363 | 8.4513 | 8.356 | 8.2499 | 8.142 | 8.0334 | 7.8297 | 6.9729 | 6.3912 | 6.1141 | 6.2196 | 381025 | 469428 | PADIHAM | PADIHAM
| Hensingham | 12.9701 | 12.7523 | 12.7697 | 12.5555 | 12.526 | 12.2195 | 11.9098 | 11.7058 | 11.3953 | 11.0291 | 9.7869 | 9.2022 | 9.1544 | 9.5437 | 17.1071 | 16.8893 | 16.9067 | 16.6925 | 16.663 | 16.3565 | 16.0468 | 15.8428 | 15.5323 | 15.1661 | 13.9239 | 13.3392 | 13.2914 | 13.6807 | 13.006 | 12.8578 | 12.82 | 12.607 | 12.5861 | 12.3196 | 12.0435 | 11.8579 | 11.5983 | 11.3329 | 10.6413 | 10.0361 | 9.6627 | 9.5313 | 17.143 | 16.9948 | 16.957 | 16.744 | 16.7231 | 16.4566 | 16.1805 | 15.9949 | 15.7353 | 15.4699 | 14.7783 | 14.1731 | 13.7997 | 13.6683 | 12.9742 | 12.7773 | 12.805 | 12.6002 | 12.5724 | 12.2962 | 11.9999 | 11.772 | 11.516 | 11.1795 | 10.0858 | 9.6245 | 9.6276 | 9.9558 | 17.1112 | 16.9143 | 16.942 | 16.7372 | 16.7094 | 16.4332 | 16.1369 | 15.909 | 15.653 | 15.3165 | 14.2228 | 13.7615 | 13.7646 | 14.0928 | 12.9727 | 12.7619 | 12.7864 | 12.5776 | 12.5727 | 12.2833 | 11.9537 | 11.7244 | 11.4565 | 11.192 | 9.6456 | 6.1628 | 3.5183 | 1.8087 | 17.1097 | 16.8989 | 16.9234 | 16.7146 | 16.7097 | 16.4203 | 16.0907 | 15.8614 | 15.5935 | 15.329 | 13.7826 | 10.2998 | 7.6553 | 5.9457 | 12.9981 | 12.7855 | 12.8147 | 12.6275 | 12.6135 | 12.3487 | 12.0695 | 11.9113 | 11.5867 | 10.7326 | 6.8854 | 3.7847 | 2.0688 | 2.7956 | 17.1351 | 16.9225 | 16.9225 | 16.7645 | 16.7505 | 16.4857 | 16.2065 | 16.0483 | 15.7237 | 14.8696 | 11.0224 | 7.9217 | 6.2058 | 6.9326 | 298465 | 517239 | EGREMONT | HARKER
| Heyrod | 9.6401 | 9.3502 | 9.3242 | 9.0837 | 8.9914 | 8.6461 | 8.3359 | 8.0571 | 7.669 | 7.2428 | 5.7254 | 4.7628 | 4.4096 | 4.3954 | 14.2771 | 13.9872 | 13.9612 | 13.7207 | 13.6284 | 13.2831 | 12.9729 | 12.6941 | 12.306 | 11.8798 | 10.3624 | 9.3998 | 9.0466 | 9.0324 | 9.7134 | 9.4559 | 9.3502 | 9.0894 | 8.9794 | 8.6303 | 8.3163 | 8.0594 | 7.659 | 7.2947 | 6.3 | 5.4006 | 4.8044 | 4.3903 | 14.3504 | 14.0929 | 13.9872 | 13.7264 | 13.6164 | 13.2673 | 12.9533 | 12.6964 | 12.296 | 11.9317 | 10.937 | 10.0376 | 9.4414 | 9.0273 | 9.6164 | 9.3469 | 9.322 | 9.1482 | 8.9952 | 8.7201 | 8.441 | 8.1759 | 7.8095 | 7.4223 | 6.0265 | 5.2066 | 4.9093 | 4.9449 | 14.2534 | 13.9839 | 13.959 | 13.7852 | 13.6322 | 13.3571 | 13.078 | 12.8129 | 12.4465 | 12.0593 | 10.6635 | 9.8436 | 9.5463 | 9.5819 | 9.6491 | 9.3597 | 9.3371 | 9.0955 | 9.0109 | 8.6588 | 8.3155 | 8.0069 | 7.6366 | 7.2874 | 5.1962 | 0.62072 | -2.8804 | -5.31 | 14.2861 | 13.9967 | 13.9741 | 13.7325 | 13.6479 | 13.2958 | 12.9525 | 12.6439 | 12.2736 | 11.9244 | 9.8332 | 5.2577 | 1.7566 | -0.67297 | 9.6839 | 9.421 | 9.4215 | 9.2235 | 9.1675 | 8.8654 | 8.575 | 8.3224 | 7.912 | 6.8432 | 1.8712 | -2.2535 | -4.5814 | -3.9911 | 14.3209 | 14.058 | 14.058 | 13.8605 | 13.8045 | 13.5024 | 13.212 | 12.9594 | 12.549 | 11.4802 | 6.5082 | 2.3835 | 0.055559 | 0.6459 | 397310 | 399981 | HARTSHEAD-HEYROD | STALYBRIDGE
| Heyside | 12.2108 | 11.803 | 11.7397 | 11.5322 | 11.3844 | 11.1278 | 10.9755 | 10.7236 | 10.395 | 10.0723 | 8.6951 | 7.5181 | 6.861 | 6.1645 | 16.8478 | 16.44 | 16.3767 | 16.1692 | 16.0214 | 15.7648 | 15.6125 | 15.3606 | 15.032 | 14.7093 | 13.3321 | 12.1551 | 11.498 | 10.8015 | 12.4169 | 12.1742 | 12.0557 | 11.8201 | 11.6817 | 11.4409 | 11.2945 | 11.0517 | 10.7347 | 10.462 | 9.5687 | 8.6607 | 7.9255 | 7.3537 | 17.0539 | 16.8112 | 16.6927 | 16.4571 | 16.3187 | 16.0779 | 15.9315 | 15.6887 | 15.3717 | 15.099 | 14.2057 | 13.2977 | 12.5625 | 11.9907 | 12.2049 | 11.8201 | 11.7611 | 11.5658 | 11.4265 | 11.1791 | 11.0342 | 10.7865 | 10.4708 | 10.1743 | 8.9709 | 8.1345 | 7.6394 | 7.3576 | 16.8419 | 16.4571 | 16.3981 | 16.2028 | 16.0635 | 15.8161 | 15.6712 | 15.4235 | 15.1078 | 14.8113 | 13.6079 | 12.7715 | 12.2764 | 11.9946 | 12.2212 | 11.8148 | 11.7537 | 11.5467 | 11.3995 | 11.1242 | 10.9268 | 10.6199 | 10.2702 | 9.9478 | 7.7406 | 3.4263 | -0.24848 | -2.6421 | 16.8582 | 16.4518 | 16.3907 | 16.1837 | 16.0365 | 15.7612 | 15.5638 | 15.2569 | 14.9072 | 14.5848 | 12.3776 | 8.0633 | 4.3885 | 1.9949 | 12.2291 | 11.829 | 11.7684 | 11.5749 | 11.4365 | 11.1691 | 10.9703 | 10.657 | 10.2055 | 9.2604 | 4.7159 | 0.56241 | -1.9137 | -1.7323 | 16.8661 | 16.466 | 16.466 | 16.2119 | 16.0735 | 15.8061 | 15.6073 | 15.294 | 14.8425 | 13.8974 | 9.3529 | 5.1994 | 2.7233 | 2.9047 | 393433 | 407129 | ROYTON | WHITEGATE
| Heywood | 6.7847 | 5.5946 | 2.9959 | -2.1226 | -7.2969 | -17.8136 | -20.4593 | 10.2991 | 10.2031 | 9.5374 | 8.3254 | 7.1664 | 6.4243 | 5.7346 | 7.4937 | 6.3036 | 3.7049 | -1.4136 | -6.5879 | -17.1046 | -19.7503 | -20.9009 | -20.9969 | -21.6626 | -22.8746 | -24.0336 | -24.7757 | -25.4654 | 7.3464 | 6.7701 | 4.7318 | 0.8255 | -3.127 | -11.1181 | -13.2255 | -14.1856 | -14.362 | -14.9736 | -15.8707 | -16.8262 | -17.6336 | -18.3606 | 8.0554 | 7.4791 | 5.4408 | 1.5345 | -2.418 | -10.4091 | -12.5165 | -13.4766 | -13.653 | -14.2646 | -15.1617 | -16.1172 | -16.9246 | -17.6516 | 6.7931 | 5.6392 | 3.0267 | -2.0829 | -7.2461 | -17.7493 | -20.381 | -21.5202 | -21.6 | -22.2277 | -23.2819 | -24.1705 | -24.7896 | -25.2346 | 7.5021 | 6.3482 | 3.7357 | -1.3739 | -6.5371 | -17.0403 | -19.672 | -20.8112 | -20.891 | -21.5187 | -22.5729 | -23.4615 | -24.0806 | -24.5256 | 6.79 | 5.6079 | 3.0175 | -2.096 | -7.2523 | -17.7775 | -20.4066 | -21.5714 | -21.683 | -22.2501 | -24.3737 | -29.4127 | -33.5125 | -36.4612 | 7.499 | 6.3169 | 3.7265 | -1.387 | -6.5433 | -17.0685 | -19.6976 | -20.8624 | -20.974 | -21.5411 | -23.6647 | -28.7037 | -32.8035 | -35.7522 | 6.789 | 5.6175 | 3.0663 | -1.9998 | -7.1156 | -17.653 | -20.2027 | -21.3252 | -21.6444 | -22.9191 | -28.0306 | -32.7351 | -35.537 | -35.4489 | 7.498 | 6.3265 | 6.3265 | -1.2908 | -6.4066 | -16.944 | -19.4937 | -20.6162 | -20.9354 | -22.2101 | -27.3216 | -32.0261 | -34.828 | -34.7399 | 385429 | 410369 | CASTLETON | ROCHDALE
| Higher Mill | 6.6354 | 6.3702 | 6.105 | 5.812 | 5.3989 | 4.9393 | 4.3779 | 3.8688 | 3.3271 | 2.6783 | 0.36097 | -0.90784 | -1.3608 | -1.3091 | 14.1354 | 13.8702 | 13.605 | 13.312 | 12.8989 | 12.4393 | 11.8779 | 11.3688 | 10.8271 | 10.1783 | 7.861 | 6.5922 | 6.1392 | 6.1909 | 6.7225 | 6.5439 | 6.2183 | 5.9423 | 5.576 | 5.1635 | 4.6577 | 4.2375 | 3.7573 | 3.2559 | 1.6071 | 0.36315 | -0.37376 | -0.80854 | 14.2225 | 14.0439 | 13.7183 | 13.4423 | 13.076 | 12.6635 | 12.1577 | 11.7375 | 11.2573 | 10.7559 | 9.1071 | 7.8632 | 7.1262 | 6.6915 | 6.6584 | 6.41 | 6.1444 | 5.8634 | 5.4662 | 5.0025 | 4.4541 | 3.9613 | 3.446 | 2.8589 | 0.75702 | -0.29687 | -0.62347 | -0.47154 | 14.1584 | 13.91 | 13.6444 | 13.3634 | 12.9662 | 12.5025 | 11.9541 | 11.4613 | 10.946 | 10.3589 | 8.257 | 7.2031 | 6.8765 | 7.0285 | 6.6448 | 6.3951 | 6.1572 | 5.895 | 5.5332 | 5.12 | 4.59 | 4.1447 | 3.7068 | 3.2518 | 0.32247 | -5.2998 | -9.6209 | -12.5342 | 14.1448 | 13.8951 | 13.6572 | 13.395 | 13.0332 | 12.62 | 12.09 | 11.6447 | 11.2068 | 10.7518 | 7.8225 | 2.2002 | -2.1209 | -5.0342 | 6.6331 | 6.3144 | 6.0707 | 5.834 | 5.4771 | 5.0908 | 4.6021 | 4.1912 | 3.6672 | 2.3269 | -3.945 | -8.9511 | -11.8599 | -11.1777 | 14.1331 | 13.8144 | 13.8144 | 13.334 | 12.9771 | 12.5908 | 12.1021 | 11.6912 | 11.1672 | 9.8269 | 3.555 | -1.4511 | -4.3599 | -3.6777 | 385731 | 388090 | MOSS NOOK | SOUTH MANCHESTER
| Higher Walton | 5.3097 | 4.8627 | 4.5314 | 4.013 | 3.813 | 3.2402 | 2.6988 | 2.0523 | 1.4083 | 0.61374 | -4.116 | -6.2595 | -7.2676 | -7.9409 | 9.9467 | 9.4997 | 9.1684 | 8.65 | 8.45 | 7.8772 | 7.3358 | 6.6893 | 6.0453 | 5.2507 | 0.52096 | -1.6225 | -2.6306 | -3.3039 | 5.5941 | 5.384 | 4.9649 | 4.4786 | 4.3332 | 3.8488 | 3.3502 | 2.7237 | 2.0747 | 1.4633 | -0.30188 | -1.8541 | -3.0466 | -3.9135 | 10.2311 | 10.021 | 9.6019 | 9.1156 | 8.9702 | 8.4858 | 7.9872 | 7.3607 | 6.7117 | 6.1003 | 4.3351 | 2.7829 | 1.5904 | 0.72346 | 5.3145 | 4.878 | 4.5599 | 4.0605 | 3.8773 | 3.3253 | 2.7413 | 2.1294 | 1.4915 | 0.7923 | -3.6018 | -5.2114 | -6.0241 | -6.2616 | 9.9515 | 9.515 | 9.1969 | 8.6975 | 8.5143 | 7.9623 | 7.3783 | 6.7664 | 6.1285 | 5.4293 | 1.0352 | -0.57442 | -1.3871 | -1.6246 | 5.3211 | 4.8732 | 4.5478 | 4.0457 | 3.857 | 3.2768 | 2.7071 | 2.0416 | 1.5148 | 0.89835 | -4.7331 | -13.3231 | -17.4452 | -20.0266 | 9.9581 | 9.5102 | 9.1848 | 8.6827 | 8.494 | 7.9138 | 7.3441 | 6.6786 | 6.1518 | 5.5353 | -0.09613 | -8.6861 | -12.8082 | -15.3896 | 5.2856 | 4.7802 | 4.4487 | 3.9585 | 3.7814 | 3.2276 | 2.5908 | 1.9303 | 1.1916 | -2.0322 | -11.1938 | -16.1845 | -19.0611 | -18.4732 | 9.9226 | 9.4172 | 9.4172 | 8.5955 | 8.4184 | 7.8646 | 7.2278 | 6.5673 | 5.8286 | 2.6048 | -6.5568 | -11.5475 | -14.4241 | -13.8362 | 358020 | 427270 | LEYLAND | PENWORTHAM
| Hill Top T11 & T12 | 5.2218 | 4.6961 | 4.2457 | 3.6864 | 3.0266 | 2.2468 | 1.4051 | 0.59418 | -0.26719 | -1.2244 | -4.9228 | -7.1489 | -8.0057 | -8.3071 | 9.3618 | 8.8361 | 8.3857 | 7.8264 | 7.1666 | 6.3868 | 5.5451 | 4.7342 | 3.8728 | 2.9156 | -0.7828 | -3.0089 | -3.8657 | -4.1671 | 5.4701 | 5.1638 | 4.6059 | 4.0524 | 3.4506 | 2.7448 | 1.9716 | 1.2231 | 0.44425 | -0.36703 | -3.1514 | -5.2069 | -6.4583 | -7.2865 | 9.6101 | 9.3038 | 8.7459 | 8.1924 | 7.5906 | 6.8848 | 6.1116 | 5.3631 | 4.5843 | 3.773 | 0.98861 | -1.0669 | -2.3183 | -3.1465 | 5.238 | 4.745 | 4.3269 | 3.7896 | 3.1652 | 2.4236 | 1.5928 | 0.78327 | -0.033821 | -0.89986 | -4.2186 | -6.0226 | -6.6775 | -6.7713 | 9.378 | 8.885 | 8.4669 | 7.9296 | 7.3052 | 6.5636 | 5.7328 | 4.9233 | 4.1062 | 3.2401 | -0.078627 | -1.8826 | -2.5375 | -2.6313 | 5.2484 | 4.7581 | 4.3495 | 3.8204 | 3.2561 | 2.5803 | 1.8337 | 1.1269 | 0.45335 | -0.25243 | -4.7087 | -11.8149 | -17.0927 | -20.7197 | 9.3884 | 8.8981 | 8.4895 | 7.9604 | 7.3961 | 6.7203 | 5.9737 | 5.2669 | 4.5933 | 3.8876 | -0.56872 | -7.6749 | -12.9527 | -16.5797 | 5.18 | 4.6046 | 4.1901 | 3.6946 | 3.1789 | 2.5788 | 1.8562 | 1.1967 | 0.40633 | -1.2823 | -9.5611 | -16.086 | -19.7425 | -18.9422 | 9.32 | 8.7446 | 8.7446 | 7.8346 | 7.3189 | 6.7188 | 5.9962 | 5.3367 | 4.5463 | 2.8577 | -5.4211 | -11.946 | -15.6025 | -14.8022 | 373466 | 403748 | KEARSLEY LOCAL | KEARSLEY
| Hill Top T13 | 4.5635 | 4.4325 | 4.2659 | 4.0873 | 3.9136 | 3.6606 | 3.4043 | 3.1637 | 2.907 | 2.6118 | 1.4316 | 0.62079 | 0.26449 | 0.048972 | 1.3135 | 1.1825 | 1.0159 | 0.83729 | 0.6636 | 0.41059 | 0.15429 | -0.086277 | -0.343 | -0.63818 | -1.8184 | -2.6292 | -2.9855 | -3.201 | 4.5952 | 4.4906 | 4.2846 | 4.1036 | 3.9408 | 3.7022 | 3.4582 | 3.23 | 2.9823 | 2.7274 | 1.8017 | 1.0591 | 0.58468 | 0.19652 | 1.3452 | 1.2406 | 1.0346 | 0.85361 | 0.6908 | 0.45222 | 0.20817 | -0.020037 | -0.26775 | -0.52258 | -1.4483 | -2.1909 | -2.6653 | -3.0535 | 4.5668 | 4.4424 | 4.2826 | 4.1099 | 3.9444 | 3.7008 | 3.4538 | 3.222 | 2.9782 | 2.7099 | 1.633 | 0.93379 | 0.63738 | 0.47305 | 1.3168 | 1.1924 | 1.0326 | 0.85986 | 0.6944 | 0.45083 | 0.20379 | -0.028009 | -0.27185 | -0.54011 | -1.617 | -2.3162 | -2.6126 | -2.777 | 4.5681 | 4.4434 | 4.2832 | 4.1052 | 3.9566 | 3.7299 | 3.4922 | 3.2708 | 3.0614 | 2.8442 | 1.1844 | -2.1828 | -4.9168 | -6.8447 | 1.3181 | 1.1934 | 1.0332 | 0.85518 | 0.70661 | 0.4799 | 0.24219 | 0.02079 | -0.1886 | -0.40577 | -2.0656 | -5.4328 | -8.1668 | -10.0947 | 4.5804 | 4.452 | 4.3022 | 4.1493 | 4.0279 | 3.8366 | 3.6321 | 3.4455 | 3.1562 | 2.413 | -1.228 | -4.3133 | -6.1844 | -6.0269 | 1.3304 | 1.202 | 1.202 | 0.89929 | 0.77786 | 0.58657 | 0.38206 | 0.19553 | -0.09381 | -0.83703 | -4.478 | -7.5633 | -9.4344 | -9.2769 | 373476 | 403758 | KEARSLEY LOCAL | KEARSLEY
| Hindley Green | 11.2458 | 10.2745 | 9.9225 | 9.1469 | 8.5835 | 7.677 | 6.6691 | 5.6479 | 4.5275 | 3.3121 | -0.9881 | -2.9065 | -3.2364 | -2.6478 | 18.2458 | 17.2745 | 16.9225 | 16.1469 | 15.5835 | 14.677 | 13.6691 | 12.6479 | 11.5275 | 10.3121 | 6.0119 | 4.0935 | 3.7636 | 4.3522 | 11.5352 | 10.8668 | 10.4147 | 9.6886 | 9.235 | 8.424 | 7.5884 | 6.7072 | 5.7868 | 4.916 | 1.9685 | 0.035303 | -1.1902 | -1.7105 | 18.5352 | 17.8668 | 17.4147 | 16.6886 | 16.235 | 15.424 | 14.5884 | 13.7072 | 12.7868 | 11.916 | 8.9685 | 7.0353 | 5.8098 | 5.2895 | 11.2717 | 10.3285 | 10.0045 | 9.2542 | 8.7216 | 7.8384 | 6.8804 | 5.8646 | 4.7921 | 3.6957 | -0.18978 | -1.757 | -1.9554 | -1.3781 | 18.2717 | 17.3285 | 17.0045 | 16.2542 | 15.7216 | 14.8384 | 13.8804 | 12.8646 | 11.7921 | 10.6957 | 6.8102 | 5.243 | 5.0446 | 5.6219 | 11.2565 | 10.2916 | 9.9856 | 9.258 | 8.7962 | 8.0114 | 7.1164 | 6.2308 | 5.4398 | 4.6974 | -0.41293 | -10.4586 | -18.4649 | -23.4046 | 18.2565 | 17.2916 | 16.9856 | 16.258 | 15.7962 | 15.0114 | 14.1164 | 13.2308 | 12.4398 | 11.6974 | 6.5871 | -3.4586 | -11.4649 | -16.4046 | 11.2723 | 10.2765 | 9.8999 | 9.2146 | 8.7982 | 8.113 | 7.3243 | 6.5773 | 5.6104 | 3.1358 | -8.4661 | -17.3804 | -22.6316 | -20.7337 | 18.2723 | 17.2765 | 17.2765 | 16.2146 | 15.7982 | 15.113 | 14.3243 | 13.5773 | 12.6104 | 10.1358 | -1.4661 | -10.3804 | -15.6316 | -13.7337 | 363389 | 403254 | ATHERTON | KEARSLEY
| Hollinwood | 13.4689 | 13.2082 | 13.0761 | 12.8819 | 12.7653 | 12.5401 | 12.3296 | 12.0779 | 11.7787 | 11.4624 | 10.2861 | 9.6461 | 9.4457 | 9.4276 | 18.1059 | 17.8452 | 17.7131 | 17.5189 | 17.4023 | 17.1771 | 16.9666 | 16.7149 | 16.4157 | 16.0994 | 14.9231 | 14.2831 | 14.0827 | 14.0646 | 13.6167 | 13.4837 | 13.3144 | 13.114 | 13.0074 | 12.8064 | 12.6166 | 12.3945 | 12.1147 | 11.849 | 11.0269 | 10.4801 | 10.1576 | 9.9523 | 18.2537 | 18.1207 | 17.9514 | 17.751 | 17.6444 | 17.4434 | 17.2536 | 17.0315 | 16.7517 | 16.486 | 15.6639 | 15.1171 | 14.7946 | 14.5893 | 13.477 | 13.2211 | 13.094 | 12.905 | 12.7935 | 12.5745 | 12.3696 | 12.1192 | 11.8345 | 11.5528 | 10.4899 | 9.9627 | 9.786 | 9.7767 | 18.114 | 17.8581 | 17.731 | 17.542 | 17.4305 | 17.2115 | 17.0066 | 16.7562 | 16.4715 | 16.1898 | 15.1269 | 14.5997 | 14.423 | 14.4137 | 13.4742 | 13.2181 | 13.0895 | 12.8957 | 12.7829 | 12.5557 | 12.331 | 12.0696 | 11.82 | 11.5647 | 10.2074 | 7.3157 | 4.9865 | 3.3226 | 18.1112 | 17.8551 | 17.7265 | 17.5327 | 17.4199 | 17.1927 | 16.968 | 16.7066 | 16.457 | 16.2017 | 14.8444 | 11.9527 | 9.6235 | 7.9596 | 13.4642 | 13.2052 | 13.0922 | 12.9291 | 12.8457 | 12.6558 | 12.4629 | 12.2381 | 11.9571 | 11.2327 | 8.0162 | 5.3624 | 3.7888 | 4.1023 | 18.1012 | 17.8422 | 17.8422 | 17.5661 | 17.4827 | 17.2928 | 17.0999 | 16.8751 | 16.5941 | 15.8697 | 12.6532 | 9.9994 | 8.4258 | 8.7393 | 390287 | 402592 | CHADDERTON | WHITEGATE
| Holme Rd | 7.1646 | 6.3781 | 6.0812 | 5.4367 | 5.167 | 4.4502 | 3.887 | 3.4497 | 2.7577 | 1.9611 | -0.9263 | -2.3167 | -2.7243 | -2.3505 | 11.3016 | 10.5151 | 10.2182 | 9.5737 | 9.304 | 8.5872 | 8.024 | 7.5867 | 6.8947 | 6.0981 | 3.2107 | 1.8203 | 1.4127 | 1.7865 | 7.4474 | 6.9164 | 6.5857 | 5.9639 | 5.7443 | 5.1027 | 4.6039 | 4.2205 | 3.5978 | 2.983 | 1.224 | -0.30629 | -1.3253 | -1.8745 | 11.5844 | 11.0534 | 10.7227 | 10.1009 | 9.8813 | 9.2397 | 8.7409 | 8.3575 | 7.7348 | 7.12 | 5.361 | 3.8307 | 2.8117 | 2.2625 | 7.1733 | 6.4095 | 6.1313 | 5.5066 | 5.2594 | 4.5717 | 4.0343 | 3.6194 | 2.967 | 2.2118 | -0.35809 | -1.5113 | -1.8525 | -1.4657 | 11.3103 | 10.5465 | 10.2683 | 9.6436 | 9.3964 | 8.7087 | 8.1713 | 7.7564 | 7.104 | 6.3488 | 3.7789 | 2.6257 | 2.2845 | 2.6713 | 7.1847 | 6.4266 | 6.1689 | 5.5687 | 5.3828 | 4.7519 | 4.2239 | 3.8334 | 3.2788 | 2.7418 | -0.49999 | -6.9322 | -12.095 | -15.4109 | 11.3217 | 10.5636 | 10.3059 | 9.7057 | 9.5198 | 8.8889 | 8.3609 | 7.9704 | 7.4158 | 6.8788 | 3.637 | -2.7952 | -7.958 | -11.2739 | 7.1315 | 6.3012 | 6.0544 | 5.4869 | 5.291 | 4.6928 | 4.2438 | 3.9499 | 3.2637 | 1.653 | -5.5726 | -11.3926 | -14.8209 | -13.8458 | 11.2685 | 10.4382 | 10.4382 | 9.6239 | 9.428 | 8.8298 | 8.3808 | 8.0869 | 7.4007 | 5.79 | -1.4356 | -7.2556 | -10.6839 | -9.7088 | 352311 | 429141 | RIBBLE | PENWORTHAM
| Holt St | 3.7941 | 3.2999 | 2.9782 | 2.4615 | 2.0513 | 1.363 | 0.77572 | 0.17001 | -0.45794 | -1.2338 | -3.7189 | -5.1572 | -5.7577 | -5.9845 | 7.2941 | 6.7999 | 6.4782 | 5.9615 | 5.5513 | 4.863 | 4.2757 | 3.67 | 3.0421 | 2.2662 | -0.21888 | -1.6572 | -2.2577 | -2.4845 | 4.013 | 3.6923 | 3.3493 | 2.9247 | 2.6132 | 2.0412 | 1.5645 | 1.0687 | 0.54238 | -0.052839 | -1.803 | -3.0663 | -3.9544 | -4.4655 | 7.513 | 7.1923 | 6.8493 | 6.4247 | 6.1132 | 5.5412 | 5.0645 | 4.5687 | 4.0424 | 3.4472 | 1.697 | 0.43366 | -0.4544 | -0.96553 | 3.7954 | 3.3158 | 2.9913 | 2.483 | 2.0836 | 1.4095 | 0.83437 | 0.23952 | -0.36692 | -1.0789 | -3.3119 | -4.4117 | -4.8376 | -4.8605 | 7.2954 | 6.8158 | 6.4913 | 5.983 | 5.5836 | 4.9095 | 4.3344 | 3.7395 | 3.1331 | 2.4211 | 0.18809 | -0.91174 | -1.3376 | -1.3605 | 3.8174 | 3.3436 | 3.0712 | 2.6172 | 2.2964 | 1.7101 | 1.2089 | 0.68404 | 0.20762 | -0.33774 | -3.7102 | -9.7021 | -14.2151 | -16.8848 | 7.3174 | 6.8436 | 6.5712 | 6.1172 | 5.7964 | 5.2101 | 4.7089 | 4.184 | 3.7076 | 3.1623 | -0.21022 | -6.2021 | -10.7151 | -13.3848 | 3.7416 | 3.1773 | 2.8572 | 2.4358 | 2.1631 | 1.6248 | 1.1589 | 0.69815 | 0.098609 | -1.3536 | -8.0578 | -13.3144 | -16.174 | -15.0992 | 7.2416 | 6.6773 | 6.6773 | 5.9358 | 5.6631 | 5.1248 | 4.6589 | 4.1982 | 3.5986 | 2.1464 | -4.5578 | -9.8144 | -12.674 | -11.5992 | 378620 | 416362 | BURY | KEARSLEY
| Hurst | 6.132 | 5.8969 | 5.6183 | 5.2642 | 5.0381 | 4.6423 | 4.1634 | 3.686 | 3.1784 | 2.604 | 0.71886 | -0.087593 | -0.13438 | 0.11364 | 9.632 | 9.3969 | 9.1183 | 8.7642 | 8.5381 | 8.1423 | 7.6634 | 7.186 | 6.6784 | 6.104 | 4.2189 | 3.4124 | 3.3656 | 3.6136 | 6.1939 | 6.0103 | 5.7022 | 5.3916 | 5.2687 | 4.9271 | 4.574 | 4.2256 | 3.8405 | 3.4378 | 2.0584 | 1.1791 | 0.71716 | 0.49262 | 9.6939 | 9.5103 | 9.2022 | 8.8916 | 8.7687 | 8.4271 | 8.074 | 7.7256 | 7.3405 | 6.9378 | 5.5584 | 4.6791 | 4.2172 | 3.9926 | 6.1414 | 5.9143 | 5.6442 | 5.2985 | 5.1055 | 4.7119 | 4.2411 | 3.7746 | 3.2866 | 2.7634 | 1.0704 | 0.38304 | 0.28804 | 0.49871 | 9.6414 | 9.4143 | 9.1442 | 8.7985 | 8.6055 | 8.2119 | 7.7411 | 7.2746 | 6.7866 | 6.2634 | 4.5704 | 3.883 | 3.788 | 3.9987 | 6.1367 | 5.9051 | 5.635 | 5.2929 | 5.1082 | 4.7481 | 4.3102 | 3.9006 | 3.5295 | 3.1392 | 0.7908 | -3.9373 | -7.6191 | -10.0706 | 9.6367 | 9.4051 | 9.135 | 8.7929 | 8.6082 | 8.2481 | 7.8102 | 7.4006 | 7.0295 | 6.6392 | 4.2908 | -0.43729 | -4.1191 | -6.5706 | 6.1521 | 5.9006 | 5.6274 | 5.3201 | 5.1428 | 4.848 | 4.4594 | 4.1243 | 3.6799 | 2.4848 | -2.9941 | -7.2416 | -9.6199 | -8.7456 | 9.6521 | 9.4006 | 9.4006 | 8.8201 | 8.6428 | 8.348 | 7.9594 | 7.6243 | 7.1799 | 5.9848 | 0.5059 | -3.7416 | -6.1199 | -5.2456 | 394658 | 400360 | HARTSHEAD-HEYROD | STALYBRIDGE
| Hutton End & Skelton C | 5.8724 | 5.6783 | 5.676 | 5.547 | 5.4052 | 5.1588 | 4.8773 | 4.7104 | 4.4498 | 4.0138 | 2.4413 | 1.5561 | 1.0902 | 1.3013 | 15.5124 | 15.3183 | 15.316 | 15.187 | 15.0452 | 14.7988 | 14.5173 | 14.3504 | 14.0898 | 13.6538 | 12.0813 | 11.1961 | 10.7302 | 10.9413 | 6.0679 | 6.0327 | 5.967 | 5.7466 | 5.6149 | 5.3802 | 5.1073 | 4.9417 | 4.7153 | 4.4453 | 3.6018 | 2.4762 | 1.5084 | 0.87828 | 15.7079 | 15.6727 | 15.607 | 15.3866 | 15.2549 | 15.0202 | 14.7473 | 14.5817 | 14.3553 | 14.0853 | 13.2418 | 12.1162 | 11.1484 | 10.5183 | 5.8743 | 5.6818 | 5.681 | 5.6146 | 5.4504 | 5.2501 | 4.9762 | 4.8148 | 4.5674 | 4.1676 | 2.7337 | 1.975 | 1.5825 | 1.822 | 15.5143 | 15.3218 | 15.321 | 15.2546 | 15.0904 | 14.8901 | 14.6162 | 14.4548 | 14.2074 | 13.8076 | 12.3737 | 11.615 | 11.2225 | 11.462 | 5.8881 | 5.7002 | 5.7032 | 5.5356 | 5.3532 | 5.0486 | 4.6803 | 4.4418 | 4.1669 | 3.8573 | 2.5536 | 1.7701 | 1.704 | 1.6175 | 15.5281 | 15.3402 | 15.3432 | 15.1756 | 14.9932 | 14.6886 | 14.3203 | 14.0818 | 13.8069 | 13.4973 | 12.1936 | 11.4101 | 11.344 | 11.2575 | 5.8824 | 5.6797 | 5.6755 | 5.4959 | 5.2747 | 4.9569 | 4.6067 | 4.3947 | 4.1475 | 3.809 | 2.3882 | 1.7887 | 1.889 | 2.2233 | 15.5224 | 15.3197 | 15.3197 | 15.1359 | 14.9147 | 14.5969 | 14.2467 | 14.0347 | 13.7875 | 13.449 | 12.0282 | 11.4287 | 11.529 | 11.8633 | 345810 | 538827 | PENRITH & SHAP | HUTTON
| Hyde | 6.8389 | 6.5656 | 6.3122 | 5.9217 | 5.7543 | 5.2662 | 4.7898 | 4.3577 | 3.8702 | 3.2299 | 1.2511 | 0.188 | -0.078559 | 0.044764 | 11.4759 | 11.2026 | 10.9492 | 10.5587 | 10.3913 | 9.9032 | 9.4268 | 8.9947 | 8.5072 | 7.8669 | 5.8881 | 4.825 | 4.5584 | 4.6818 | 6.9197 | 6.7028 | 6.3419 | 5.925 | 5.7599 | 5.2767 | 4.7968 | 4.3556 | 3.8467 | 3.2478 | 1.882 | 0.83211 | 0.17743 | -0.21291 | 11.5567 | 11.3398 | 10.9789 | 10.562 | 10.3969 | 9.9137 | 9.4338 | 8.9926 | 8.4837 | 7.8848 | 6.519 | 5.4691 | 4.8144 | 4.4241 | 6.8505 | 6.593 | 6.3563 | 5.9828 | 5.8298 | 5.3613 | 4.9037 | 4.4888 | 4.0276 | 3.4459 | 1.6907 | 0.73287 | 0.53738 | 0.65868 | 11.4875 | 11.23 | 10.9933 | 10.6198 | 10.4668 | 9.9983 | 9.5407 | 9.1258 | 8.6646 | 8.0829 | 6.3277 | 5.3699 | 5.1744 | 5.2957 | 6.8453 | 6.5795 | 6.341 | 5.969 | 5.8345 | 5.382 | 4.9225 | 4.5047 | 4.0732 | 3.5617 | 0.96205 | -4.6028 | -8.975 | -11.821 | 11.4823 | 11.2165 | 10.978 | 10.606 | 10.4715 | 10.019 | 9.5595 | 9.1417 | 8.7102 | 8.1987 | 5.5991 | 0.034172 | -4.338 | -7.184 | 6.8929 | 6.6345 | 6.4131 | 6.0965 | 6.0089 | 5.6282 | 5.2431 | 4.9026 | 4.4017 | 2.9354 | -3.3772 | -8.3845 | -11.2254 | -10.2645 | 11.5299 | 11.2715 | 11.2715 | 10.7335 | 10.6459 | 10.2652 | 9.8801 | 9.5396 | 9.0387 | 7.5724 | 1.2598 | -3.7475 | -6.5884 | -5.6275 | 395215 | 395126 | HYDE | STALYBRIDGE
| Hyndburn Rd | 4.0475 | 3.833 | 3.8495 | 3.7745 | 3.6747 | 3.5433 | 3.4013 | 3.256 | 3.1112 | 2.9591 | 2.3451 | 1.8021 | 1.5218 | 1.3147 | 16.3475 | 16.133 | 16.1495 | 16.0745 | 15.9747 | 15.8433 | 15.7013 | 15.556 | 15.4112 | 15.2591 | 14.6451 | 14.1021 | 13.8218 | 13.6147 | 4.2484 | 4.2133 | 4.0767 | 3.9095 | 3.7509 | 3.5577 | 3.3461 | 3.0705 | 2.7254 | 2.3536 | 1.9754 | 1.6284 | 1.4454 | 1.3282 | 16.5484 | 16.5133 | 16.3767 | 16.2095 | 16.0509 | 15.8577 | 15.6461 | 15.3705 | 15.0254 | 14.6536 | 14.2754 | 13.9284 | 13.7454 | 13.6282 | 4.055 | 3.8598 | 3.8572 | 3.7886 | 3.6902 | 3.5695 | 3.4293 | 3.2891 | 3.154 | 3.0128 | 2.4632 | 2.0751 | 1.8692 | 1.7796 | 16.355 | 16.1598 | 16.1572 | 16.0886 | 15.9902 | 15.8695 | 15.7293 | 15.5891 | 15.454 | 15.3128 | 14.7632 | 14.3751 | 14.1692 | 14.0796 | 4.0603 | 3.8581 | 3.8851 | 3.8194 | 3.7247 | 3.5933 | 3.4416 | 3.2784 | 3.1195 | 2.9607 | 1.7515 | -0.86125 | -2.9052 | -4.2712 | 16.3603 | 16.1581 | 16.1851 | 16.1194 | 16.0247 | 15.8933 | 15.7416 | 15.5784 | 15.4195 | 15.2607 | 14.0515 | 11.4388 | 9.3948 | 8.0288 | 4.0812 | 3.8916 | 3.9305 | 3.8788 | 3.8018 | 3.6893 | 3.5383 | 3.3783 | 3.1578 | 2.5505 | -0.29855 | -2.7959 | -4.241 | -3.6479 | 16.3812 | 16.1916 | 16.1916 | 16.1788 | 16.1018 | 15.9893 | 15.8383 | 15.6783 | 15.4578 | 14.8505 | 12.0014 | 9.5041 | 8.059 | 8.6521 | 375688 | 428877 | HUNCOAT | PADIHAM
| India St | 12.8008 | 12.3047 | 12.0847 | 11.7503 | 11.6339 | 11.2771 | 10.9935 | 10.7587 | 10.3925 | 9.9751 | 6.3821 | 5.3109 | 5.0639 | 5.2138 | 17.4378 | 16.9417 | 16.7217 | 16.3873 | 16.2709 | 15.9141 | 15.6305 | 15.3957 | 15.0295 | 14.6121 | 11.0191 | 9.9479 | 9.7009 | 9.8508 | 12.9848 | 12.6788 | 12.4675 | 12.1571 | 12.0613 | 11.7337 | 11.4722 | 11.2552 | 10.9066 | 10.5659 | 9.7237 | 9.0453 | 8.5523 | 8.3099 | 17.6218 | 17.3158 | 17.1045 | 16.7941 | 16.6983 | 16.3707 | 16.1092 | 15.8922 | 15.5436 | 15.2029 | 14.3607 | 13.6823 | 13.1893 | 12.9469 | 12.7959 | 12.3247 | 12.1046 | 11.7963 | 11.6922 | 11.351 | 11.0809 | 10.858 | 10.5119 | 10.135 | 6.6975 | 5.7738 | 5.5603 | 5.7519 | 17.4329 | 16.9617 | 16.7416 | 16.4333 | 16.3292 | 15.988 | 15.7179 | 15.495 | 15.1489 | 14.772 | 11.3345 | 10.4108 | 10.1973 | 10.3889 | 12.8033 | 12.3086 | 12.0945 | 11.7702 | 11.6718 | 11.3329 | 11.0569 | 10.8315 | 10.5225 | 10.2259 | 6.0686 | 0.44807 | -3.1369 | -5.2669 | 17.4403 | 16.9456 | 16.7315 | 16.4072 | 16.3088 | 15.9699 | 15.6939 | 15.4685 | 15.1595 | 14.8629 | 10.7056 | 5.0851 | 1.5001 | -0.62995 | 12.8215 | 12.3099 | 12.1093 | 11.8228 | 11.7576 | 11.4687 | 11.2423 | 11.0732 | 10.2315 | 7.277 | 1.1697 | -2.7861 | -5.1256 | -4.2143 | 17.4585 | 16.9469 | 16.9469 | 16.4598 | 16.3946 | 16.1057 | 15.8793 | 15.7102 | 14.8685 | 11.914 | 5.8067 | 1.8509 | -0.4886 | 0.42271 | 369485 | 421865 | LOWER DARWEN | ROCHDALE
| Ingleton | 1.7089 | 1.651 | 1.5855 | 1.4831 | 1.4732 | 1.3375 | 1.2499 | 1.1395 | 1.0782 | 0.92948 | 0.41036 | 0.13731 | -0.02625 | -0.017735 | 9.7089 | 9.651 | 9.5855 | 9.4831 | 9.4732 | 9.3375 | 9.2499 | 9.1395 | 9.0782 | 8.9295 | 8.4104 | 8.1373 | 7.9738 | 7.9823 | 1.752 | 1.7289 | 1.6363 | 1.5289 | 1.5118 | 1.3711 | 1.2746 | 1.1513 | 1.0763 | 0.94294 | 0.65845 | 0.39142 | 0.15261 | -0.0055132 | 9.752 | 9.7289 | 9.6363 | 9.5289 | 9.5118 | 9.3711 | 9.2746 | 9.1513 | 9.0763 | 8.9429 | 8.6584 | 8.3914 | 8.1526 | 7.9945 | 1.7118 | 1.6579 | 1.598 | 1.503 | 1.4975 | 1.3694 | 1.288 | 1.1845 | 1.1294 | 0.99706 | 0.52718 | 0.28569 | 0.13838 | 0.14131 | 9.7118 | 9.6579 | 9.598 | 9.503 | 9.4975 | 9.3694 | 9.288 | 9.1845 | 9.1294 | 8.9971 | 8.5272 | 8.2857 | 8.1384 | 8.1413 | 1.7116 | 1.6485 | 1.5758 | 1.4647 | 1.4384 | 1.2777 | 1.1562 | 1.0103 | 0.92931 | 0.79179 | 0.22697 | -0.45591 | -0.90539 | -1.2219 | 9.7116 | 9.6485 | 9.5758 | 9.4647 | 9.4384 | 9.2777 | 9.1562 | 9.0103 | 8.9293 | 8.7918 | 8.227 | 7.5441 | 7.0946 | 6.7781 | 1.7134 | 1.6478 | 1.5794 | 1.4754 | 1.4505 | 1.2993 | 1.194 | 1.0694 | 1.0028 | 0.78558 | -0.1394 | -0.70469 | -0.98411 | -0.87725 | 9.7134 | 9.6478 | 9.6478 | 9.4754 | 9.4505 | 9.2993 | 9.194 | 9.0694 | 9.0028 | 8.7856 | 7.8606 | 7.2953 | 7.0159 | 7.1227 | 368913 | 472337 | KENDAL (PARKSIDE RD) | HUTTON
| Irlam | 5.2391 | 3.9969 | 3.4154 | 2.9256 | 3.1475 | 2.5474 | 1.987 | 1.4221 | 0.66282 | 0.026378 | -2.7164 | -5.3564 | -6.8178 | -8.8821 | 9.3791 | 8.1369 | 7.5554 | 7.0656 | 7.2875 | 6.6874 | 6.127 | 5.5621 | 4.8028 | 4.1664 | 1.4236 | -1.2164 | -2.6778 | -4.7421 | 5.676 | 4.9066 | 4.3292 | 3.7627 | 3.9852 | 3.3925 | 2.8289 | 2.2224 | 1.4892 | 0.90187 | -1.2581 | -3.3906 | -4.988 | -6.3673 | 9.816 | 9.0466 | 8.4692 | 7.9027 | 8.1252 | 7.5325 | 6.9689 | 6.3624 | 5.6292 | 5.0419 | 2.8819 | 0.74935 | -0.84797 | -2.2273 | 5.2496 | 4.0516 | 3.4919 | 2.9792 | 3.2591 | 2.6871 | 2.1289 | 1.5331 | 0.89564 | 0.32035 | -2.1726 | -4.1583 | -5.4283 | -6.2932 | 9.3896 | 8.1916 | 7.6319 | 7.1192 | 7.3991 | 6.8271 | 6.2689 | 5.6731 | 5.0356 | 4.4604 | 1.9674 | -0.018317 | -1.2883 | -2.1532 | 5.2436 | 4.0117 | 3.4332 | 2.9201 | 3.1747 | 2.5815 | 1.9842 | 1.346 | 0.55089 | -0.034677 | -4.383 | -12.6445 | -19.8278 | -24.1779 | 9.3836 | 8.1517 | 7.5732 | 7.0601 | 7.3147 | 6.7215 | 6.1242 | 5.486 | 4.6909 | 4.1053 | -0.24302 | -8.5045 | -15.6878 | -20.0379 | 5.2695 | 4.0259 | 3.4519 | 2.9809 | 3.2343 | 2.6583 | 2.0621 | 1.4379 | 0.41517 | -1.2242 | -9.7352 | -17.9777 | -23.1327 | -22.9052 | 9.4095 | 8.1659 | 8.1659 | 7.1209 | 7.3743 | 6.7983 | 6.2021 | 5.5779 | 4.5552 | 2.9158 | -5.5952 | -13.8377 | -18.9927 | -18.7652 | 371680 | 393360 | CARRINGTON BSP | CARRINGTON
| James St | 5.4429 | 4.552 | 4.5851 | 4.2919 | 4.1826 | 3.6173 | 3.2558 | 3.2715 | 2.6797 | 2.3619 | 0.9534 | -0.21456 | -0.96166 | -1.2972 | 9.5799 | 8.689 | 8.7221 | 8.4289 | 8.3196 | 7.7543 | 7.3928 | 7.4085 | 6.8167 | 6.4989 | 5.0904 | 3.9224 | 3.1753 | 2.8398 | 5.8585 | 5.3239 | 5.162 | 4.7387 | 4.5306 | 3.9075 | 3.4529 | 3.3707 | 2.6433 | 2.0844 | 1.0788 | 0.22592 | -0.40135 | -0.67581 | 9.9955 | 9.4609 | 9.299 | 8.8757 | 8.6676 | 8.0445 | 7.5899 | 7.5077 | 6.7803 | 6.2214 | 5.2158 | 4.3629 | 3.7356 | 3.4612 | 5.4551 | 4.5937 | 4.6476 | 4.3776 | 4.2912 | 3.7574 | 3.4236 | 3.4587 | 2.9057 | 2.6361 | 1.4172 | 0.56315 | -0.0244 | -0.13249 | 9.5921 | 8.7307 | 8.7846 | 8.5146 | 8.4282 | 7.8944 | 7.5606 | 7.5957 | 7.0427 | 6.7731 | 5.5542 | 4.7001 | 4.1126 | 4.0045 | 5.4547 | 4.5727 | 4.6076 | 4.3049 | 4.185 | 3.5985 | 3.1933 | 3.1525 | 2.5126 | 2.1822 | -0.32688 | -5.9119 | -10.6207 | -13.407 | 9.5917 | 8.7097 | 8.7446 | 8.4419 | 8.322 | 7.7355 | 7.3303 | 7.2895 | 6.6496 | 6.3192 | 3.8101 | -1.7749 | -6.4837 | -9.27 | 5.4789 | 4.6022 | 4.6482 | 4.3732 | 4.2874 | 3.7422 | 3.3656 | 3.3527 | 2.6491 | 1.4585 | -4.7285 | -10.1005 | -13.277 | -12.1935 | 9.6159 | 8.7392 | 8.7392 | 8.5102 | 8.4244 | 7.8792 | 7.5026 | 7.4897 | 6.7861 | 5.5955 | -0.59146 | -5.9635 | -9.14 | -8.0565 | 340034 | 555418 | CARLISLE | HARKER
| Kay St | 13.4465 | 13.2958 | 13.1224 | 12.8751 | 12.5707 | 12.2261 | 11.846 | 11.4452 | 10.9914 | 10.4619 | 8.7482 | 8.0459 | 8.0917 | 8.3459 | 17.5835 | 17.4328 | 17.2594 | 17.0121 | 16.7077 | 16.3631 | 15.983 | 15.5822 | 15.1284 | 14.5989 | 12.8852 | 12.1829 | 12.2287 | 12.4829 | 13.4928 | 13.3878 | 13.1785 | 12.946 | 12.6775 | 12.3733 | 12.0351 | 11.6749 | 11.2892 | 10.9115 | 9.8389 | 9.1064 | 8.7757 | 8.6314 | 17.6298 | 17.5248 | 17.3155 | 17.083 | 16.8145 | 16.5103 | 16.1721 | 15.8119 | 15.4262 | 15.0485 | 13.9759 | 13.2434 | 12.9127 | 12.7684 | 13.4539 | 13.3257 | 13.1686 | 12.9324 | 12.6415 | 12.3111 | 11.945 | 11.5402 | 11.0869 | 10.6046 | 9.0526 | 8.4736 | 8.556 | 8.8878 | 17.5909 | 17.4627 | 17.3056 | 17.0694 | 16.7785 | 16.4481 | 16.082 | 15.6772 | 15.2239 | 14.7416 | 13.1896 | 12.6106 | 12.693 | 13.0248 | 13.4523 | 13.3117 | 13.1562 | 12.9358 | 12.6721 | 12.3741 | 12.0375 | 11.6888 | 11.3735 | 11.0739 | 8.8747 | 4.2595 | 0.81908 | -1.2956 | 17.5893 | 17.4487 | 17.2932 | 17.0728 | 16.8091 | 16.5111 | 16.1745 | 15.8258 | 15.5105 | 15.2109 | 13.0117 | 8.3965 | 4.9561 | 2.8414 | 13.4676 | 13.2899 | 13.1266 | 12.9319 | 12.6926 | 12.4414 | 12.1527 | 11.8662 | 11.4407 | 10.2879 | 5.0188 | 0.916 | -1.2139 | -0.11964 | 17.6046 | 17.4269 | 17.4269 | 17.0689 | 16.8296 | 16.5784 | 16.2897 | 16.0032 | 15.5777 | 14.4249 | 9.1558 | 5.053 | 2.9231 | 4.0174 | 373863 | 427594 | HUNCOAT | PADIHAM
| Kendal | 4.0473 | 3.2906 | 3.2263 | 2.7271 | 2.584 | 1.9289 | 1.3541 | 1.1563 | 0.45436 | -0.25491 | -2.6713 | -4.1145 | -4.923 | -4.7459 | 8.1873 | 7.4306 | 7.3663 | 6.8671 | 6.724 | 6.0689 | 5.4941 | 5.2963 | 4.5944 | 3.8851 | 1.4687 | 0.025511 | -0.78302 | -0.6059 | 4.1983 | 3.5716 | 3.3995 | 2.8796 | 2.7197 | 2.0458 | 1.4382 | 1.1966 | 0.44907 | -0.17297 | -1.6808 | -3.1718 | -4.4417 | -5.1652 | 8.3383 | 7.7116 | 7.5395 | 7.0196 | 6.8597 | 6.1858 | 5.5782 | 5.3366 | 4.5891 | 3.967 | 2.4592 | 0.96818 | -0.30173 | -1.0252 | 4.0612 | 3.3484 | 3.32 | 2.8539 | 2.7373 | 2.1176 | 1.5749 | 1.3995 | 0.74366 | 0.11694 | -2.022 | -3.2656 | -3.872 | -3.7197 | 8.2012 | 7.4884 | 7.46 | 6.9939 | 6.8773 | 6.2576 | 5.7149 | 5.5395 | 4.8837 | 4.2569 | 2.118 | 0.87438 | 0.26802 | 0.4203 | 4.0572 | 3.2967 | 3.23 | 2.7156 | 2.5478 | 1.8501 | 1.1954 | 0.92302 | 0.2288 | -0.32401 | -3.4067 | -9.6159 | -14.5896 | -17.825 | 8.1972 | 7.4367 | 7.37 | 6.8556 | 6.6878 | 5.9901 | 5.3354 | 5.063 | 4.3688 | 3.816 | 0.73333 | -5.4759 | -10.4496 | -13.685 | 4.0878 | 3.3305 | 3.2946 | 2.8385 | 2.7045 | 2.0763 | 1.5122 | 1.3386 | 0.60485 | -0.94734 | -8.0041 | -13.5815 | -16.9619 | -16.0213 | 8.2278 | 7.4705 | 7.4705 | 6.9785 | 6.8445 | 6.2163 | 5.6522 | 5.4786 | 4.7448 | 3.1927 | -3.8641 | -9.4415 | -12.8219 | -11.8813 | 351915 | 491858 | KENDAL (PARKSIDE RD) | HUTTON
| Keswick | 3.1502 | 2.8475 | 2.6637 | 2.4787 | 2.3425 | 2.1447 | 1.8617 | 1.6771 | 1.4709 | 1.1463 | 0.045352 | -0.53986 | -0.80095 | -0.65493 | 5.6502 | 5.3475 | 5.1637 | 4.9787 | 4.8425 | 4.6447 | 4.3617 | 4.1771 | 3.9709 | 3.6463 | 2.5454 | 1.9601 | 1.6991 | 1.8451 | 3.4055 | 3.3192 | 3.0584 | 2.8271 | 2.6508 | 2.4273 | 2.1066 | 1.8683 | 1.1904 | 0.37766 | -0.095812 | -0.36688 | -0.42518 | -0.53804 | 5.9055 | 5.8192 | 5.5584 | 5.3271 | 5.1508 | 4.9273 | 4.6066 | 4.3683 | 3.6904 | 2.8777 | 2.4042 | 2.1331 | 2.0748 | 1.962 | 3.1602 | 2.8725 | 2.7084 | 2.5459 | 2.4303 | 2.2539 | 1.9948 | 1.8316 | 1.6493 | 1.3721 | 0.41967 | -0.063579 | -0.27078 | -0.1325 | 5.6602 | 5.3725 | 5.2084 | 5.0459 | 4.9303 | 4.7539 | 4.4948 | 4.3316 | 4.1493 | 3.8721 | 2.9197 | 2.4364 | 2.2292 | 2.3675 | 3.1567 | 2.845 | 2.6459 | 2.4459 | 2.277 | 2.0328 | 1.6787 | 1.4157 | 1.1533 | 0.83881 | -0.5046 | -2.9841 | -4.8797 | -6.3035 | 5.6567 | 5.345 | 5.1459 | 4.9459 | 4.777 | 4.5328 | 4.1787 | 3.9157 | 3.6533 | 3.3388 | 1.9954 | -0.48408 | -2.3797 | -3.8035 | 3.162 | 2.8461 | 2.6544 | 2.4634 | 2.3024 | 2.0832 | 1.7697 | 1.5611 | 1.3418 | 0.68513 | -2.1602 | -4.5766 | -5.8238 | -5.3447 | 5.662 | 5.3461 | 5.3461 | 4.9634 | 4.8024 | 4.5832 | 4.2697 | 4.0611 | 3.8418 | 3.1851 | 0.33984 | -2.0766 | -3.3238 | -2.8447 | 327022 | 523784 | STAINBURN & SIDDICK | HARKER
| Kingsway | 23.5896 | 23.212 | 23.0252 | 23.0337 | 23.002 | 22.9113 | 22.7951 | 22.7364 | 22.7267 | 22.5951 | 22.3188 | 21.8705 | 21.4422 | 20.861 | 38.5896 | 38.212 | 38.0252 | 38.0337 | 38.002 | 37.9113 | 37.7951 | 37.7364 | 37.7267 | 37.5951 | 37.3188 | 36.8705 | 36.4422 | 35.861 | 23.8741 | 23.7593 | 23.5988 | 23.5741 | 23.5248 | 23.4364 | 23.3213 | 23.2556 | 23.2318 | 23.0973 | 22.856 | 22.5426 | 22.2163 | 21.9286 | 38.8741 | 38.7593 | 38.5988 | 38.5741 | 38.5248 | 38.4364 | 38.3213 | 38.2556 | 38.2318 | 38.0973 | 37.856 | 37.5426 | 37.2163 | 36.9286 | 23.5899 | 23.2125 | 23.0259 | 23.0341 | 23.0024 | 22.9118 | 22.796 | 22.7374 | 22.7284 | 22.6001 | 22.388 | 22.1459 | 21.8894 | 21.5676 | 38.5899 | 38.2125 | 38.0259 | 38.0341 | 38.0024 | 37.9118 | 37.796 | 37.7374 | 37.7284 | 37.6001 | 37.388 | 37.1459 | 36.8894 | 36.5676 | 23.6007 | 23.2347 | 23.0604 | 23.0818 | 23.0649 | 22.9824 | 22.8692 | 22.8071 | 22.7887 | 22.647 | 22.0668 | 21.0556 | 20.3508 | 20.0598 | 38.6007 | 38.2347 | 38.0604 | 38.0818 | 38.0649 | 37.9824 | 37.8692 | 37.8071 | 37.7887 | 37.647 | 37.0668 | 36.0556 | 35.3508 | 35.0598 | 23.5946 | 23.2179 | 23.0341 | 23.0482 | 23.0237 | 22.9247 | 22.7833 | 22.686 | 22.6265 | 22.4257 | 21.5668 | 20.6292 | 20.1971 | 20.1454 | 38.5946 | 38.2179 | 38.2179 | 38.0482 | 38.0237 | 37.9247 | 37.7833 | 37.686 | 37.6265 | 37.4257 | 36.5668 | 35.6292 | 35.1971 | 35.1454 | 391636 | 411724 | BELFIELD | ROCHDALE
| Kinkry Hill | 0.76685 | 0.72218 | 0.69233 | 0.64858 | 0.61405 | 0.56271 | 0.503 | 0.45001 | 0.38048 | 0.29447 | 0.0050717 | -0.11076 | -0.13332 | -0.044992 | 2.2668 | 2.2222 | 2.1923 | 2.1486 | 2.1141 | 2.0627 | 2.003 | 1.95 | 1.8805 | 1.7945 | 1.5051 | 1.3892 | 1.3667 | 1.455 | 0.78074 | 0.74896 | 0.71653 | 0.67997 | 0.64261 | 0.59815 | 0.53956 | 0.47993 | 0.41602 | 0.35087 | 0.20668 | 0.063047 | -0.064361 | -0.13203 | 2.2807 | 2.249 | 2.2165 | 2.18 | 2.1426 | 2.0981 | 2.0396 | 1.9799 | 1.916 | 1.8509 | 1.7067 | 1.563 | 1.4356 | 1.368 | 0.76768 | 0.72552 | 0.69789 | 0.65665 | 0.62377 | 0.5744 | 0.5165 | 0.46486 | 0.39901 | 0.32303 | 0.07069 | -0.034755 | -0.057942 | 0.0071844 | 2.2677 | 2.2255 | 2.1979 | 2.1566 | 2.1238 | 2.0744 | 2.0165 | 1.9649 | 1.899 | 1.823 | 1.5707 | 1.4652 | 1.4421 | 1.5072 | 0.768 | 0.7217 | 0.69101 | 0.64738 | 0.61003 | 0.55506 | 0.49087 | 0.43767 | 0.37813 | 0.32488 | 0.11802 | -0.12255 | -0.21687 | -0.26235 | 2.268 | 2.2217 | 2.191 | 2.1474 | 2.11 | 2.0551 | 1.9909 | 1.9377 | 1.8781 | 1.8249 | 1.618 | 1.3774 | 1.2831 | 1.2376 | 0.75805 | 0.70066 | 0.66876 | 0.62525 | 0.5831 | 0.5278 | 0.46747 | 0.42132 | 0.36999 | 0.31705 | 0.10713 | 0.013414 | -0.0068624 | 0.0080998 | 2.2581 | 2.2007 | 2.2007 | 2.1253 | 2.0831 | 2.0278 | 1.9675 | 1.9213 | 1.87 | 1.817 | 1.6071 | 1.5134 | 1.4931 | 1.5081 | 350800 | 575111 | - | HARKER
| Kirkby Lonsdale | 1.184 | 1.031 | 0.92894 | 0.78118 | 0.76739 | 0.5322 | 0.34235 | 0.15116 | -0.09216 | -0.419 | -1.5219 | -2.0408 | -2.1541 | -1.9133 | 5.184 | 5.031 | 4.9289 | 4.7812 | 4.7674 | 4.5322 | 4.3424 | 4.1512 | 3.9078 | 3.581 | 2.4781 | 1.9592 | 1.8459 | 2.0867 | 1.3427 | 1.3101 | 1.1447 | 0.9706 | 0.93943 | 0.71448 | 0.5205 | 0.36299 | 0.123 | -0.13437 | -0.80674 | -1.4298 | -1.8527 | -2.084 | 5.3427 | 5.3101 | 5.1447 | 4.9706 | 4.9394 | 4.7145 | 4.5205 | 4.363 | 4.123 | 3.8656 | 3.1933 | 2.5702 | 2.1473 | 1.916 | 1.1863 | 1.0358 | 0.94951 | 0.79531 | 0.7729 | 0.54249 | 0.35326 | 0.20908 | -0.02165 | -0.31822 | -1.3239 | -1.7784 | -1.8691 | -1.6374 | 5.1863 | 5.0358 | 4.9495 | 4.7953 | 4.7729 | 4.5425 | 4.3533 | 4.2091 | 3.9784 | 3.6818 | 2.6761 | 2.2216 | 2.1309 | 2.3626 | 1.1954 | 1.0445 | 0.94225 | 0.79088 | 0.75843 | 0.48575 | 0.22564 | 0.055402 | -0.14945 | -0.41262 | -1.3981 | -2.5536 | -3.1956 | -3.5921 | 5.1954 | 5.0445 | 4.9422 | 4.7909 | 4.7584 | 4.4857 | 4.2256 | 4.0554 | 3.8505 | 3.5874 | 2.6019 | 1.4464 | 0.80436 | 0.40789 | 1.1949 | 1.0354 | 0.94055 | 0.7944 | 0.72994 | 0.46063 | 0.2059 | 0.066789 | -0.12106 | -0.49485 | -2.0234 | -2.9448 | -3.278 | -2.9728 | 5.1949 | 5.0354 | 5.0354 | 4.7944 | 4.7299 | 4.4606 | 4.2059 | 4.0668 | 3.8789 | 3.5051 | 1.9766 | 1.0552 | 0.72201 | 1.0272 | 359833 | 478813 | KENDAL (PARKSIDE RD) | HUTTON
| Kirkby Moor | 2.1305 | 2.0318 | 1.9837 | 1.9262 | 1.8561 | 1.7384 | 1.6198 | 1.5306 | 1.3971 | 1.2596 | 0.76646 | 0.44269 | 0.27036 | 0.18028 | 5.6305 | 5.5318 | 5.4837 | 5.4262 | 5.3561 | 5.2384 | 5.1198 | 5.0306 | 4.8971 | 4.7596 | 4.2665 | 3.9427 | 3.7704 | 3.6803 | 2.2135 | 2.1837 | 2.11 | 2.0339 | 1.9451 | 1.8147 | 1.6798 | 1.5812 | 1.4317 | 1.2805 | 1.0247 | 0.88388 | 0.83454 | 0.88013 | 5.7135 | 5.6837 | 5.61 | 5.5339 | 5.4451 | 5.3147 | 5.1798 | 5.0812 | 4.9317 | 4.7805 | 4.5247 | 4.3839 | 4.3345 | 4.3801 | 2.133 | 2.0368 | 1.9915 | 1.9367 | 1.8697 | 1.7562 | 1.6493 | 1.5556 | 1.435 | 1.3117 | 0.84962 | 0.56679 | 0.41789 | 0.34317 | 5.633 | 5.5368 | 5.4915 | 5.4367 | 5.3697 | 5.2562 | 5.1493 | 5.0556 | 4.935 | 4.8117 | 4.3496 | 4.0668 | 3.9179 | 3.8432 | 2.1369 | 2.0427 | 1.9941 | 1.9319 | 1.8511 | 1.7156 | 1.5767 | 1.4436 | 1.2723 | 1.0833 | 0.35979 | -0.12233 | -0.33017 | -0.37551 | 5.6369 | 5.5427 | 5.4941 | 5.4319 | 5.3511 | 5.2156 | 5.0767 | 4.9436 | 4.7723 | 4.5833 | 3.8598 | 3.3777 | 3.1698 | 3.1245 | 2.1205 | 2.0042 | 1.9477 | 1.885 | 1.8053 | 1.6764 | 1.541 | 1.4203 | 1.2674 | 1.1001 | 0.5092 | 0.21928 | 0.11733 | 0.27242 | 5.6205 | 5.5042 | 5.5042 | 5.385 | 5.3053 | 5.1764 | 5.041 | 4.9203 | 4.7674 | 4.6001 | 4.0092 | 3.7193 | 3.6173 | 3.7724 | 326099 | 483011 | ULVERSTON | HARKER
| Kirkby Stephen | 8.564 | 8.2919 | 8.187 | 7.9703 | 7.8586 | 7.6468 | 7.4089 | 7.2129 | 6.9471 | 6.5205 | 4.8781 | 3.8292 | 3.194 | 3.2727 | 11.064 | 10.7919 | 10.687 | 10.4703 | 10.3586 | 10.1468 | 9.9089 | 9.7129 | 9.4471 | 9.0205 | 7.3781 | 6.3292 | 5.694 | 5.7727 | 8.6242 | 8.4122 | 8.2802 | 8.0953 | 7.9898 | 7.7733 | 7.5232 | 7.3266 | 7.0774 | 6.803 | 6.0405 | 4.8787 | 3.8421 | 3.1208 | 11.1242 | 10.9122 | 10.7802 | 10.5953 | 10.4898 | 10.2733 | 10.0232 | 9.8266 | 9.5774 | 9.303 | 8.5405 | 7.3787 | 6.3421 | 5.6208 | 8.565 | 8.3193 | 8.2306 | 8.0352 | 7.9042 | 7.7086 | 7.485 | 7.2853 | 7.0383 | 6.6569 | 5.185 | 4.3059 | 3.7803 | 3.9055 | 11.065 | 10.8193 | 10.7306 | 10.5352 | 10.4042 | 10.2086 | 9.985 | 9.7853 | 9.5383 | 9.1569 | 7.685 | 6.8059 | 6.2803 | 6.4055 | 8.5628 | 8.2587 | 8.1171 | 7.8609 | 7.6774 | 7.3585 | 6.9766 | 6.6678 | 6.329 | 5.9803 | 4.3119 | 2.5432 | 1.6167 | 1.0768 | 11.0628 | 10.7587 | 10.6171 | 10.3609 | 10.1774 | 9.8585 | 9.4766 | 9.1678 | 8.829 | 8.4803 | 6.8119 | 5.0432 | 4.1167 | 3.5768 | 8.5402 | 8.2139 | 8.0792 | 7.82 | 7.5921 | 7.2567 | 6.8924 | 6.5884 | 6.2667 | 5.7355 | 3.3183 | 1.7951 | 1.2174 | 1.4865 | 11.0402 | 10.7139 | 10.7139 | 10.32 | 10.0921 | 9.7567 | 9.3924 | 9.0884 | 8.7667 | 8.2355 | 5.8183 | 4.2951 | 3.7174 | 3.9865 | 376579 | 509136 | PENRITH & SHAP | HUTTON
| Kirkby Thore | 5.9369 | 5.7437 | 5.6784 | 5.488 | 5.3211 | 5.1729 | 4.9185 | 4.7363 | 4.5253 | 4.2881 | 3.3047 | 2.8601 | 2.7085 | 2.8297 | 17.1869 | 16.9937 | 16.9284 | 16.738 | 16.5711 | 16.4229 | 16.1685 | 15.9863 | 15.7753 | 15.5381 | 14.5547 | 14.1101 | 13.9585 | 14.0797 | 6.147 | 6.1204 | 5.9634 | 5.7293 | 5.5306 | 5.3641 | 5.0854 | 4.8704 | 4.6233 | 4.4009 | 3.7354 | 3.2003 | 2.7824 | 2.6421 | 17.397 | 17.3704 | 17.2134 | 16.9793 | 16.7806 | 16.6141 | 16.3354 | 16.1204 | 15.8733 | 15.6509 | 14.9854 | 14.4503 | 14.0324 | 13.8921 | 5.9422 | 5.7539 | 5.6944 | 5.5107 | 5.3508 | 5.2097 | 4.9637 | 4.789 | 4.5887 | 4.3713 | 3.4534 | 3.1007 | 2.9835 | 3.1613 | 17.1922 | 17.0039 | 16.9444 | 16.7607 | 16.6008 | 16.4597 | 16.2137 | 16.039 | 15.8387 | 15.6213 | 14.7034 | 14.3507 | 14.2335 | 14.4113 | 5.9575 | 5.7795 | 5.7332 | 5.5617 | 5.4057 | 5.2666 | 5.0138 | 4.8375 | 4.6606 | 4.5133 | 3.6115 | 2.2175 | 1.5885 | 1.3237 | 17.2075 | 17.0295 | 16.9832 | 16.8117 | 16.6557 | 16.5166 | 16.2638 | 16.0875 | 15.9106 | 15.7633 | 14.8615 | 13.4675 | 12.8385 | 12.5737 | 5.9557 | 5.7664 | 5.7224 | 5.5626 | 5.4088 | 5.2825 | 5.0484 | 4.3954 | 4.2681 | 4.0367 | 2.708 | 1.5993 | 1.2907 | 1.8105 | 17.2057 | 17.0164 | 17.0164 | 16.8126 | 16.6588 | 16.5325 | 16.2984 | 15.6454 | 15.5181 | 15.2867 | 13.958 | 12.8493 | 12.5407 | 13.0605 | 364439 | 526672 | PENRITH & SHAP | HUTTON
| Kirkhall Lane | 6.2095 | 5.7754 | 5.8238 | 5.3856 | 5.2704 | 4.8745 | 4.5214 | 4.1316 | 3.7432 | 3.2408 | 1.6902 | 0.97603 | 0.80231 | 1.0376 | 8.5595 | 8.1254 | 8.1738 | 7.7356 | 7.6204 | 7.2245 | 6.8714 | 6.4816 | 6.0932 | 5.5908 | 4.0402 | 3.326 | 3.1523 | 3.3876 | 6.271 | 5.8912 | 5.8943 | 5.4829 | 5.4616 | 5.0883 | 4.8258 | 4.5066 | 4.179 | 3.7944 | 2.6988 | 1.9575 | 1.4895 | 1.2744 | 8.621 | 8.2412 | 8.2443 | 7.8329 | 7.8116 | 7.4383 | 7.1758 | 6.8566 | 6.529 | 6.1444 | 5.0488 | 4.3075 | 3.8395 | 3.6244 | 6.2244 | 5.8011 | 5.868 | 5.4357 | 5.2541 | 4.8967 | 4.5539 | 4.1726 | 3.7787 | 3.3372 | 1.9264 | 1.2954 | 1.1436 | 1.3578 | 8.5744 | 8.1511 | 8.218 | 7.7857 | 7.6041 | 7.2467 | 6.9039 | 6.5226 | 6.1287 | 5.6872 | 4.2764 | 3.6454 | 3.4936 | 3.7078 | 6.2138 | 5.7844 | 5.839 | 5.4034 | 5.3729 | 4.9772 | 4.6487 | 4.2885 | 3.9864 | 3.6275 | 1.6503 | -2.4873 | -5.9014 | -8.1574 | 8.5638 | 8.1344 | 8.189 | 7.7534 | 7.7229 | 7.3272 | 6.9987 | 6.6385 | 6.3364 | 5.9775 | 4.0003 | -0.13729 | -3.5514 | -5.8074 | 6.2407 | 5.8063 | 5.8612 | 5.4609 | 5.4087 | 5.0598 | 4.7838 | 4.4902 | 4.1296 | 3.0616 | -1.6469 | -5.381 | -7.6417 | -6.9404 | 8.5907 | 8.1563 | 8.1563 | 7.8109 | 7.7587 | 7.4098 | 7.1338 | 6.8402 | 6.4796 | 5.4116 | 0.70306 | -3.031 | -5.2917 | -4.5904 | 365510 | 401069 | ATHERTON | KEARSLEY
| Kitt Green | 4.4102 | 3.8188 | 3.7556 | 3.6753 | 3.5389 | 3.3333 | 3.1287 | 2.953 | 2.742 | 2.5 | -6.3857 | -7.8726 | -8.6886 | -8.9338 | 11.4102 | 10.8188 | 10.7556 | 10.6753 | 10.5389 | 10.3333 | 10.1287 | 9.953 | 9.742 | 9.5 | 0.61427 | -0.87259 | -1.6886 | -1.9338 | 4.9004 | 4.7581 | 4.5922 | 4.4229 | 4.2236 | 3.9999 | 3.7515 | 3.5312 | 3.2851 | 3.031 | 2.1701 | 1.4494 | 0.8794 | 0.48233 | 11.9004 | 11.7581 | 11.5922 | 11.4229 | 11.2236 | 10.9999 | 10.7515 | 10.5312 | 10.2851 | 10.031 | 9.1701 | 8.4494 | 7.8794 | 7.4823 | 4.3966 | 3.8333 | 3.77 | 3.6921 | 3.5436 | 3.3571 | 3.172 | 2.976 | 2.7713 | 2.5515 | -6.1955 | -7.2696 | -7.8735 | -7.7538 | 11.3966 | 10.8333 | 10.77 | 10.6921 | 10.5436 | 10.3571 | 10.172 | 9.976 | 9.7713 | 9.5515 | 0.80454 | -0.26961 | -0.87349 | -0.75382 | 4.4452 | 3.8957 | 3.8707 | 3.8203 | 3.6775 | 3.4364 | 3.1748 | 2.9037 | 2.6527 | 2.3896 | -8.1344 | -14.6864 | -17.1922 | -17.9562 | 11.4452 | 10.8957 | 10.8707 | 10.8203 | 10.6775 | 10.4364 | 10.1748 | 9.9037 | 9.6527 | 9.3896 | -1.1344 | -7.6864 | -10.1922 | -10.9562 | 4.4445 | 3.8846 | 3.8533 | 3.8056 | 3.6889 | 3.479 | 3.1869 | 2.8344 | 2.4591 | -8.0319 | -10.5665 | -13.3685 | -15.0013 | -14.123 | 11.4445 | 10.8846 | 10.8846 | 10.8056 | 10.6889 | 10.479 | 10.1869 | 9.8344 | 9.4591 | -1.0319 | -3.5665 | -6.3685 | -8.0013 | -7.123 | 354934 | 405497 | ORRELL | KIRKBY
| Knott Mill | 3.3267 | 2.1903 | 2.043 | 1.8789 | 1.6532 | 1.3623 | 0.98178 | 7.3228 | 7.1882 | 6.872 | 5.6412 | 4.8812 | 4.5366 | 4.5412 | 7.9637 | 6.8273 | 6.68 | 6.5159 | 6.2902 | 5.9993 | 5.6188 | 5.3228 | 5.1882 | 4.872 | 3.6412 | 2.8812 | 2.5366 | 2.5412 | 3.9441 | 3.3709 | 3.1795 | 2.9305 | 2.6406 | 2.3032 | 1.8552 | 1.4738 | 1.2293 | 0.85208 | -0.10751 | -0.86581 | -1.3236 | -1.59 | 8.5811 | 8.0079 | 7.8165 | 7.5675 | 7.2776 | 6.9402 | 6.4922 | 6.1108 | 5.8663 | 5.4891 | 4.5295 | 3.7712 | 3.3134 | 3.047 | 3.3352 | 2.2195 | 2.0907 | 1.9423 | 1.7321 | 1.4558 | 1.0906 | 0.80874 | 0.6895 | 0.4006 | -0.74008 | -1.4641 | -1.779 | -1.7877 | 7.9722 | 6.8565 | 6.7277 | 6.5793 | 6.3691 | 6.0928 | 5.7276 | 5.4457 | 5.3265 | 5.0376 | 3.8969 | 3.1729 | 2.858 | 2.8493 | 3.3593 | 2.2522 | 2.1362 | 1.9954 | 1.7781 | 1.4835 | 1.0748 | 0.74154 | 0.6085 | 0.32789 | -1.2123 | -4.3138 | -6.6303 | -8.3608 | 7.9963 | 6.8892 | 6.7732 | 6.6324 | 6.4151 | 6.1205 | 5.7118 | 5.3785 | 5.2455 | 4.9649 | 3.4247 | 0.32319 | -1.9933 | -3.7238 | 3.3697 | 2.2847 | 2.2089 | 2.1238 | 1.9525 | 1.7152 | 1.3699 | 1.1047 | 1.0182 | 0.28609 | -3.2544 | -6.0504 | -7.6273 | -7.1708 | 8.0067 | 6.9217 | 6.9217 | 6.7608 | 6.5895 | 6.3522 | 6.0069 | 5.7417 | 5.6552 | 4.9231 | 1.3826 | -1.4134 | -2.9903 | -2.5338 | 383136 | 397725 | BLOOM ST | SOUTH MANCHESTER
| Lamberhead | 11.1581 | 10.5436 | 10.1682 | 9.8128 | 9.3581 | 8.8573 | 8.3157 | 7.7881 | 7.2459 | 6.6635 | 4.6006 | 3.6503 | 3.5407 | 3.8097 | 15.7981 | 15.1836 | 14.8082 | 14.4528 | 13.9981 | 13.4973 | 12.9557 | 12.4281 | 11.8859 | 11.3035 | 9.2406 | 8.2903 | 8.1807 | 8.4497 | 11.4778 | 11.1531 | 10.7913 | 10.4674 | 10.0919 | 9.6842 | 9.2396 | 8.8024 | 8.3436 | 7.8944 | 6.524 | 5.6971 | 5.339 | 5.2354 | 16.1178 | 15.7931 | 15.4313 | 15.1074 | 14.7319 | 14.3242 | 13.8796 | 13.4424 | 12.9836 | 12.5344 | 11.164 | 10.3371 | 9.979 | 9.8754 | 11.1621 | 10.552 | 10.1808 | 9.8301 | 9.3828 | 8.8911 | 8.3581 | 7.8379 | 7.3114 | 6.775 | 4.8667 | 4.0251 | 3.9383 | 4.2078 | 15.8021 | 15.192 | 14.8208 | 14.4701 | 14.0228 | 13.5311 | 12.9981 | 12.4779 | 11.9514 | 11.415 | 9.5067 | 8.6651 | 8.5783 | 8.8478 | 11.177 | 10.5869 | 10.2446 | 9.9299 | 9.5416 | 9.1201 | 8.6614 | 8.2262 | 7.8251 | 7.4365 | 4.9677 | -0.0067801 | -3.8003 | -6.2851 | 15.817 | 15.2269 | 14.8846 | 14.5699 | 14.1816 | 13.7601 | 13.3014 | 12.8662 | 12.4651 | 12.0765 | 9.6077 | 4.6332 | 0.83973 | -1.6451 | 11.0924 | 10.4169 | 10.0526 | 9.7512 | 9.3815 | 9.0097 | 8.5951 | 8.2291 | 7.7888 | 6.8524 | 1.2101 | -3.1199 | -5.4746 | -4.6887 | 15.7324 | 15.0569 | 15.0569 | 14.3912 | 14.0215 | 13.6497 | 13.2351 | 12.8691 | 12.4288 | 11.4924 | 5.8501 | 1.5201 | -0.83462 | -0.048748 | 355516 | 404030 | ORRELL | KIRKBY
| Lancaster | 3.4581 | 3.4905 | 3.2063 | 2.8105 | 0.50353 | 0.25055 | -0.29579 | -1.2193 | -1.4542 | -2.1007 | -4.8547 | -7.3633 | -8.9792 | -6.5449 | 7.5951 | 7.6275 | 7.3433 | 6.9475 | 4.6405 | 4.3875 | 3.8412 | 2.9177 | 2.6828 | 2.0363 | -0.71772 | -3.2263 | -4.8422 | -2.4079 | 3.8603 | 4.2203 | 3.836 | 3.43 | 2.746 | 2.4495 | 1.8768 | 0.95972 | 0.67035 | 0.095869 | -2.04 | -3.653 | -5.9483 | -4.4823 | 7.9973 | 8.3573 | 7.973 | 7.567 | 6.883 | 6.5865 | 6.0138 | 5.0967 | 4.8073 | 4.2329 | 2.097 | 0.48405 | -1.8113 | -0.34525 | 3.4742 | 3.5239 | 3.2607 | 2.8784 | 0.59045 | 0.35315 | -0.17641 | -1.0809 | -1.2924 | -1.8763 | -4.3665 | -6.5981 | -8.0566 | -5.5127 | 7.6112 | 7.6609 | 7.3977 | 7.0154 | 4.7274 | 4.4902 | 3.9606 | 3.0561 | 2.8446 | 2.2607 | -0.22951 | -2.4611 | -3.9196 | -1.3757 | 3.4915 | 3.5586 | 3.3224 | 2.9762 | 0.8041 | 0.62282 | 0.13369 | -1.8679 | -1.8847 | -2.2198 | -5.1141 | -11.0011 | -15.6714 | -14.9009 | 7.6285 | 7.6956 | 7.4594 | 7.1132 | 4.9411 | 4.7598 | 4.2707 | 2.2691 | 2.2523 | 1.9172 | -0.97711 | -6.8641 | -11.5344 | -10.7639 | 3.4618 | 3.473 | 3.2363 | 2.9299 | 2.3032 | -0.62019 | -0.95948 | -1.6665 | -1.695 | -2.7433 | -8.7431 | -13.0644 | -16.6062 | -12.7188 | 7.5988 | 7.61 | 7.61 | 7.0669 | 6.4402 | 3.5168 | 3.1775 | 2.4705 | 2.442 | 1.3937 | -4.6061 | -8.9274 | -12.4692 | -8.5818 | 348644 | 463628 | LANCASTER | HEYSHAM
| Langley | 8.3479 | 7.6495 | 7.3599 | 7.077 | 6.7228 | 6.2996 | 5.8764 | 5.3926 | 4.8779 | 4.3092 | 2.1753 | 0.90883 | 0.39944 | 0.32349 | 12.9849 | 12.2865 | 11.9969 | 11.714 | 11.3598 | 10.9366 | 10.5134 | 10.0296 | 9.5149 | 8.9462 | 6.8123 | 5.5458 | 5.0364 | 4.9605 | 8.5772 | 8.1446 | 7.8011 | 7.5688 | 7.2201 | 6.8305 | 6.4607 | 6.0201 | 5.5307 | 5.0704 | 3.5154 | 2.3061 | 1.536 | 0.97034 | 13.2142 | 12.7816 | 12.4381 | 12.2058 | 11.8571 | 11.4675 | 11.0977 | 10.6571 | 10.1677 | 9.7074 | 8.1524 | 6.9431 | 6.173 | 5.6073 | 8.366 | 7.7115 | 7.4067 | 7.1681 | 6.8225 | 6.4233 | 6.0323 | 5.5699 | 5.0846 | 4.5733 | 2.6592 | 1.5533 | 1.0888 | 0.991 | 13.003 | 12.3485 | 12.0437 | 11.8051 | 11.4595 | 11.0603 | 10.6693 | 10.2069 | 9.7216 | 9.2103 | 7.2962 | 6.1903 | 5.7258 | 5.628 | 8.3467 | 7.6454 | 7.3391 | 7.0429 | 6.6863 | 6.2443 | 5.7595 | 5.2019 | 4.6937 | 4.2063 | 1.2561 | -4.8919 | -9.7546 | -13.3585 | 12.9837 | 12.2824 | 11.9761 | 11.6799 | 11.3233 | 10.8813 | 10.3965 | 9.8389 | 9.3307 | 8.8433 | 5.8931 | -0.25492 | -5.1176 | -8.7215 | 8.392 | 7.7051 | 7.4177 | 7.1318 | 6.8073 | 6.4234 | 6.0091 | 5.5341 | 4.9753 | 3.5201 | -3.3649 | -8.9164 | -12.2494 | -11.7293 | 13.029 | 12.3421 | 12.3421 | 11.7688 | 11.4443 | 11.0604 | 10.6461 | 10.1711 | 9.6123 | 8.1571 | 1.2721 | -4.2794 | -7.6124 | -7.0923 | 386421 | 406330 | CHADDERTON | WHITEGATE
| Langroyd Rd | 10.5884 | 10.3041 | 10.117 | 9.868 | 9.5964 | 9.26 | 8.8642 | 8.4289 | 7.9993 | 7.4598 | 5.6514 | 4.7798 | 4.6508 | 4.9661 | 15.2284 | 14.9441 | 14.757 | 14.508 | 14.2364 | 13.9 | 13.5042 | 13.0689 | 12.6393 | 12.0998 | 10.2914 | 9.4198 | 9.2908 | 9.6061 | 10.7081 | 10.5158 | 10.2624 | 10.0109 | 9.7471 | 9.4348 | 9.0526 | 8.6405 | 8.2235 | 7.7868 | 6.6557 | 5.8033 | 5.337 | 5.0607 | 15.3481 | 15.1558 | 14.9024 | 14.6509 | 14.3871 | 14.0748 | 13.6926 | 13.2805 | 12.8635 | 12.4268 | 11.2957 | 10.4433 | 9.977 | 9.7007 | 10.6019 | 10.3315 | 10.1553 | 9.9317 | 9.6725 | 9.3534 | 8.9648 | 8.5625 | 8.1585 | 7.6824 | 6.0474 | 5.2779 | 5.2057 | 5.5102 | 15.2419 | 14.9715 | 14.7953 | 14.5717 | 14.3125 | 13.9934 | 13.6048 | 13.2025 | 12.7985 | 12.3224 | 10.6874 | 9.9179 | 9.8457 | 10.1502 | 10.5932 | 10.3005 | 10.1042 | 9.8483 | 9.5647 | 9.2061 | 8.7817 | 8.3307 | 7.9364 | 7.5275 | 5.0589 | -0.25553 | -4.1134 | -6.5713 | 15.2332 | 14.9405 | 14.7442 | 14.4883 | 14.2047 | 13.8461 | 13.4217 | 12.9707 | 12.5764 | 12.1675 | 9.6989 | 4.3845 | 0.52656 | -1.9313 | 10.6203 | 10.342 | 10.1725 | 9.9641 | 9.7157 | 9.4168 | 9.0662 | 8.7042 | 8.2384 | 6.9074 | 0.88333 | -3.7681 | -6.1347 | -4.9692 | 15.2603 | 14.982 | 14.982 | 14.6041 | 14.3557 | 14.0568 | 13.7062 | 13.3442 | 12.8784 | 11.5474 | 5.5233 | 0.87188 | -1.4947 | -0.32922 | 389077 | 440584 | NELSON | PADIHAM
| Leigh | 3.3292 | 3.1823 | 3.1688 | 3.0596 | 3.0324 | 2.8759 | 2.78 | 2.669 | 2.5684 | 2.3907 | 1.8879 | 1.5663 | 1.3897 | 1.3583 | 11.3292 | 11.1823 | 11.1688 | 11.0596 | 11.0324 | 10.8759 | 10.78 | 10.669 | 10.5684 | 10.3907 | 9.8879 | 9.5663 | 9.3897 | 9.3583 | 3.3846 | 3.2845 | 3.2362 | 3.1093 | 3.0696 | 2.9048 | 2.7957 | 2.668 | 2.5476 | 2.3727 | 2.0384 | 1.7512 | 1.5189 | 1.3743 | 11.3846 | 11.2845 | 11.2362 | 11.1093 | 11.0696 | 10.9048 | 10.7957 | 10.668 | 10.5476 | 10.3727 | 10.0384 | 9.7512 | 9.5189 | 9.3743 | 3.3328 | 3.1918 | 3.1833 | 3.0798 | 3.057 | 2.9071 | 2.8167 | 2.7113 | 2.6182 | 2.4564 | 1.9981 | 1.7174 | 1.5588 | 1.533 | 11.3328 | 11.1918 | 11.1833 | 11.0798 | 11.057 | 10.9071 | 10.8167 | 10.7113 | 10.6182 | 10.4564 | 9.9981 | 9.7174 | 9.5588 | 9.533 | 3.3309 | 3.1842 | 3.1698 | 3.0561 | 3.0259 | 2.8609 | 2.7448 | 2.6107 | 2.5009 | 2.3354 | 1.4827 | -0.51661 | -2.1257 | -3.1646 | 11.3309 | 11.1842 | 11.1698 | 11.0561 | 11.0259 | 10.8609 | 10.7448 | 10.6107 | 10.5009 | 10.3354 | 9.4827 | 7.4834 | 5.8743 | 4.8354 | 3.3479 | 3.2115 | 3.206 | 3.1069 | 3.0855 | 2.9373 | 2.8425 | 2.7321 | 2.5823 | 2.0528 | -0.18179 | -1.9849 | -3.0491 | -2.7343 | 11.3479 | 11.2115 | 11.2115 | 11.1069 | 11.0855 | 10.9373 | 10.8425 | 10.7321 | 10.5823 | 10.0528 | 7.8182 | 6.0151 | 4.9509 | 5.2657 | 365863 | 399907 | ATHERTON | KEARSLEY
| Levenshulme | 4.1317 | 4.0246 | 3.645 | 3.3831 | 3.0657 | 2.6917 | 2.0382 | 1.5815 | 1.2138 | 0.5623 | -1.6365 | -2.877 | -3.453 | -3.653 | 7.6317 | 7.5246 | 7.145 | 6.8831 | 6.5657 | 6.1917 | 5.5382 | 5.0815 | 4.7138 | 4.0623 | 1.8635 | 0.62298 | 0.047023 | -0.15302 | 4.1382 | 4.0334 | 3.595 | 3.3398 | 3.0424 | 2.6816 | 2.0352 | 1.5933 | 1.2511 | 0.33887 | -0.8346 | -1.9731 | -2.7158 | -3.1911 | 7.6382 | 7.5334 | 7.095 | 6.8398 | 6.5424 | 6.1816 | 5.5352 | 5.0933 | 4.7511 | 3.8389 | 2.6654 | 1.5269 | 0.78423 | 0.30889 | 4.1435 | 4.0524 | 3.6934 | 3.4468 | 3.1478 | 2.7829 | 2.1601 | 1.7017 | 1.3657 | 0.76496 | -1.1558 | -2.2112 | -2.6875 | -2.6956 | 7.6435 | 7.5524 | 7.1934 | 6.9468 | 6.6478 | 6.2829 | 5.6601 | 5.2017 | 4.8657 | 4.265 | 2.3442 | 1.2888 | 0.81248 | 0.80444 | 4.1324 | 4.0207 | 3.6347 | 3.3553 | 3.05 | 2.682 | 2.0202 | 1.5639 | 1.2991 | 0.76189 | -2.3394 | -8.6985 | -13.5727 | -16.4674 | 7.6324 | 7.5207 | 7.1347 | 6.8553 | 6.55 | 6.182 | 5.5202 | 5.0639 | 4.7991 | 4.2619 | 1.1606 | -5.1985 | -10.0727 | -12.9674 | 4.1763 | 4.0709 | 3.6979 | 3.4631 | 3.2163 | 2.9174 | 2.3373 | 1.9419 | 1.5127 | -0.12082 | -7.3435 | -12.9868 | -16.1323 | -14.9656 | 7.6763 | 7.5709 | 7.5709 | 6.9631 | 6.7163 | 6.4174 | 5.8373 | 5.4419 | 5.0127 | 3.3792 | -3.8435 | -9.4868 | -12.6323 | -11.4656 | 387494 | 394155 | LONGSIGHT | BREDBURY
| Leyland National | 17.906 | 17.5857 | 17.6161 | 17.4478 | 17.3554 | 17.2202 | 16.9956 | 16.7878 | 16.5761 | 16.2733 | 15.1463 | 14.0546 | 13.1025 | 12.5217 | 22.043 | 21.7227 | 21.7531 | 21.5848 | 21.4924 | 21.3572 | 21.1326 | 20.9248 | 20.7131 | 20.4103 | 19.2833 | 18.1916 | 17.2395 | 16.6587 | 18.136 | 18.0216 | 18.0169 | 17.8216 | 17.715 | 17.6376 | 17.441 | 17.2583 | 17.0703 | 16.8182 | 16.0271 | 15.2958 | 14.8349 | 14.5866 | 22.273 | 22.1586 | 22.1539 | 21.9586 | 21.852 | 21.7746 | 21.578 | 21.3953 | 21.2073 | 20.9552 | 20.1641 | 19.4328 | 18.9719 | 18.7236 | 17.9001 | 17.5789 | 17.6087 | 17.4414 | 17.3507 | 17.2357 | 17.0184 | 16.819 | 16.6203 | 16.3439 | 15.3578 | 14.6806 | 14.1931 | 13.9365 | 22.0371 | 21.7159 | 21.7457 | 21.5784 | 21.4877 | 21.3727 | 21.1554 | 20.956 | 20.7573 | 20.4809 | 19.4948 | 18.8176 | 18.3301 | 18.0735 | 17.9099 | 17.5982 | 17.6303 | 17.4586 | 17.3543 | 17.29 | 17.0625 | 16.8069 | 16.5079 | 16.281 | 14.441 | 12.3367 | 10.7745 | 10.0752 | 22.0469 | 21.7352 | 21.7673 | 21.5956 | 21.4913 | 21.427 | 21.1995 | 20.9439 | 20.6449 | 20.418 | 18.578 | 16.4737 | 14.9115 | 14.2122 | 17.9025 | 17.572 | 17.5856 | 17.3952 | 17.2716 | 17.1631 | 16.8804 | 16.5481 | 16.1588 | 15.8356 | 14.054 | 12.2322 | 11.0269 | 10.5983 | 22.0395 | 21.709 | 21.709 | 21.5322 | 21.4086 | 21.3001 | 21.0174 | 20.6851 | 20.2958 | 19.9726 | 18.191 | 16.3692 | 15.1639 | 14.7353 | 301973 | 525948 | STAINBURN & SIDDICK | HARKER
| Little Hulton | 2.9238 | 2.2012 | 1.7532 | 1.0475 | 0.25919 | -1.134 | -2.5435 | 2.4211 | 1.3485 | 0.37678 | -2.1935 | -4.0142 | -4.8386 | -5.4437 | 6.9738 | 6.2512 | 5.8032 | 5.0975 | 4.3092 | 2.916 | 1.5065 | 0.42114 | -0.65152 | -1.6232 | -4.1935 | -6.0142 | -6.8386 | -7.4437 | 3.2843 | 2.8971 | 2.4476 | 2.0041 | 1.5071 | 0.80415 | 0.080084 | 5.4738 | 4.8185 | 4.1957 | 2.1466 | 0.53304 | -0.48918 | -1.3169 | 7.3343 | 6.9471 | 6.4976 | 6.0541 | 5.5571 | 4.8542 | 4.1301 | 3.4738 | 2.8185 | 2.1957 | 0.14664 | -1.467 | -2.4892 | -3.3169 | 2.9419 | 2.2316 | 1.7959 | 1.1013 | 0.32923 | -1.0462 | -2.4382 | 2.5437 | 1.496 | 0.57819 | -1.7344 | -3.1961 | -3.8626 | -4.2532 | 6.9919 | 6.2816 | 5.8459 | 5.1513 | 4.3792 | 3.0038 | 1.6118 | 0.54367 | -0.50403 | -1.4218 | -3.7344 | -5.1961 | -5.8626 | -6.2532 | 2.9297 | 2.2105 | 1.7552 | 1.0237 | 0.24829 | -1.145 | -2.5871 | 2.3269 | 1.2739 | 0.36672 | -3.2596 | -9.8834 | -14.933 | -18.5907 | 6.9797 | 6.2605 | 5.8052 | 5.0737 | 4.2983 | 2.905 | 1.4629 | 0.32694 | -0.72611 | -1.6333 | -5.2596 | -11.8834 | -16.933 | -20.5907 | 2.9325 | 2.1799 | 1.7112 | 0.99263 | 0.24843 | -1.1028 | -2.5173 | 2.4289 | 1.2752 | -0.5867 | -7.9989 | -14.0403 | -17.5153 | -17.1982 | 6.9825 | 6.2299 | 6.2299 | 5.0426 | 4.2984 | 2.9472 | 1.5327 | 0.42888 | -0.7248 | -2.5867 | -9.9989 | -16.0403 | -19.5153 | -19.1982 | 372024 | 403826 | KEARSLEY LOCAL | KEARSLEY
| Little Salkeld | 6.4039 | 6.1701 | 6.0804 | 5.9234 | 5.71 | 5.5038 | 5.2114 | 4.9515 | 4.6653 | 4.3141 | 2.9461 | 2.1322 | 1.7463 | 1.7731 | 8.4039 | 8.1701 | 8.0804 | 7.9234 | 7.71 | 7.5038 | 7.2114 | 6.9515 | 6.6653 | 6.3141 | 4.9461 | 4.1322 | 3.7463 | 3.7731 | 6.4496 | 6.2792 | 6.1811 | 6.0074 | 5.8041 | 5.6091 | 5.3303 | 5.0777 | 4.8002 | 4.5226 | 3.7328 | 3.0228 | 2.3894 | 1.9061 | 8.4496 | 8.2792 | 8.1811 | 8.0074 | 7.8041 | 7.6091 | 7.3303 | 7.0777 | 6.8002 | 6.5226 | 5.7328 | 5.0228 | 4.3894 | 3.9061 | 6.4052 | 6.1794 | 6.098 | 5.997 | 5.7737 | 5.5587 | 5.3282 | 5.0815 | 4.8072 | 4.4739 | 3.244 | 2.6041 | 2.3178 | 2.4322 | 8.4052 | 8.1794 | 8.098 | 7.997 | 7.7737 | 7.5587 | 7.3282 | 7.0815 | 6.8072 | 6.4739 | 5.244 | 4.6041 | 4.3178 | 4.4322 | 6.4107 | 6.1659 | 6.0503 | 5.8739 | 5.6778 | 5.4028 | 5.0713 | 4.7923 | 4.5276 | 4.2373 | 2.5222 | 0.90609 | 0.030358 | -0.47266 | 8.4107 | 8.1659 | 8.0503 | 7.8739 | 7.6778 | 7.4028 | 7.0713 | 6.7923 | 6.5276 | 6.2373 | 4.5222 | 2.9061 | 2.0304 | 1.5273 | 6.4088 | 6.1407 | 6.0302 | 5.8643 | 5.6523 | 5.3817 | 5.0767 | 4.8332 | 4.5525 | 4.1591 | 2.243 | 1.0805 | 0.60527 | 0.65727 | 8.4088 | 8.1407 | 8.1407 | 7.8643 | 7.6523 | 7.3817 | 7.0767 | 6.8332 | 6.5525 | 6.1591 | 4.243 | 3.0805 | 2.6053 | 2.6573 | 356221 | 537513 | PENRITH & SHAP | HUTTON
| Littleborough | 3.1724 | 2.5208 | 2.3944 | 2.2765 | 1.9004 | 1.4215 | 0.93666 | 0.6197 | 0.012408 | -0.39703 | -1.9181 | -2.7533 | -2.9356 | -2.9248 | 6.6724 | 6.0208 | 5.8944 | 5.7765 | 5.4004 | 4.9215 | 4.4367 | 4.1197 | 3.5124 | 3.103 | 1.5819 | 0.74675 | 0.56436 | 0.57522 | 3.4255 | 3.0009 | 2.8091 | 2.6535 | 2.2785 | 1.8189 | 1.3484 | 1.0389 | 0.43714 | 0.075386 | -1.0898 | -2.0232 | -2.5496 | -2.989 | 6.9255 | 6.5009 | 6.3091 | 6.1535 | 5.7785 | 5.3189 | 4.8484 | 4.5389 | 3.9371 | 3.5754 | 2.4102 | 1.4768 | 0.95044 | 0.511 | 3.1782 | 2.534 | 2.4127 | 2.3 | 1.9325 | 1.4639 | 0.98926 | 0.68013 | 0.089124 | -0.28723 | -1.7172 | -2.4973 | -2.6775 | -2.6763 | 6.6782 | 6.034 | 5.9127 | 5.8 | 5.4325 | 4.9639 | 4.4893 | 4.1801 | 3.5891 | 3.2128 | 1.7828 | 1.0027 | 0.82247 | 0.82372 | 3.1898 | 2.5619 | 2.4676 | 2.3863 | 2.0703 | 1.6658 | 1.2546 | 1.0197 | 0.54905 | 0.32443 | -1.3695 | -5.6483 | -9.1764 | -11.6291 | 6.6898 | 6.0619 | 5.9676 | 5.8863 | 5.5703 | 5.1658 | 4.7546 | 4.5197 | 4.049 | 3.8244 | 2.1305 | -2.1483 | -5.6764 | -8.1291 | 3.2108 | 2.5735 | 2.4882 | 2.4474 | 2.1708 | 1.8269 | 1.4784 | 1.3148 | 0.80713 | -0.0084593 | -4.5165 | -8.6312 | -10.9113 | -10.3579 | 6.7108 | 6.0735 | 6.0735 | 5.9474 | 5.6708 | 5.3269 | 4.9784 | 4.8148 | 4.3071 | 3.4915 | -1.0165 | -5.1312 | -7.4113 | -6.8579 | 393221 | 416124 | BELFIELD | ROCHDALE
| Longford Bridge | 10.238 | 9.3093 | 8.8406 | 8.6622 | 8.3763 | 8.052 | 7.5977 | 7.3579 | 6.9729 | 6.5037 | 4.7724 | 3.6865 | 3.2066 | 3.1929 | 14.875 | 13.9463 | 13.4776 | 13.2992 | 13.0133 | 12.689 | 12.2347 | 11.9949 | 11.6099 | 11.1407 | 9.4094 | 8.3235 | 7.8436 | 7.8299 | 10.6166 | 10.1221 | 9.6987 | 9.5317 | 9.2702 | 8.9701 | 8.571 | 8.2985 | 7.952 | 7.5809 | 6.4634 | 5.4285 | 4.6693 | 4.0985 | 15.2536 | 14.7591 | 14.3357 | 14.1687 | 13.9072 | 13.6071 | 13.208 | 12.9355 | 12.589 | 12.2179 | 11.1004 | 10.0655 | 9.3063 | 8.7355 | 10.2499 | 9.3019 | 8.8762 | 8.7163 | 8.4466 | 8.103 | 7.7255 | 7.4025 | 7.0408 | 6.6653 | 5.1104 | 4.2335 | 3.8211 | 3.7924 | 14.8869 | 13.9389 | 13.5132 | 13.3533 | 13.0836 | 12.74 | 12.3625 | 12.0395 | 11.6778 | 11.3023 | 9.7474 | 8.8705 | 8.4581 | 8.4294 | 10.2386 | 9.3178 | 8.833 | 8.6438 | 8.3525 | 8.0052 | 7.4686 | 7.1263 | 6.7242 | 6.3178 | 3.7781 | -1.5875 | -5.6408 | -8.4815 | 14.8756 | 13.9548 | 13.47 | 13.2808 | 12.9895 | 12.6422 | 12.1056 | 11.7633 | 11.3612 | 10.9548 | 8.4151 | 3.0495 | -1.0038 | -3.8445 | 10.2625 | 9.3356 | 8.8868 | 8.7314 | 8.4351 | 8.0924 | 7.6144 | 7.3539 | 6.8848 | 5.614 | -0.35492 | -5.1695 | -7.8577 | -7.1947 | 14.8995 | 13.9726 | 13.9726 | 13.3684 | 13.0721 | 12.7294 | 12.2514 | 11.9909 | 11.5218 | 10.251 | 4.2821 | -0.53254 | -3.2207 | -2.5577 | 380056 | 395083 | STRETFORD | SOUTH MANCHESTER
| Longridge | 10.7934 | 10.425 | 10.0771 | 9.6721 | 9.5042 | 9.1198 | 8.6971 | 8.3001 | 7.9346 | 7.2556 | 4.7801 | 3.1939 | 2.2978 | 2.2849 | 14.9304 | 14.562 | 14.2141 | 13.8091 | 13.6412 | 13.2568 | 12.8341 | 12.4371 | 12.0716 | 11.3926 | 8.9171 | 7.3309 | 6.4348 | 6.4219 | 10.8918 | 10.6168 | 10.2441 | 9.8813 | 9.7367 | 9.3696 | 8.9568 | 8.5625 | 8.1891 | 7.6797 | 6.3297 | 4.8368 | 3.4983 | 2.6355 | 15.0288 | 14.7538 | 14.3811 | 14.0183 | 13.8737 | 13.5066 | 13.0938 | 12.6995 | 12.3261 | 11.8167 | 10.4667 | 8.9738 | 7.6353 | 6.7725 | 10.8014 | 10.4501 | 10.1228 | 9.7434 | 9.596 | 9.2355 | 8.8371 | 8.4638 | 8.12 | 7.5115 | 5.294 | 3.9643 | 3.1521 | 3.1696 | 14.9384 | 14.5871 | 14.2598 | 13.8804 | 13.733 | 13.3725 | 12.9741 | 12.6008 | 12.257 | 11.6485 | 9.431 | 8.1013 | 7.2891 | 7.3066 | 10.7982 | 10.4043 | 10.0279 | 9.5905 | 9.3678 | 8.8919 | 8.3226 | 7.7692 | 7.3226 | 6.7329 | 4.1869 | 0.46832 | -2.0514 | -3.7736 | 14.9352 | 14.5413 | 14.1649 | 13.7275 | 13.5048 | 13.0289 | 12.4596 | 11.9062 | 11.4596 | 10.8699 | 8.3239 | 4.6053 | 2.0856 | 0.3634 | 10.8168 | 10.4315 | 10.0844 | 9.6795 | 9.4617 | 9.023 | 8.5301 | 8.07 | 7.6708 | 6.6783 | 2.3038 | -0.83617 | -2.5509 | -2.2142 | 14.9538 | 14.5685 | 14.5685 | 13.8165 | 13.5987 | 13.16 | 12.6671 | 12.207 | 11.8078 | 10.8153 | 6.4408 | 3.3008 | 1.5861 | 1.9228 | 360581 | 437001 | PRESTON EAST | PENWORTHAM
| Longsight | 5.4901 | 4.8456 | 4.874 | 4.4434 | 4.3208 | 3.9026 | 3.4868 | 3.1737 | 2.6844 | 2.2243 | 0.34681 | -0.81844 | -1.4009 | -1.4685 | 9.6271 | 8.9826 | 9.011 | 8.5804 | 8.4578 | 8.0396 | 7.6238 | 7.3107 | 6.8214 | 6.3613 | 4.4838 | 3.3186 | 2.7361 | 2.6685 | 5.7671 | 5.3589 | 5.2713 | 4.7522 | 4.5536 | 4.1322 | 3.6545 | 3.2646 | 2.7306 | 2.237 | 0.89621 | -0.21994 | -1.0216 | -1.5219 | 9.9041 | 9.4959 | 9.4083 | 8.8892 | 8.6906 | 8.2692 | 7.7915 | 7.4016 | 6.8676 | 6.374 | 5.0332 | 3.9171 | 3.1154 | 2.6151 | 5.5209 | 4.8908 | 4.912 | 4.483 | 4.3705 | 3.9669 | 3.5657 | 3.2657 | 2.7969 | 2.3724 | 0.58218 | -0.49791 | -1.0468 | -1.086 | 9.6579 | 9.0278 | 9.049 | 8.62 | 8.5075 | 8.1039 | 7.7027 | 7.4027 | 6.9339 | 6.5094 | 4.7192 | 3.6391 | 3.0902 | 3.051 | 5.5057 | 4.8774 | 4.9226 | 4.5023 | 4.3987 | 3.9937 | 3.5532 | 3.21 | 2.7345 | 2.334 | 0.15897 | -4.9765 | -9.0399 | -11.7329 | 9.6427 | 9.0144 | 9.0596 | 8.6393 | 8.5357 | 8.1307 | 7.6902 | 7.347 | 6.8715 | 6.471 | 4.296 | -0.8395 | -4.9029 | -7.5959 | 5.553 | 4.9478 | 5.0185 | 4.6298 | 4.5562 | 4.2055 | 3.8351 | 3.5683 | 3.0828 | 2.0528 | -3.3648 | -8.1702 | -10.9398 | -10.1939 | 9.69 | 9.0848 | 9.0848 | 8.7668 | 8.6932 | 8.3425 | 7.9721 | 7.7053 | 7.2198 | 6.1898 | 0.7722 | -4.0332 | -6.8028 | -6.0569 | 385535 | 396037 | LONGSIGHT | BREDBURY
| Lostock | 10.0069 | 8.8719 | 8.663 | 8.2611 | 8.0706 | 7.3628 | 6.9066 | 6.3879 | 5.937 | 5.2443 | 3.3879 | 2.6313 | 2.4752 | 2.5944 | 16.0069 | 14.8719 | 14.663 | 14.2611 | 14.0706 | 13.3628 | 12.9066 | 12.3879 | 11.937 | 11.2443 | 9.3879 | 8.6313 | 8.4752 | 8.5944 | 10.7328 | 10.2486 | 10.0228 | 9.5241 | 9.3489 | 8.7182 | 8.3175 | 7.8542 | 7.4424 | 6.8512 | 5.4911 | 4.6707 | 4.0374 | 3.8976 | 16.7328 | 16.2486 | 16.0228 | 15.5241 | 15.3489 | 14.7182 | 14.3175 | 13.8542 | 13.4424 | 12.8512 | 11.4911 | 10.6707 | 10.0374 | 9.8976 | 10.0152 | 8.8883 | 8.6667 | 8.2853 | 8.1026 | 7.4058 | 6.9585 | 6.448 | 6.0136 | 5.3712 | 3.7184 | 3.2213 | 3.1632 | 3.5358 | 16.0152 | 14.8883 | 14.6667 | 14.2853 | 14.1026 | 13.4058 | 12.9585 | 12.448 | 12.0136 | 11.3712 | 9.7184 | 9.2213 | 9.1632 | 9.5358 | 10.0384 | 8.9425 | 8.7687 | 8.4855 | 8.4144 | 7.8259 | 7.5179 | 7.1021 | 6.8908 | 6.2951 | 3.8386 | -0.28278 | -3.5868 | -5.7252 | 16.0384 | 14.9425 | 14.7687 | 14.4855 | 14.4144 | 13.8259 | 13.5179 | 13.1021 | 12.8908 | 12.2951 | 9.8386 | 5.7172 | 2.4132 | 0.27483 | 10.0033 | 8.848 | 8.6435 | 8.366 | 8.3124 | 7.7886 | 7.4569 | 7.1707 | 6.731 | 5.4507 | 0.67271 | -2.9851 | -5.4448 | -4.4989 | 16.0033 | 14.848 | 14.848 | 14.366 | 14.3124 | 13.7886 | 13.4569 | 13.1707 | 12.731 | 11.4507 | 6.6727 | 3.0149 | 0.55524 | 1.5011 | 365293 | 409079 | WESTHOUGHTON | KEARSLEY
| Lower Darwen | 9.7504 | 9.4921 | 9.4778 | 9.3411 | 9.4109 | 9.2337 | 9.0912 | 9.0019 | 8.9757 | 8.7694 | 8.3919 | 8.1659 | 7.9873 | 8.0186 | 16.7504 | 16.4921 | 16.4778 | 16.3411 | 16.4109 | 16.2337 | 16.0912 | 16.0019 | 15.9757 | 15.7694 | 15.3919 | 15.1659 | 14.9873 | 15.0186 | 10.1165 | 10.1551 | 10.0296 | 9.8245 | 9.8446 | 9.6622 | 9.5022 | 9.3865 | 9.3249 | 9.0961 | 8.7874 | 8.5725 | 8.3343 | 8.4044 | 17.1165 | 17.1551 | 17.0296 | 16.8245 | 16.8446 | 16.6622 | 16.5022 | 16.3865 | 16.3249 | 16.0961 | 15.7874 | 15.5725 | 15.3343 | 15.4044 | 9.7523 | 9.4963 | 9.4846 | 9.3512 | 9.4235 | 9.25 | 9.1111 | 9.0251 | 9.0034 | 8.809 | 8.4935 | 8.3923 | 8.2753 | 8.4155 | 16.7523 | 16.4963 | 16.4846 | 16.3512 | 16.4235 | 16.25 | 16.1111 | 16.0251 | 16.0034 | 15.809 | 15.4935 | 15.3923 | 15.2753 | 15.4155 | 9.775 | 9.5414 | 9.5521 | 9.4426 | 9.537 | 9.3835 | 9.2606 | 9.1873 | 9.1789 | 9.0066 | 8.5021 | 7.5592 | 6.7814 | 6.5782 | 16.775 | 16.5414 | 16.5521 | 16.4426 | 16.537 | 16.3835 | 16.2606 | 16.1873 | 16.1789 | 16.0066 | 15.5021 | 14.5592 | 13.7814 | 13.5782 | 9.7594 | 9.5134 | 9.5235 | 9.417 | 9.5145 | 9.3631 | 9.2366 | 9.1595 | 9.1311 | 8.7927 | 7.6595 | 6.8271 | 6.3708 | 6.8369 | 16.7594 | 16.5134 | 16.5134 | 16.417 | 16.5145 | 16.3631 | 16.2366 | 16.1595 | 16.1311 | 15.7927 | 14.6595 | 13.8271 | 13.3708 | 13.8369 | 369695 | 424981 | LOWER DARWEN | ROCHDALE
| Lyons Rd | 11.9222 | 10.8457 | 10.4304 | 10.5052 | 10.5537 | 10.3389 | 10.2149 | 10.0454 | 9.8741 | 9.652 | 5.4875 | -10.8499 | -12.0212 | -11.2961 | 16.5592 | 15.4827 | 15.0674 | 15.1422 | 15.1907 | 14.9759 | 14.8519 | 14.6824 | 14.5111 | 14.289 | 10.1245 | -6.2129 | -7.3842 | -6.6591 | 12.6215 | 12.1801 | 11.8143 | 11.8351 | 11.8356 | 11.631 | 11.5014 | 11.2843 | 11.0986 | 10.9537 | 10.3658 | 9.6747 | 8.9072 | 8.5906 | 17.2585 | 16.8171 | 16.4513 | 16.4721 | 16.4726 | 16.268 | 16.1384 | 15.9213 | 15.7356 | 15.5907 | 15.0028 | 14.3117 | 13.5442 | 13.2276 | 11.9266 | 10.8537 | 10.4443 | 10.4909 | 10.5398 | 10.3144 | 10.2038 | 10.034 | 9.8631 | 9.6415 | 5.6031 | -10.3661 | -11.3493 | -10.2903 | 16.5636 | 15.4907 | 15.0813 | 15.1279 | 15.1768 | 14.9514 | 14.8408 | 14.671 | 14.5001 | 14.2785 | 10.2401 | -5.7291 | -6.7123 | -5.6533 | 11.9418 | 10.886 | 10.4914 | 10.5865 | 10.6518 | 10.4444 | 10.3144 | 10.1265 | 9.925 | 9.6679 | -10.7397 | -12.0483 | -13.9409 | -13.1336 | 16.5788 | 15.523 | 15.1284 | 15.2235 | 15.2888 | 15.0814 | 14.9514 | 14.7635 | 14.562 | 14.3049 | -6.1027 | -7.4113 | -9.3039 | -8.4966 | 11.9255 | 10.8444 | 10.4382 | 10.4952 | 10.5486 | 10.3126 | 10.1409 | 9.8986 | 9.6331 | 5.2998 | 3.7489 | 1.9674 | 0.80308 | 1.2846 | 16.5625 | 15.4814 | 15.4814 | 15.1322 | 15.1856 | 14.9496 | 14.7779 | 14.5356 | 14.2701 | 9.9368 | 8.3859 | 6.6044 | 5.4401 | 5.9216 | 378253 | 397241 | BARTON | CARRINGTON
| Marple | 1.048 | 0.97407 | 0.88592 | 0.78556 | 0.69729 | 0.58552 | 0.37274 | 0.30003 | 0.19356 | 0.010675 | -0.52774 | -0.79106 | -0.87337 | -0.78617 | 0.04804 | -0.025933 | -0.11408 | -0.21444 | -0.30271 | -0.41448 | -0.62726 | -0.69997 | -0.80644 | -0.98932 | -1.5277 | -1.7911 | -1.8734 | -1.7862 | 1.0821 | 1.0284 | 0.92245 | 0.81283 | 0.74005 | 0.63425 | 0.42908 | 0.3593 | 0.25298 | 0.089459 | -0.28912 | -0.56299 | -0.7489 | -0.82295 | 0.082092 | 0.028422 | -0.077552 | -0.18717 | -0.25995 | -0.36575 | -0.57092 | -0.6407 | -0.74702 | -0.91054 | -1.2891 | -1.563 | -1.7489 | -1.823 | 1.0482 | 0.99215 | 0.89791 | 0.81139 | 0.71862 | 0.61198 | 0.40576 | 0.33697 | 0.23733 | 0.071371 | -0.41593 | -0.64735 | -0.71919 | -0.63803 | 0.048189 | -0.0078475 | -0.10209 | -0.18861 | -0.28138 | -0.38802 | -0.59424 | -0.66303 | -0.76267 | -0.92863 | -1.4159 | -1.6473 | -1.7192 | -1.638 | 1.0528 | 0.98307 | 0.90296 | 0.80937 | 0.73379 | 0.63314 | 0.42638 | 0.35927 | 0.27788 | 0.14132 | -0.67432 | -2.575 | -4.1303 | -5.1151 | 0.052778 | -0.016934 | -0.097041 | -0.19063 | -0.26621 | -0.36686 | -0.57362 | -0.64073 | -0.72212 | -0.85868 | -1.6743 | -3.575 | -5.1303 | -6.1151 | 1.0539 | 0.97929 | 0.89584 | 0.81588 | 0.75016 | 0.66852 | 0.48465 | 0.44349 | 0.32347 | -0.15412 | -2.2704 | -3.984 | -5.0153 | -4.6637 | 0.053911 | -0.020709 | -0.020709 | -0.18412 | -0.24984 | -0.33148 | -0.51535 | -0.55651 | -0.67653 | -1.1541 | -3.2704 | -4.984 | -6.0153 | -5.6637 | 395671 | 388643 | HAZEL GROVE | BREDBURY
| Marton | 9.6889 | 9.4196 | 9.3065 | 9.0892 | 8.8131 | 8.519 | 8.1795 | 7.8219 | 7.4596 | 7.093 | 5.491 | 4.6699 | 4.5637 | 4.7849 | 14.2889 | 14.0196 | 13.9065 | 13.6892 | 13.4131 | 13.119 | 12.7795 | 12.4219 | 12.0596 | 11.693 | 10.091 | 9.2699 | 9.1637 | 9.3849 | 9.9045 | 9.808 | 9.5933 | 9.327 | 9.0337 | 8.7395 | 8.3919 | 8.0129 | 7.6117 | 7.2362 | 6.452 | 5.9743 | 5.6489 | 5.5121 | 14.5045 | 14.408 | 14.1933 | 13.927 | 13.6337 | 13.3395 | 12.9919 | 12.6129 | 12.2117 | 11.8362 | 11.052 | 10.5743 | 10.2489 | 10.1121 | 9.7064 | 9.4373 | 9.3576 | 9.142 | 8.894 | 8.5977 | 8.2745 | 7.9375 | 7.5814 | 7.2159 | 5.7743 | 5.0929 | 5.0372 | 5.2905 | 14.3064 | 14.0373 | 13.9576 | 13.742 | 13.494 | 13.1977 | 12.8745 | 12.5375 | 12.1814 | 11.8159 | 10.3743 | 9.6929 | 9.6372 | 9.8905 | 9.7132 | 9.4719 | 9.3914 | 9.2095 | 8.9745 | 8.7219 | 8.4239 | 8.1134 | 7.792 | 7.4524 | 5.3092 | 1.2855 | -1.8725 | -4.4508 | 14.3132 | 14.0719 | 13.9914 | 13.8095 | 13.5745 | 13.3219 | 13.0239 | 12.7134 | 12.392 | 12.0524 | 9.9092 | 5.8855 | 2.7275 | 0.14918 | 9.6729 | 9.3625 | 9.2913 | 9.141 | 8.9386 | 8.7357 | 8.481 | 8.1957 | 7.8049 | 6.8411 | 2.3204 | -1.5227 | -3.9316 | -3.4192 | 14.2729 | 13.9625 | 13.9625 | 13.741 | 13.5386 | 13.3357 | 13.081 | 12.7957 | 12.4049 | 11.4411 | 6.9204 | 3.0773 | 0.66842 | 1.1808 | 333341 | 433485 | BLACKPOOL | PENWORTHAM
| Maryport | 13.7409 | 13.5146 | 13.2178 | 12.7535 | 12.4189 | 11.8881 | 11.2981 | 10.7318 | 10.2076 | 9.4909 | 6.8864 | 5.6015 | 5.3883 | 5.8019 | 17.7409 | 17.5146 | 17.2178 | 16.7535 | 16.4189 | 15.8881 | 15.2981 | 14.7318 | 14.2076 | 13.4909 | 10.8864 | 9.6015 | 9.3883 | 9.8019 | 13.7879 | 13.603 | 13.2811 | 12.9321 | 12.7237 | 12.3217 | 11.8672 | 11.4343 | 10.9902 | 10.5174 | 9.0757 | 8.0752 | 7.5059 | 7.1688 | 17.7879 | 17.603 | 17.2811 | 16.9321 | 16.7237 | 16.3217 | 15.8672 | 15.4343 | 14.9902 | 14.5174 | 13.0757 | 12.0752 | 11.5059 | 11.1688 | 13.7471 | 13.5335 | 13.2523 | 12.8108 | 12.4982 | 11.9933 | 11.4298 | 10.8887 | 10.3912 | 9.7439 | 7.3982 | 6.2965 | 6.1332 | 6.5336 | 17.7471 | 17.5335 | 17.2523 | 16.8108 | 16.4982 | 15.9933 | 15.4298 | 14.8887 | 14.3912 | 13.7439 | 11.3982 | 10.2965 | 10.1332 | 10.5336 | 13.7439 | 13.4886 | 13.1623 | 12.6906 | 12.3474 | 11.782 | 11.1199 | 10.4676 | 9.9329 | 9.3584 | 6.6337 | 2.0604 | -0.84101 | -3.0987 | 17.7439 | 17.4886 | 17.1623 | 16.6906 | 16.3474 | 15.782 | 15.1199 | 14.4676 | 13.9329 | 13.3584 | 10.6337 | 6.0604 | 3.159 | 0.90128 | 13.7647 | 13.4848 | 13.1393 | 12.6666 | 12.3437 | 11.8416 | 11.2723 | 10.7537 | 10.3077 | 9.1679 | 3.8585 | 0.19759 | -1.593 | -0.86213 | 17.7647 | 17.4848 | 17.4848 | 16.6666 | 16.3437 | 15.8416 | 15.2723 | 14.7537 | 14.3077 | 13.1679 | 7.8585 | 4.1976 | 2.407 | 3.1379 | 303716 | 535313 | STAINBURN & SIDDICK | HARKER
| Medipark | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 23.3775 | 23.3775 | 23.3775 | 23.3775 | 23.3775 | 23.3775 | 23.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 28.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 34.3775 | 380477 | 387810 | ALTRINCHAM | CARRINGTON
| Melling | 1.4263 | 1.3423 | 1.2563 | 1.1459 | 1.0715 | 0.96109 | 0.82399 | 0.6838 | 0.54261 | 0.34371 | -0.29198 | -0.57114 | -0.64618 | -0.5172 | 3.4263 | 3.3423 | 3.2563 | 3.1459 | 3.0715 | 2.9611 | 2.824 | 2.6838 | 2.5426 | 2.3437 | 1.708 | 1.4289 | 1.3538 | 1.4828 | 1.4497 | 1.3875 | 1.2946 | 1.2013 | 1.1485 | 1.0424 | 0.92019 | 0.80215 | 0.67754 | 0.53395 | 0.14892 | -0.21542 | -0.49094 | -0.64095 | 3.4497 | 3.3875 | 3.2946 | 3.2013 | 3.1485 | 3.0424 | 2.9202 | 2.8021 | 2.6775 | 2.5339 | 2.1489 | 1.7846 | 1.5091 | 1.3591 | 1.4284 | 1.3483 | 1.2666 | 1.1559 | 1.0895 | 0.98359 | 0.84739 | 0.71496 | 0.58112 | 0.39799 | -0.17692 | -0.42647 | -0.51396 | -0.39962 | 3.4284 | 3.3483 | 3.2666 | 3.1559 | 3.0895 | 2.9836 | 2.8474 | 2.715 | 2.5811 | 2.398 | 1.8231 | 1.5735 | 1.486 | 1.6004 | 1.4291 | 1.3427 | 1.2571 | 1.1501 | 1.0741 | 0.95613 | 0.81174 | 0.67322 | 0.55322 | 0.42014 | -0.10251 | -0.58127 | -0.77556 | -0.86272 | 3.4291 | 3.3427 | 3.2571 | 3.1501 | 3.0741 | 2.9561 | 2.8117 | 2.6732 | 2.5532 | 2.4201 | 1.8975 | 1.4187 | 1.2244 | 1.1373 | 1.4096 | 1.3002 | 1.2158 | 1.1149 | 1.0412 | 0.9374 | 0.8096 | 0.69135 | 0.58983 | 0.40812 | -0.33272 | -0.7079 | -0.79037 | -0.60235 | 3.4096 | 3.3002 | 3.3002 | 3.1149 | 3.0412 | 2.9374 | 2.8096 | 2.6914 | 2.5898 | 2.4081 | 1.6673 | 1.2921 | 1.2096 | 1.3977 | 360144 | 471643 | KENDAL (PARKSIDE RD) | HUTTON
| Mereside | 7.467 | 7.2903 | 7.2185 | 7.0738 | 6.9414 | 6.7939 | 6.5976 | 6.3941 | 6.2252 | 5.9913 | 5.2264 | 4.7684 | 4.6114 | 4.5993 | 18.727 | 18.5503 | 18.4785 | 18.3338 | 18.2014 | 18.0539 | 17.8576 | 17.6541 | 17.4852 | 17.2513 | 16.4864 | 16.0284 | 15.8714 | 15.8593 | 7.6344 | 7.5948 | 7.452 | 7.2794 | 7.1372 | 6.9965 | 6.8021 | 6.5954 | 6.4104 | 6.1836 | 5.7084 | 5.3655 | 5.1781 | 5.0928 | 18.8944 | 18.8548 | 18.712 | 18.5394 | 18.3972 | 18.2565 | 18.0621 | 17.8554 | 17.6704 | 17.4436 | 16.9684 | 16.6255 | 16.4381 | 16.3528 | 7.4735 | 7.305 | 7.2426 | 7.1074 | 6.985 | 6.8475 | 6.6619 | 6.4691 | 6.312 | 6.1038 | 5.4179 | 5.0002 | 4.855 | 4.9033 | 18.7335 | 18.565 | 18.5026 | 18.3674 | 18.245 | 18.1075 | 17.9219 | 17.7291 | 17.572 | 17.3638 | 16.6779 | 16.2602 | 16.115 | 16.1633 | 7.4796 | 7.3125 | 7.2484 | 7.1112 | 6.9823 | 6.8297 | 6.6148 | 6.3852 | 6.1995 | 5.9706 | 5.015 | 3.2324 | 1.901 | 0.8432 | 18.7396 | 18.5725 | 18.5084 | 18.3712 | 18.2423 | 18.0897 | 17.8748 | 17.6452 | 17.4595 | 17.2306 | 16.275 | 14.4924 | 13.161 | 12.1032 | 7.4687 | 7.2859 | 7.225 | 7.1002 | 6.9844 | 6.8534 | 6.6613 | 6.4632 | 6.2933 | 5.8648 | 3.9892 | 2.3362 | 1.4364 | 1.6941 | 18.7287 | 18.5459 | 18.5459 | 18.3602 | 18.2444 | 18.1134 | 17.9213 | 17.7232 | 17.5533 | 17.1248 | 15.2492 | 13.5962 | 12.6964 | 12.9541 | 334431 | 434843 | PEEL | PENWORTHAM
| Middleton Junction | 6.6467 | 5.7185 | 5.544 | 5.1946 | 5.0019 | 4.5988 | 4.3444 | 3.9408 | 3.4309 | 2.955 | 1.1492 | 0.05432 | -0.42549 | -0.56857 | 11.1467 | 10.2185 | 10.044 | 9.6946 | 9.5019 | 9.0988 | 8.8444 | 8.4408 | 7.9309 | 7.455 | 5.6492 | 4.5543 | 4.0745 | 3.9314 | 7.0476 | 6.5016 | 6.3045 | 5.9343 | 5.7424 | 5.3631 | 5.1191 | 4.7344 | 4.2455 | 3.8507 | 2.472 | 1.3778 | 0.61848 | 0.071175 | 11.5476 | 11.0016 | 10.8045 | 10.4343 | 10.2424 | 9.8631 | 9.6191 | 9.2344 | 8.7455 | 8.3507 | 6.972 | 5.8778 | 5.1185 | 4.5712 | 6.6545 | 5.7498 | 5.5781 | 5.24 | 5.0608 | 4.6727 | 4.4313 | 4.0545 | 3.5671 | 3.1357 | 1.5117 | 0.5998 | 0.19784 | 0.12877 | 11.1545 | 10.2498 | 10.0781 | 9.74 | 9.5608 | 9.1727 | 8.9313 | 8.5545 | 8.0671 | 7.6357 | 6.0117 | 5.0998 | 4.6978 | 4.6288 | 6.6621 | 5.7528 | 5.5972 | 5.2697 | 5.1152 | 4.7495 | 4.5059 | 4.1288 | 3.7022 | 3.3442 | 0.88098 | -4.3068 | -8.4576 | -11.6033 | 11.1621 | 10.2528 | 10.0972 | 9.7697 | 9.6152 | 9.2495 | 9.0059 | 8.6288 | 8.2022 | 7.8442 | 5.381 | 0.1932 | -3.9576 | -7.1033 | 6.6966 | 5.7795 | 5.6302 | 5.3586 | 5.212 | 4.8628 | 4.6689 | 4.329 | 3.773 | 2.5861 | -3.0636 | -7.7822 | -10.7757 | -10.3774 | 11.1966 | 10.2795 | 10.2795 | 9.8586 | 9.712 | 9.3628 | 9.1689 | 8.829 | 8.273 | 7.0861 | 1.4364 | -3.2822 | -6.2757 | -5.8774 | 388606 | 405292 | CHADDERTON | WHITEGATE
| Midway | 8.9041 | 8.6931 | 8.5919 | 8.3864 | 8.2357 | 7.952 | 7.667 | 7.5058 | 7.1929 | 6.861 | 5.6249 | 5.0079 | 4.8295 | 5.1447 | 11.4041 | 11.1931 | 11.0919 | 10.8864 | 10.7357 | 10.452 | 10.167 | 10.0058 | 9.6929 | 9.361 | 8.1249 | 7.5079 | 7.3295 | 7.6447 | 8.9691 | 8.8305 | 8.7111 | 8.5481 | 8.4391 | 8.2222 | 7.9834 | 7.8142 | 7.5257 | 7.2398 | 6.7448 | 6.1256 | 5.653 | 5.4326 | 11.4691 | 11.3305 | 11.2111 | 11.0481 | 10.9391 | 10.7222 | 10.4834 | 10.3142 | 10.0257 | 9.7398 | 9.2448 | 8.6256 | 8.153 | 7.9326 | 8.9089 | 8.7008 | 8.6156 | 8.417 | 8.2759 | 8.0041 | 7.7301 | 7.576 | 7.2811 | 6.9887 | 5.8979 | 5.3991 | 5.2917 | 5.619 | 11.4089 | 11.2008 | 11.1156 | 10.917 | 10.7759 | 10.5041 | 10.2301 | 10.076 | 9.7811 | 9.4887 | 8.3979 | 7.8991 | 7.7917 | 8.119 | 8.9081 | 8.6866 | 8.5764 | 8.3716 | 8.2082 | 7.9003 | 7.573 | 7.3644 | 7.0635 | 6.8287 | 5.6877 | 4.2252 | 3.442 | 2.944 | 11.4081 | 11.1866 | 11.0764 | 10.8716 | 10.7082 | 10.4003 | 10.073 | 9.8644 | 9.5635 | 9.3287 | 8.1877 | 6.7252 | 5.942 | 5.444 | 8.8959 | 8.6339 | 8.5256 | 8.3093 | 8.1387 | 7.8459 | 7.5524 | 7.404 | 7.1394 | 6.7509 | 4.9075 | 3.7754 | 3.3491 | 3.7776 | 11.3959 | 11.1339 | 11.1339 | 10.8093 | 10.6387 | 10.3459 | 10.0524 | 9.904 | 9.6394 | 9.2509 | 7.4075 | 6.2754 | 5.8491 | 6.2776 | 304525 | 501993 | EGREMONT | HARKER
| Milnrow | 11.1542 | 11.0371 | 10.846 | 10.6855 | 10.3868 | 10.1422 | 9.7171 | 9.3789 | 9.1289 | 8.6962 | 7.2015 | 6.2412 | 5.7698 | 5.6487 | 15.7942 | 15.6771 | 15.486 | 15.3255 | 15.0268 | 14.7822 | 14.3571 | 14.0189 | 13.7689 | 13.3362 | 11.8415 | 10.8812 | 10.4098 | 10.2887 | 11.2501 | 11.2098 | 10.9455 | 10.7634 | 10.4643 | 10.2279 | 9.8075 | 9.4725 | 9.2248 | 8.8569 | 7.7575 | 6.8104 | 6.1258 | 5.6352 | 15.8901 | 15.8498 | 15.5855 | 15.4034 | 15.1043 | 14.8679 | 14.4475 | 14.1125 | 13.8648 | 13.4969 | 12.3975 | 11.4504 | 10.7658 | 10.2752 | 11.1657 | 11.0602 | 10.8823 | 10.7313 | 10.4473 | 10.2168 | 9.808 | 9.4847 | 9.2538 | 8.8629 | 7.532 | 6.7238 | 6.3252 | 6.2502 | 15.8057 | 15.7002 | 15.5223 | 15.3713 | 15.0873 | 14.8568 | 14.448 | 14.1247 | 13.8938 | 13.5029 | 12.172 | 11.3638 | 10.9652 | 10.8902 | 11.1601 | 11.0502 | 10.8674 | 10.7108 | 10.4322 | 10.2021 | 9.7598 | 9.4022 | 9.1827 | 8.8418 | 6.7784 | 2.3919 | -1.079 | -3.4611 | 15.8001 | 15.6902 | 15.5074 | 15.3508 | 15.0722 | 14.8421 | 14.3998 | 14.0422 | 13.8227 | 13.4818 | 11.4184 | 7.0319 | 3.561 | 1.1789 | 11.1921 | 11.0931 | 10.924 | 10.7953 | 10.5269 | 10.3255 | 9.9323 | 9.6281 | 9.338 | 8.2819 | 3.4432 | -0.53672 | -2.8925 | -2.4309 | 15.8321 | 15.7331 | 15.7331 | 15.4353 | 15.1669 | 14.9655 | 14.5723 | 14.2681 | 13.978 | 12.9219 | 8.0832 | 4.1033 | 1.7475 | 2.2091 | 392351 | 413056 | CASTLETON | ROCHDALE
| Mintsfeet | 1.8276 | 1.1086 | 1.2 | 0.79562 | 0.78336 | 0.29962 | -0.12917 | -0.27634 | -1.159 | -1.6727 | -4.2273 | -9.5387 | -13.0862 | -12.8987 | 7.8276 | 7.1086 | 7.2 | 6.7956 | 6.7834 | 6.2996 | 5.8708 | 5.7237 | 4.841 | 4.3273 | 1.7727 | -3.5387 | -7.0862 | -6.8987 | 2.1799 | 1.6536 | 1.6271 | 1.1806 | 1.1042 | 0.65431 | 0.20114 | -0.2809 | -0.78645 | -1.3348 | -2.8641 | -4.0066 | -4.9405 | -5.6407 | 8.1799 | 7.6536 | 7.6271 | 7.1806 | 7.1042 | 6.6543 | 6.2011 | 5.7191 | 5.2136 | 4.6652 | 3.1359 | 1.9934 | 1.0595 | 0.35931 | 1.9242 | 1.145 | 1.2553 | 0.87208 | 0.87307 | 0.41113 | 0.00098967 | -0.20537 | -1.0865 | -1.5203 | -3.702 | -8.7261 | -12.2596 | -11.8784 | 7.9242 | 7.145 | 7.2553 | 6.8721 | 6.8731 | 6.4111 | 6.001 | 5.7946 | 4.9135 | 4.4797 | 2.298 | -2.7261 | -6.2596 | -5.8784 | 1.8577 | 1.1208 | 1.2091 | 0.79102 | 0.73586 | 0.20132 | -0.33232 | -0.59955 | -1.5842 | -2.3705 | -14.902 | -19.7277 | -22.5569 | -24.2591 | 7.8577 | 7.1208 | 7.2091 | 6.791 | 6.7359 | 6.2013 | 5.6677 | 5.4004 | 4.4158 | 3.6295 | -8.902 | -13.7277 | -16.5569 | -18.2591 | 1.8469 | 1.086 | 1.1791 | 0.783 | 0.72649 | -4.5728 | -4.7767 | -5.1148 | -5.8867 | -6.6814 | -12.7882 | -16.8649 | -18.869 | -17.9607 | 7.8469 | 7.086 | 7.086 | 6.783 | 6.7265 | 1.4272 | 1.2233 | 0.88523 | 0.11328 | -0.68144 | -6.7882 | -10.8649 | -12.869 | -11.9607 | 351827 | 494315 | KENDAL (PARKSIDE RD) | HUTTON
| Monsall | 6.8044 | 6.6142 | 6.5822 | 6.5491 | 6.5406 | 6.5173 | 6.4615 | 2.4466 | 2.4047 | 2.4002 | 2.2741 | 2.2878 | 2.3108 | 2.3765 | 16.3044 | 16.1142 | 16.0822 | 16.0491 | 16.0406 | 16.0173 | 15.9615 | 15.9466 | 15.9047 | 15.9002 | 15.7741 | 15.7878 | 15.8108 | 15.8765 | 6.9892 | 6.9606 | 6.9094 | 6.8499 | 6.8226 | 6.7954 | 6.734 | 6.7091 | 6.6572 | 6.6406 | 6.4902 | 6.4554 | 6.4425 | 6.4912 | 16.4892 | 16.4606 | 16.4094 | 16.3499 | 16.3226 | 16.2954 | 16.234 | 16.2091 | 16.1572 | 16.1406 | 15.9902 | 15.9554 | 15.9425 | 15.9912 | 6.8044 | 6.6143 | 6.5824 | 6.5493 | 6.541 | 6.5178 | 6.4622 | 6.4474 | 6.4057 | 6.4019 | 6.2778 | 6.2926 | 6.3159 | 6.3814 | 16.3044 | 16.1143 | 16.0824 | 16.0493 | 16.041 | 16.0178 | 15.9622 | 15.9474 | 15.9057 | 15.9019 | 15.7778 | 15.7926 | 15.8159 | 15.8814 | 6.8143 | 6.6344 | 6.6125 | 6.5901 | 6.5921 | 6.5794 | 6.5347 | 6.5304 | 6.5003 | 6.509 | 6.4392 | 6.4371 | 6.4512 | 6.5231 | 16.3143 | 16.1344 | 16.1125 | 16.0901 | 16.0921 | 16.0794 | 16.0347 | 16.0304 | 16.0003 | 16.009 | 15.9392 | 15.9371 | 15.9512 | 16.0231 | 6.8136 | 6.6323 | 6.6096 | 6.5865 | 6.5878 | 6.575 | 6.5305 | 6.527 | 6.4977 | 6.4886 | 6.3476 | 6.3518 | 6.3884 | 6.5347 | 16.3136 | 16.1323 | 16.1323 | 16.0865 | 16.0878 | 16.075 | 16.0305 | 16.027 | 15.9977 | 15.9886 | 15.8476 | 15.8518 | 15.8884 | 16.0347 | 386332 | 401003 | STUART ST | STALYBRIDGE
| Monton | 6.7037 | 6.2199 | 6.099 | 5.7845 | 5.4501 | 5.029 | 4.5126 | 4.0136 | 3.457 | 2.891 | 0.81148 | -0.47145 | -1.0084 | -1.2075 | 10.2037 | 9.7199 | 9.599 | 9.2845 | 8.9501 | 8.529 | 8.0126 | 7.5136 | 6.957 | 6.391 | 4.3115 | 3.0285 | 2.4916 | 2.2925 | 6.782 | 6.3492 | 6.184 | 5.9032 | 5.6351 | 5.2459 | 4.7863 | 4.3262 | 3.7888 | 3.3087 | 1.6735 | 0.40651 | -0.40594 | -1.0538 | 10.282 | 9.8492 | 9.684 | 9.4032 | 9.1351 | 8.7459 | 8.2863 | 7.8262 | 7.2888 | 6.8087 | 5.1735 | 3.9065 | 3.0941 | 2.4462 | 6.7133 | 6.2549 | 6.1525 | 5.8525 | 5.5355 | 5.1377 | 4.6412 | 4.1628 | 3.6382 | 3.1274 | 1.2787 | 0.11659 | -0.26894 | -0.48016 | 10.2133 | 9.7549 | 9.6525 | 9.3525 | 9.0355 | 8.6377 | 8.1412 | 7.6628 | 7.1382 | 6.6274 | 4.7787 | 3.6166 | 3.2311 | 3.0198 | 6.7175 | 6.2488 | 6.1488 | 5.8483 | 5.5599 | 5.1723 | 4.6873 | 4.2202 | 3.7416 | 3.3187 | 0.77184 | -3.2242 | -6.096 | -8.0896 | 10.2175 | 9.7488 | 9.6488 | 9.3483 | 9.0599 | 8.6723 | 8.1873 | 7.7202 | 7.2416 | 6.8187 | 4.2718 | 0.27576 | -2.596 | -4.5896 | 6.5882 | 6.058 | 5.9987 | 5.7476 | 5.4972 | 5.1739 | 4.7329 | 4.3258 | 3.8409 | 2.8562 | -1.8331 | -5.4352 | -7.3275 | -6.9212 | 10.0882 | 9.558 | 9.558 | 9.2476 | 8.9972 | 8.6739 | 8.2329 | 7.8258 | 7.3409 | 6.3562 | 1.6669 | -1.9352 | -3.8275 | -3.4212 | 376321 | 399494 | BARTON | CARRINGTON
| Moorside | 8.3215 | 7.5867 | 7.0505 | 6.6607 | 6.5299 | 6.1718 | 5.7749 | 5.3943 | 5.0299 | 4.4698 | 2.7487 | 1.9103 | 1.6455 | 1.9135 | 11.8215 | 11.0867 | 10.5505 | 10.1607 | 10.0299 | 9.6718 | 9.2749 | 8.8943 | 8.5299 | 7.9698 | 6.2487 | 5.4103 | 5.1455 | 5.4135 | 8.6509 | 8.2351 | 7.8127 | 7.4869 | 7.4031 | 7.1071 | 6.7743 | 6.4527 | 6.1351 | 5.729 | 4.6789 | 3.7908 | 3.1087 | 2.7854 | 12.1509 | 11.7351 | 11.3127 | 10.9869 | 10.9031 | 10.6071 | 10.2743 | 9.9527 | 9.6351 | 9.229 | 8.1789 | 7.2908 | 6.6087 | 6.2854 | 8.326 | 7.6005 | 7.0756 | 6.7002 | 6.5803 | 6.2363 | 5.8533 | 5.4856 | 5.1389 | 4.6281 | 3.0867 | 2.3976 | 2.1907 | 2.4409 | 11.826 | 11.1005 | 10.5756 | 10.2002 | 10.0803 | 9.7363 | 9.3533 | 8.9856 | 8.6389 | 8.1281 | 6.5867 | 5.8976 | 5.6907 | 5.9409 | 8.3307 | 7.5923 | 7.0597 | 6.6812 | 6.5539 | 6.1915 | 5.7758 | 5.3824 | 5.0585 | 4.6433 | 3.1067 | 1.324 | 0.36746 | -0.16097 | 11.8307 | 11.0923 | 10.5597 | 10.1812 | 10.0539 | 9.6915 | 9.2758 | 8.8824 | 8.5585 | 8.1433 | 6.6067 | 4.824 | 3.8675 | 3.339 | 8.2961 | 7.5021 | 6.9636 | 6.5986 | 6.4809 | 6.1511 | 5.7819 | 5.4545 | 5.1961 | 4.6185 | 2.2728 | 0.87621 | 0.33362 | 0.84986 | 11.7961 | 11.0021 | 11.0021 | 10.0986 | 9.9809 | 9.6511 | 9.2819 | 8.9545 | 8.6961 | 8.1185 | 5.7728 | 4.3762 | 3.8336 | 4.3499 | 349331 | 435746 | RIBBLE | PENWORTHAM
| Morton Park & Pirelli | 8.3888 | 7.6728 | 7.6926 | 4.2358 | 1.1697 | -2.432 | -6.0486 | 2.4718 | -0.73805 | -3.4421 | -8.6715 | -11.1024 | -11.7859 | -11.4474 | 12.1888 | 11.4728 | 11.4926 | 8.0358 | 4.9697 | 1.368 | -2.2486 | -4.5282 | -7.7381 | -10.4421 | -15.6715 | -18.1024 | -18.7859 | -18.4474 | 8.668 | 8.1778 | 8.0715 | 6.9038 | 6.0839 | 4.817 | 3.5331 | 13.5249 | 12.3883 | 11.3341 | 9.4103 | 8.1877 | 7.5028 | 7.2155 | 12.468 | 11.9778 | 11.8715 | 10.7038 | 9.8839 | 8.617 | 7.3331 | 6.5249 | 5.3883 | 4.3341 | 2.4103 | 1.1877 | 0.50276 | 0.21552 | 8.4035 | 7.7129 | 7.7532 | 4.3173 | 1.2744 | -2.2996 | -5.889 | 2.587 | -0.51756 | -3.1534 | -8.2842 | -10.526 | -10.9589 | -10.6098 | 12.2035 | 11.5129 | 11.5532 | 8.1173 | 5.0744 | 1.5004 | -2.089 | -4.413 | -7.5176 | -10.1534 | -15.2842 | -17.526 | -17.9589 | -17.6098 | 8.4086 | 7.7028 | 7.7277 | 4.27 | 1.2235 | -2.365 | -5.994 | 2.5108 | -0.61653 | -4.9862 | -13.3531 | -19.8542 | -24.0885 | -26.7823 | 12.2086 | 11.5028 | 11.5277 | 8.07 | 5.0235 | 1.435 | -2.194 | -4.4892 | -7.6165 | -11.9862 | -20.3531 | -26.8542 | -31.0885 | -33.7823 | 8.4511 | 7.7507 | 7.7827 | 4.3624 | 1.3558 | -2.693 | -10.2433 | -4.6248 | -8.541 | -11.6606 | -18.5558 | -23.415 | -26.2914 | -25.1413 | 12.2511 | 11.5507 | 11.5507 | 8.1624 | 5.1558 | 1.107 | -6.4433 | -11.6248 | -15.541 | -18.6606 | -25.5558 | -30.415 | -33.2914 | -32.1413 | 337826 | 553939 | CARLISLE | HARKER
| Mosley Rd | 8.9515 | 8.4579 | 8.3854 | 8.291 | 8.1263 | 7.9133 | 7.7057 | 7.5005 | 7.3012 | 7.1292 | 5.8118 | 3.4634 | 0.60005 | -0.91289 | 7.0885 | 6.5949 | 6.5224 | 6.428 | 6.2633 | 6.0503 | 5.8427 | 5.6375 | 5.4382 | 5.2662 | 3.9488 | 1.6004 | -1.263 | -2.7759 | 9.4394 | 9.3478 | 9.1817 | 9.0043 | 8.7943 | 8.5787 | 8.3581 | 8.1341 | 7.9074 | 7.7089 | 6.6779 | 5.6647 | 4.5475 | 3.6538 | 7.5764 | 7.4848 | 7.3187 | 7.1413 | 6.9313 | 6.7157 | 6.4951 | 6.2711 | 6.0444 | 5.8459 | 4.8149 | 3.8017 | 2.6845 | 1.7908 | 8.9535 | 8.4613 | 8.3898 | 8.2959 | 8.132 | 7.9205 | 7.7144 | 7.5108 | 7.3155 | 7.1555 | 6.0687 | 4.4515 | 1.9502 | 1.132 | 7.0905 | 6.5983 | 6.5268 | 6.4329 | 6.269 | 6.0575 | 5.8514 | 5.6478 | 5.4525 | 5.2925 | 4.2057 | 2.5885 | 0.087155 | -0.73104 | 8.9784 | 8.5126 | 8.466 | 8.3974 | 8.2566 | 8.0406 | 7.8022 | 7.5403 | 7.2604 | 6.9939 | 1.9677 | -1.4315 | -3.5266 | -4.3787 | 7.1154 | 6.6496 | 6.603 | 6.5344 | 6.3936 | 6.1776 | 5.9392 | 5.6773 | 5.3974 | 5.1309 | 0.10466 | -3.2945 | -5.3896 | -6.2417 | 8.9492 | 8.4409 | 8.3654 | 8.2727 | 8.1061 | 7.834 | 7.5003 | 6.7489 | 4.7713 | 4.2443 | -0.071714 | -2.8752 | -4.2012 | -4.0907 | 7.0862 | 6.5779 | 6.5779 | 6.4097 | 6.2431 | 5.971 | 5.6373 | 4.8859 | 2.9083 | 2.3813 | -1.9347 | -4.7382 | -6.0642 | -5.9537 | 379058 | 396289 | STRETFORD | SOUTH MANCHESTER
| Moss Lane | 1.971 | 1.6844 | 1.2254 | 0.63302 | 0.043423 | -0.74639 | -1.6319 | 0.48421 | -0.35255 | -1.3235 | -4.5504 | -6.1442 | -6.5002 | -6.3844 | 6.108 | 5.8214 | 5.3624 | 4.77 | 4.1804 | 3.3906 | 2.5051 | 1.6842 | 0.84745 | -0.12354 | -3.3504 | -4.9442 | -5.3002 | -5.1844 | 2.0474 | 1.8824 | 1.3818 | 0.85459 | 0.3986 | -0.23321 | -0.93952 | -1.6175 | -2.3284 | -3.0899 | -5.4782 | -7.1039 | -8.1292 | -8.7593 | 6.1844 | 6.0194 | 5.5188 | 4.9916 | 4.5356 | 3.9038 | 3.1975 | 2.5195 | 1.8086 | 1.0471 | -1.3412 | -2.9669 | -3.9922 | -4.6223 | 1.9854 | 1.7373 | 1.3069 | 0.73352 | 0.1379 | -0.62771 | -1.4899 | -2.2904 | -3.092 | -3.9726 | -6.8462 | -8.0895 | -8.3189 | -7.976 | 6.1224 | 5.8743 | 5.4439 | 4.8705 | 4.2749 | 3.5093 | 2.6471 | 1.8466 | 1.045 | 0.16442 | -2.7092 | -3.9525 | -4.1819 | -3.839 | 1.981 | 1.72 | 1.3059 | 0.76615 | 0.28271 | -0.37363 | -1.1423 | -1.8312 | -2.44 | -3.0879 | -6.9887 | -14.1999 | -19.55 | -23.1294 | 6.118 | 5.857 | 5.4429 | 4.9032 | 4.4197 | 3.7634 | 2.9947 | 2.3058 | 1.697 | 1.0491 | -2.8517 | -10.0629 | -15.413 | -18.9924 | 1.9501 | 1.604 | 1.1855 | 0.71005 | 0.25667 | -0.30908 | -0.98582 | -1.5582 | -2.2365 | -4.0026 | -12.2434 | -18.6679 | -22.1999 | -20.9556 | 6.0871 | 5.741 | 5.741 | 4.847 | 4.3937 | 3.8279 | 3.1512 | 2.5788 | 1.9005 | 0.13438 | -8.1064 | -14.5309 | -18.0629 | -16.8186 | 380858 | 405856 | KEARSLEY LOCAL | KEARSLEY
| Moss Nook Primary | 17.6536 | 17.2158 | 17.1246 | 16.9404 | 16.7633 | 16.4816 | 16.2124 | 15.9426 | 15.5132 | 15.0246 | 13.3836 | 12.6694 | 12.5916 | 12.8372 | 23.6536 | 23.2158 | 23.1246 | 22.9404 | 22.7633 | 22.4816 | 22.2124 | 21.9426 | 21.5132 | 21.0246 | 19.3836 | 18.6694 | 18.5916 | 18.8372 | 18.0498 | 17.9523 | 17.7694 | 17.515 | 17.3038 | 17.0287 | 16.7573 | 16.3613 | 15.8687 | 15.3425 | 14.2186 | 13.6545 | 13.4247 | 13.457 | 24.0498 | 23.9523 | 23.7694 | 23.515 | 23.3038 | 23.0287 | 22.7573 | 22.3613 | 21.8687 | 21.3425 | 20.2186 | 19.6545 | 19.4247 | 19.457 | 17.6594 | 17.2275 | 17.1426 | 16.9656 | 16.7965 | 16.5244 | 16.2648 | 16.0045 | 15.6866 | 15.2604 | 13.6653 | 13.0345 | 12.9739 | 13.2139 | 23.6594 | 23.2275 | 23.1426 | 22.9656 | 22.7965 | 22.5244 | 22.2648 | 22.0045 | 21.6866 | 21.2604 | 19.6653 | 19.0345 | 18.9739 | 19.2139 | 17.6831 | 17.2773 | 17.2178 | 17.0642 | 16.9182 | 16.6666 | 16.4229 | 16.1749 | 15.9101 | 15.6256 | 13.8835 | 10.6047 | 7.6556 | 5.6181 | 23.6831 | 23.2773 | 23.2178 | 23.0642 | 22.9182 | 22.6666 | 22.4229 | 22.1749 | 21.9101 | 21.6256 | 19.8835 | 16.6047 | 13.6556 | 11.6181 | 17.6765 | 17.2465 | 17.1827 | 17.044 | 16.9162 | 16.6949 | 16.4777 | 16.268 | 16.0345 | 15.5115 | 11.3603 | 7.9155 | 5.9613 | 6.6199 | 23.6765 | 23.2465 | 23.2465 | 23.044 | 22.9162 | 22.6949 | 22.4777 | 22.268 | 22.0345 | 21.5115 | 17.3603 | 13.9155 | 11.9613 | 12.6199 | 384084 | 385010 | MOSS NOOK | SOUTH MANCHESTER
| Moss Side (Leyland) & Seven Stars | 4.0457 | 3.4011 | 3.2707 | 2.8297 | 2.5877 | 2.0121 | 1.5341 | 0.84674 | 0.17107 | -0.5935 | -3.3125 | -4.9353 | -5.479 | -5.9302 | 10.3957 | 9.7511 | 9.6207 | 9.1797 | 8.9377 | 8.3621 | 7.8841 | 7.1967 | 6.5211 | 5.7565 | 3.0375 | 1.4147 | 0.87104 | 0.41982 | 4.4039 | 4.0115 | 3.8023 | 3.3546 | 3.139 | 2.6266 | 2.2243 | 1.7409 | 1.1599 | 0.55419 | -1.5161 | -2.9971 | -3.9034 | -4.4764 | 10.7539 | 10.3615 | 10.1523 | 9.7046 | 9.489 | 8.9766 | 8.5743 | 8.0909 | 7.5099 | 6.9042 | 4.8339 | 3.3529 | 2.4466 | 1.8736 | 4.0521 | 3.4691 | 3.3525 | 2.9243 | 2.6967 | 2.1391 | 1.6521 | 0.98205 | 0.33409 | -0.36337 | -2.766 | -3.9399 | -4.2416 | -4.3726 | 10.4021 | 9.8191 | 9.7025 | 9.2743 | 9.0467 | 8.4891 | 8.0021 | 7.3321 | 6.6841 | 5.9866 | 3.584 | 2.4101 | 2.1084 | 1.9774 | 4.0638 | 3.4332 | 3.324 | 2.9026 | 2.6969 | 2.1512 | 1.7105 | 1.2549 | 0.73753 | 0.23454 | -3.071 | -8.5204 | -12.6238 | -15.5934 | 10.4138 | 9.7832 | 9.674 | 9.2526 | 9.0469 | 8.5012 | 8.0605 | 7.6049 | 7.0875 | 6.5845 | 3.279 | -2.1704 | -6.2738 | -9.2434 | 4.0513 | 3.3674 | 3.2523 | 2.8567 | 2.6836 | 2.1775 | 1.7587 | 1.2646 | 0.65945 | -0.66265 | -6.665 | -11.5498 | -14.5455 | -14.2381 | 10.4013 | 9.7174 | 9.7174 | 9.2067 | 9.0336 | 8.5275 | 8.1087 | 7.6146 | 7.0094 | 5.6873 | -0.31499 | -5.1998 | -8.1955 | -7.8881 | 352170 | 422970 | LEYLAND | PENWORTHAM
| Moss Side (Longsight) | 4.2381 | 4.0021 | 1.6606 | -0.49322 | -2.648 | -4.854 | -7.5366 | -0.66717 | -1.69 | -4.9434 | -7.7947 | -8.7687 | -9.6233 | -9.4663 | 10.7381 | 10.5021 | 8.1606 | 6.0068 | 3.852 | 1.646 | -1.0366 | -2.1672 | -3.19 | -6.4434 | -9.2947 | -10.2687 | -11.1233 | -10.9663 | 4.4716 | 4.4298 | 1.9895 | -0.22793 | -2.4244 | -4.6547 | -7.3716 | -8.5449 | -9.6071 | -11.131 | -12.163 | -13.1601 | -14.1178 | -14.5834 | 10.9716 | 10.9298 | 8.4895 | 6.2721 | 4.0756 | 1.8453 | -0.87157 | -2.0449 | -3.1071 | -4.631 | -5.663 | -6.6601 | -7.6178 | -8.0834 | 4.2469 | 4.0224 | 1.6953 | -0.44815 | -2.5911 | -4.785 | -7.452 | -8.5709 | -9.5771 | -12.7887 | -15.4983 | -16.3539 | -17.1469 | -16.9876 | 10.7469 | 10.5224 | 8.1953 | 6.0518 | 3.9089 | 1.715 | -0.95199 | -2.0709 | -3.0771 | -6.2887 | -8.9983 | -9.8539 | -10.6469 | -10.4876 | 4.2537 | 4.0347 | 1.7119 | -0.43224 | -2.5686 | -4.7689 | -7.4964 | -8.6797 | -9.6977 | -12.8228 | -16.407 | -22.0307 | -25.7417 | -27.688 | 10.7537 | 10.5347 | 8.2119 | 6.0678 | 3.9314 | 1.7311 | -0.99636 | -2.1797 | -3.1977 | -6.3228 | -9.907 | -15.5307 | -19.2417 | -21.188 | 4.2921 | 4.1071 | 1.8219 | -0.27897 | -2.4078 | -4.579 | -7.24 | -8.3583 | -9.4301 | -15.3074 | -20.9702 | -24.6977 | -27.2158 | -26.281 | 10.7921 | 10.6071 | 10.6071 | 6.221 | 4.0922 | 1.921 | -0.74002 | -1.8583 | -2.9301 | -8.8074 | -14.4702 | -18.1977 | -20.7158 | -19.781 | 384007 | 395893 | LONGSIGHT | BREDBURY
| Mossley | 9.6794 | 9.4084 | 9.1164 | 8.7093 | 8.3589 | 7.8365 | 7.2262 | 6.6439 | 6.0361 | 5.3225 | 2.9554 | 1.9026 | 1.8008 | 2.0627 | 14.3164 | 14.0454 | 13.7534 | 13.3463 | 12.9959 | 12.4735 | 11.8632 | 11.2809 | 10.6731 | 9.9595 | 7.5924 | 6.5396 | 6.4378 | 6.6997 | 9.7354 | 9.5063 | 9.1628 | 8.7986 | 8.5874 | 8.1493 | 7.7008 | 7.2264 | 6.7123 | 6.1849 | 4.5644 | 3.4711 | 2.8573 | 2.5502 | 14.3724 | 14.1433 | 13.7998 | 13.4356 | 13.2244 | 12.7863 | 12.3378 | 11.8634 | 11.3493 | 10.8219 | 9.2014 | 8.1081 | 7.4943 | 7.1872 | 9.6868 | 9.4281 | 9.1496 | 8.7576 | 8.4087 | 7.9052 | 7.3138 | 6.7488 | 6.1676 | 5.5206 | 3.3938 | 2.5062 | 2.4543 | 2.7525 | 14.3238 | 14.0651 | 13.7866 | 13.3946 | 13.0457 | 12.5422 | 11.9508 | 11.3858 | 10.8046 | 10.1576 | 8.0308 | 7.1432 | 7.0913 | 7.3895 | 9.6883 | 9.4214 | 9.1435 | 8.7626 | 8.495 | 8.0358 | 7.4766 | 6.9558 | 6.4862 | 6.0086 | 3.149 | -2.4497 | -6.5765 | -9.2953 | 14.3253 | 14.0584 | 13.7805 | 13.3996 | 13.132 | 12.6728 | 12.1136 | 11.5928 | 11.1232 | 10.6456 | 7.786 | 2.1873 | -1.9395 | -4.6583 | 9.6983 | 9.4013 | 9.1233 | 8.7778 | 8.4642 | 8.0704 | 7.5891 | 7.1716 | 6.6315 | 5.2151 | -1.2553 | -6.1497 | -8.7704 | -7.6244 | 14.3353 | 14.0383 | 14.0383 | 13.4148 | 13.1012 | 12.7074 | 12.2261 | 11.8086 | 11.2685 | 9.8521 | 3.3817 | -1.5127 | -4.1334 | -2.9874 | 397437 | 401979 | HARTSHEAD-HEYROD | STALYBRIDGE
| Mount St | 11.1997 | 10.0016 | 9.4421 | 9.0531 | 8.8516 | 8.263 | 7.6172 | 7.0778 | 6.4411 | 5.8067 | 3.3593 | 1.8774 | 1.5048 | 0.82523 | 15.8366 | 14.6386 | 14.079 | 13.69 | 13.4885 | 12.8999 | 12.2541 | 11.7148 | 11.078 | 10.4437 | 7.9962 | 6.5143 | 6.1417 | 5.4622 | 11.8221 | 11.2173 | 10.6439 | 10.2312 | 10.0821 | 9.5542 | 8.9619 | 8.4582 | 7.8596 | 7.3221 | 5.3878 | 3.8705 | 3.1326 | 2.5658 | 16.4591 | 15.8543 | 15.2808 | 14.8681 | 14.7191 | 14.1912 | 13.5988 | 13.0952 | 12.4965 | 11.9591 | 10.0247 | 8.5074 | 7.7696 | 7.2027 | 11.2142 | 10.0275 | 9.4946 | 9.0795 | 8.8903 | 8.3194 | 7.6919 | 7.1692 | 6.5592 | 5.9814 | 3.7397 | 2.4491 | 2.1355 | 2.0535 | 15.8511 | 14.6644 | 14.1316 | 13.7164 | 13.5272 | 12.9563 | 12.3288 | 11.8062 | 11.1961 | 10.6183 | 8.3766 | 7.0861 | 6.7725 | 6.6904 | 11.219 | 10.0342 | 9.4686 | 9.1103 | 8.9698 | 8.4284 | 7.8074 | 7.2951 | 6.7461 | 6.2659 | 2.8398 | -2.0612 | -5.7502 | -8.5299 | 15.8559 | 14.6711 | 14.1056 | 13.7473 | 13.6067 | 13.0653 | 12.4443 | 11.932 | 11.3831 | 10.9028 | 7.4768 | 2.5757 | -1.1133 | -3.893 | 11.1954 | 9.9645 | 9.362 | 8.925 | 8.7619 | 8.235 | 7.6394 | 7.1703 | 6.5587 | 5.2914 | -0.6868 | -5.2954 | -8.0742 | -7.5227 | 15.8323 | 14.6014 | 14.6014 | 13.5619 | 13.3988 | 12.8719 | 12.2764 | 11.8072 | 11.1957 | 9.9283 | 3.9501 | -0.65846 | -3.4372 | -2.8857 | 376250 | 397574 | BARTON | CARRINGTON
| Musgrave Rd | 8.6058 | 8.3322 | 8.2011 | 7.8531 | 7.6792 | 7.3158 | 6.9206 | 6.5514 | 6.1725 | 5.7224 | 4.1458 | 3.3257 | 3.0065 | 3.0769 | 14.2258 | 13.9522 | 13.8211 | 13.4731 | 13.2992 | 12.9358 | 12.5406 | 12.1714 | 11.7925 | 11.3424 | 9.7658 | 8.9457 | 8.6265 | 8.6969 | 8.6839 | 8.4749 | 8.2978 | 7.966 | 7.8297 | 7.5076 | 7.1494 | 6.8159 | 6.4668 | 6.104 | 4.9996 | 4.2363 | 3.6606 | 3.3698 | 14.3039 | 14.0949 | 13.9178 | 13.586 | 13.4497 | 13.1276 | 12.7694 | 12.4359 | 12.0868 | 11.724 | 10.6196 | 9.8563 | 9.2806 | 8.9898 | 8.6151 | 8.3487 | 8.2321 | 7.8966 | 7.7353 | 7.3866 | 7.0056 | 6.6493 | 6.2905 | 5.8865 | 4.491 | 3.8582 | 3.6178 | 3.7756 | 14.2351 | 13.9687 | 13.8521 | 13.5166 | 13.3553 | 13.0066 | 12.6256 | 12.2693 | 11.9105 | 11.5065 | 10.111 | 9.4782 | 9.2378 | 9.3956 | 8.6158 | 8.3551 | 8.2432 | 7.916 | 7.7744 | 7.4399 | 7.0558 | 6.6969 | 6.3851 | 6.0579 | 3.6619 | -1.5156 | -5.6644 | -8.1515 | 14.2358 | 13.9751 | 13.8632 | 13.536 | 13.3944 | 13.0599 | 12.6758 | 12.3169 | 12.0051 | 11.6779 | 9.2819 | 4.1044 | -0.044356 | -2.5315 | 8.6234 | 8.3239 | 8.2217 | 7.9396 | 7.8379 | 7.5605 | 7.2311 | 6.9343 | 6.5156 | 5.2775 | -0.57119 | -5.2163 | -7.9194 | -6.8266 | 14.2434 | 13.9439 | 13.9439 | 13.5596 | 13.4579 | 13.1805 | 12.8511 | 12.5543 | 12.1356 | 10.8975 | 5.0488 | 0.40369 | -2.2994 | -1.2066 | 370045 | 409863 | BOLTON | KEARSLEY
| Nelson | 4.7048 | 3.4827 | 3.0522 | 2.8407 | 2.6302 | 2.3214 | 1.9937 | 1.6559 | 1.3139 | 0.89931 | -0.52985 | -1.447 | -1.7394 | -1.7376 | 9.3448 | 8.1227 | 7.6922 | 7.4807 | 7.2702 | 6.9614 | 6.6337 | 6.2959 | 5.9539 | 5.5393 | 4.1102 | 3.193 | 2.9006 | 2.9024 | 5.4063 | 4.8687 | 4.4161 | 4.1078 | 3.8248 | 3.4695 | 3.0765 | 2.6579 | 2.2242 | 1.77 | 0.84174 | 0.028998 | -0.43053 | -0.70047 | 10.0463 | 9.5087 | 9.0561 | 8.7478 | 8.4648 | 8.1095 | 7.7165 | 7.2979 | 6.8642 | 6.41 | 5.4817 | 4.669 | 4.2095 | 3.9395 | 4.7169 | 3.5103 | 3.0949 | 2.9092 | 2.7632 | 2.4748 | 2.1676 | 1.8505 | 1.5357 | 1.1697 | -0.097731 | -0.80959 | -1.007 | -0.89846 | 9.3569 | 8.1503 | 7.7349 | 7.5492 | 7.4032 | 7.1148 | 6.8076 | 6.4905 | 6.1757 | 5.8097 | 4.5423 | 3.8304 | 3.633 | 3.7415 | 4.7257 | 3.5199 | 3.0929 | 2.8902 | 2.685 | 2.3704 | 2.0112 | 1.6352 | 1.2911 | 0.94205 | -1.4398 | -6.7954 | -10.7524 | -13.1104 | 9.3657 | 8.1599 | 7.7329 | 7.5302 | 7.325 | 7.0104 | 6.6512 | 6.2752 | 5.9311 | 5.5821 | 3.2002 | -2.1554 | -6.1124 | -8.4704 | 4.7461 | 3.5439 | 3.1396 | 2.9774 | 2.8373 | 2.5698 | 2.2633 | 1.9453 | 1.4931 | 0.17879 | -5.8528 | -10.6719 | -13.0987 | -11.8767 | 9.3861 | 8.1839 | 8.1839 | 7.6174 | 7.4773 | 7.2098 | 6.9033 | 6.5853 | 6.1331 | 4.8188 | -1.2128 | -6.0319 | -8.4587 | -7.2367 | 386020 | 438507 | NELSON | PADIHAM
| New Moston | 10.5906 | 10.298 | 10.0961 | 9.7391 | 9.3796 | 8.9066 | 8.4422 | 7.9252 | 7.3633 | 6.7044 | 4.269 | 2.8897 | 2.4047 | 2.5486 | 15.2276 | 14.935 | 14.7331 | 14.3761 | 14.0166 | 13.5436 | 13.0792 | 12.5622 | 12.0003 | 11.3414 | 8.906 | 7.5267 | 7.0417 | 7.1856 | 10.6961 | 10.4891 | 10.2202 | 9.8852 | 9.5786 | 9.1658 | 8.7568 | 8.2952 | 7.8014 | 7.3248 | 5.637 | 4.1621 | 3.1821 | 2.5145 | 15.3331 | 15.1261 | 14.8572 | 14.5222 | 14.2156 | 13.8028 | 13.3938 | 12.9322 | 12.4384 | 11.9618 | 10.274 | 8.7991 | 7.8191 | 7.1515 | 10.6009 | 10.3186 | 10.1264 | 9.7794 | 9.4321 | 8.9729 | 8.5216 | 8.0176 | 7.4779 | 6.8742 | 4.6399 | 3.4066 | 2.9762 | 3.1143 | 15.2379 | 14.9556 | 14.7634 | 14.4164 | 14.0691 | 13.6099 | 13.1586 | 12.6546 | 12.1149 | 11.5112 | 9.2769 | 8.0436 | 7.6132 | 7.7513 | 10.5981 | 10.3104 | 10.115 | 9.7619 | 9.4356 | 8.9774 | 8.4598 | 7.8939 | 7.3705 | 6.868 | 4.036 | -0.80577 | -4.2091 | -6.6521 | 15.2351 | 14.9474 | 14.752 | 14.3989 | 14.0726 | 13.6144 | 13.0968 | 12.5309 | 12.0075 | 11.505 | 8.673 | 3.8312 | 0.42791 | -2.0151 | 10.6288 | 10.322 | 10.1107 | 9.7608 | 9.3942 | 8.9432 | 8.4897 | 8.003 | 7.4446 | 6.2344 | 0.57453 | -3.6738 | -5.8952 | -5.2829 | 15.2658 | 14.959 | 14.959 | 14.3978 | 14.0312 | 13.5802 | 13.1267 | 12.64 | 12.0816 | 10.8714 | 5.2115 | 0.96316 | -1.2582 | -0.64592 | 388333 | 402657 | CHADDERTON | WHITEGATE
| Newbiggin on Lune | 0.56884 | 0.49327 | 0.46561 | 0.40604 | 0.38122 | 0.32041 | 0.24872 | 0.20628 | 0.12517 | 0.023105 | -0.33865 | -0.51673 | -0.59925 | -0.516 | 2.0688 | 1.9933 | 1.9656 | 1.906 | 1.8812 | 1.8204 | 1.7487 | 1.7063 | 1.6252 | 1.5231 | 1.1614 | 0.98327 | 0.90075 | 0.984 | 0.58706 | 0.52986 | 0.49991 | 0.45503 | 0.43405 | 0.37984 | 0.31775 | 0.27946 | 0.21109 | 0.14958 | -0.040884 | -0.28278 | -0.49214 | -0.6172 | 2.0871 | 2.0299 | 1.9999 | 1.955 | 1.9341 | 1.8798 | 1.8178 | 1.7795 | 1.7111 | 1.6496 | 1.4591 | 1.2172 | 1.0079 | 0.8828 | 0.5698 | 0.49822 | 0.46844 | 0.41151 | 0.38832 | 0.32981 | 0.26026 | 0.21892 | 0.14215 | 0.051908 | -0.26523 | -0.41334 | -0.476 | -0.39732 | 2.0698 | 1.9982 | 1.9684 | 1.9115 | 1.8883 | 1.8298 | 1.7603 | 1.7189 | 1.6422 | 1.5519 | 1.2348 | 1.0867 | 1.024 | 1.1027 | 0.56987 | 0.49028 | 0.45892 | 0.39771 | 0.36427 | 0.29174 | 0.20433 | 0.1515 | 0.072802 | 0.0063231 | -0.26891 | -0.41799 | -0.50393 | -0.54374 | 2.0699 | 1.9903 | 1.9589 | 1.8977 | 1.8643 | 1.7917 | 1.7043 | 1.6515 | 1.5728 | 1.5063 | 1.2311 | 1.082 | 0.99607 | 0.95626 | 0.56172 | 0.47488 | 0.44001 | 0.37807 | 0.33738 | 0.26324 | 0.18109 | 0.13699 | 0.067903 | -0.002165 | -0.29776 | -0.40229 | -0.37443 | -0.28351 | 2.0617 | 1.9749 | 1.9749 | 1.8781 | 1.8374 | 1.7632 | 1.6811 | 1.637 | 1.5679 | 1.4978 | 1.2022 | 1.0977 | 1.1256 | 1.2165 | 369770 | 505803 | PENRITH & SHAP | HUTTON
| Newby | 1.3792 | 1.2117 | 1.1545 | 1.069 | 0.96858 | 0.80891 | 0.65046 | 0.50567 | 0.35233 | 0.1577 | -0.77999 | -1.3576 | -1.6824 | -1.5814 | 8.3792 | 8.2117 | 8.1545 | 8.069 | 7.9686 | 7.8089 | 7.6505 | 7.5057 | 7.3523 | 7.1577 | 6.22 | 5.6424 | 5.3176 | 5.4186 | 1.4479 | 1.3363 | 1.2048 | 1.05 | 0.88509 | 0.65773 | 0.35573 | 0.039242 | -0.30123 | -0.73239 | -1.0237 | -1.217 | -1.4818 | -1.8345 | 8.4479 | 8.3363 | 8.2048 | 8.05 | 7.8851 | 7.6577 | 7.3557 | 7.0392 | 6.6988 | 6.2676 | 5.9763 | 5.783 | 5.5182 | 5.1655 | 1.3911 | 1.2297 | 1.1816 | 1.1057 | 1.0156 | 0.86616 | 0.70914 | 0.59971 | 0.44139 | 0.21767 | -0.6231 | -1.1165 | -1.3785 | -1.2822 | 8.3911 | 8.2297 | 8.1816 | 8.1057 | 8.0156 | 7.8662 | 7.7091 | 7.5997 | 7.4414 | 7.2177 | 6.3769 | 5.8835 | 5.6215 | 5.7178 | 1.3901 | 1.2338 | 1.1947 | 1.0994 | 0.9817 | 0.76572 | 0.50952 | 0.31066 | 0.12112 | -0.10513 | -1.0625 | -2.3989 | -3.2202 | -3.7831 | 8.3901 | 8.2338 | 8.1947 | 8.0994 | 7.9817 | 7.7657 | 7.5095 | 7.3107 | 7.1211 | 6.8949 | 5.9375 | 4.6011 | 3.7798 | 3.2169 | 1.3971 | 1.2392 | 1.2096 | 1.1249 | 1 | 0.79292 | 0.56529 | 0.40196 | 0.24315 | -0.14272 | -1.8431 | -2.9899 | -3.5277 | -3.2918 | 8.3971 | 8.2392 | 8.2392 | 8.1249 | 8 | 7.7929 | 7.5653 | 7.402 | 7.2431 | 6.8573 | 5.1569 | 4.0101 | 3.4723 | 3.7082 | 360520 | 521151 | PENRITH & SHAP | HUTTON
| Newton | 11.5383 | 11.4047 | 11.2905 | 11.1463 | 10.9985 | 10.8179 | 10.6146 | 10.4144 | 10.2076 | 9.9732 | 9.2332 | 8.9362 | 8.9007 | 9.0207 | 17.2963 | 17.1627 | 17.0485 | 16.9043 | 16.7565 | 16.5759 | 16.3726 | 16.1724 | 15.9656 | 15.7312 | 14.9912 | 14.6942 | 14.6587 | 14.7787 | 11.622 | 11.5556 | 11.4308 | 11.3031 | 11.1876 | 11.0439 | 10.8793 | 10.7168 | 10.5472 | 10.3728 | 9.8383 | 9.5109 | 9.3613 | 9.3266 | 17.38 | 17.3136 | 17.1888 | 17.0611 | 16.9456 | 16.8019 | 16.6373 | 16.4748 | 16.3052 | 16.1308 | 15.5963 | 15.2689 | 15.1193 | 15.0846 | 11.5419 | 11.4125 | 11.298 | 11.1572 | 11.0139 | 10.8384 | 10.6401 | 10.4444 | 10.2456 | 10.0327 | 9.3745 | 9.1521 | 9.1432 | 9.2803 | 17.2999 | 17.1705 | 17.056 | 16.9152 | 16.7719 | 16.5964 | 16.3981 | 16.2024 | 16.0036 | 15.7907 | 15.1325 | 14.9101 | 14.9012 | 15.0383 | 11.5449 | 11.4195 | 11.3198 | 11.1942 | 11.0742 | 10.9266 | 10.7565 | 10.5956 | 10.4514 | 10.3058 | 9.3988 | 7.8723 | 6.7802 | 6.1004 | 17.3029 | 17.1775 | 17.0778 | 16.9522 | 16.8322 | 16.6846 | 16.5145 | 16.3536 | 16.2094 | 16.0638 | 15.1568 | 13.6303 | 12.5382 | 11.8584 | 11.524 | 11.3605 | 11.2352 | 11.1039 | 10.9801 | 10.8402 | 10.6793 | 10.5361 | 10.3675 | 9.9522 | 8.0879 | 6.731 | 6.021 | 6.4126 | 17.282 | 17.1185 | 17.1185 | 16.8619 | 16.7381 | 16.5982 | 16.4373 | 16.2941 | 16.1255 | 15.7102 | 13.8459 | 12.489 | 11.779 | 12.1706 | 396385 | 396464 | HYDE | STALYBRIDGE
| Newton Heath | 3.9018 | 3.4188 | 3.1667 | 2.977 | 2.813 | 2.5769 | 2.336 | 2.0646 | 1.7757 | 1.4499 | 0.24238 | -0.44896 | -0.68486 | -0.6655 | 1.9018 | 1.4188 | 1.1667 | 0.977 | 0.81301 | 0.57689 | 0.33598 | 0.064591 | -0.22432 | -0.55015 | -1.7576 | -2.449 | -2.6849 | -2.6655 | 4.1345 | 3.8621 | 3.6384 | 3.4435 | 3.2946 | 3.0733 | 2.8436 | 2.5827 | 2.3025 | 2.0301 | 1.1522 | 0.4813 | 0.081727 | -0.19294 | 2.1345 | 1.8621 | 1.6384 | 1.4435 | 1.2946 | 1.0733 | 0.84362 | 0.58267 | 0.30252 | 0.030104 | -0.84778 | -1.5187 | -1.9183 | -2.1929 | 3.9152 | 3.4409 | 3.2059 | 3.0269 | 2.871 | 2.6488 | 2.4215 | 2.1639 | 1.8937 | 1.6031 | 0.51311 | -0.083846 | -0.26488 | -0.21841 | 1.9152 | 1.4409 | 1.2059 | 1.0269 | 0.871 | 0.64881 | 0.42146 | 0.16392 | -0.10626 | -0.39693 | -1.4869 | -2.0838 | -2.2649 | -2.2184 | 3.9037 | 3.4202 | 3.1635 | 2.9621 | 2.8057 | 2.5658 | 2.2975 | 1.9937 | 1.7164 | 1.4474 | -0.22434 | -3.725 | -6.4461 | -8.3845 | 1.9037 | 1.4202 | 1.1635 | 0.96206 | 0.80575 | 0.56577 | 0.2975 | -0.0062914 | -0.28357 | -0.55257 | -2.2243 | -5.725 | -8.4461 | -10.3845 | 3.9149 | 3.4183 | 3.1842 | 2.9993 | 2.8361 | 2.6222 | 2.3897 | 2.1293 | 1.8108 | 0.97057 | -2.984 | -6.1425 | -7.9783 | -7.5763 | 1.9149 | 1.4183 | 1.4183 | 0.99927 | 0.83612 | 0.62216 | 0.38972 | 0.12934 | -0.18924 | -1.0294 | -4.984 | -8.1425 | -9.9783 | -9.5763 | 388030 | 400511 | CHADDERTON | WHITEGATE
| Newton Le Willows | 8.8977 | 8.5919 | 8.3258 | 7.9667 | 7.5755 | 7.027 | 6.4671 | 5.9161 | 5.3751 | 4.6901 | 2.3596 | 1.0295 | 0.57863 | 0.30653 | 13.0347 | 12.7289 | 12.4628 | 12.1037 | 11.7125 | 11.164 | 10.6041 | 10.0531 | 9.5121 | 8.8271 | 6.4966 | 5.1665 | 4.7156 | 4.4435 | 9.0609 | 8.886 | 8.5401 | 8.1873 | 7.839 | 7.3466 | 6.8416 | 6.3433 | 5.8446 | 5.2612 | 3.6181 | 2.4693 | 1.7598 | 1.3205 | 13.1979 | 13.023 | 12.6771 | 12.3243 | 11.976 | 11.4836 | 10.9786 | 10.4803 | 9.9816 | 9.3982 | 7.7551 | 6.6063 | 5.8968 | 5.4575 | 8.911 | 8.6172 | 8.3635 | 8.0158 | 7.6391 | 7.1079 | 6.5645 | 6.0291 | 5.5121 | 4.8855 | 2.8566 | 1.855 | 1.5396 | 1.5709 | 13.048 | 12.7542 | 12.5005 | 12.1528 | 11.7761 | 11.2449 | 10.7015 | 10.1661 | 9.6491 | 9.0225 | 6.9936 | 5.992 | 5.6766 | 5.7079 | 8.9069 | 8.6124 | 8.3609 | 8.0154 | 7.6673 | 7.1667 | 6.6505 | 6.1419 | 5.7079 | 5.1886 | 2.0831 | -4.1641 | -9.1191 | -12.4027 | 13.0439 | 12.7494 | 12.4979 | 12.1524 | 11.8043 | 11.3037 | 10.7875 | 10.2789 | 9.8449 | 9.3256 | 6.2201 | -0.027101 | -4.9821 | -8.2657 | 8.9024 | 8.5585 | 8.2882 | 7.9639 | 7.6563 | 7.2111 | 6.7301 | 6.2674 | 5.7098 | 4.1784 | -2.7919 | -8.4282 | -11.7172 | -10.9298 | 13.0394 | 12.6955 | 12.6955 | 12.1009 | 11.7933 | 11.3481 | 10.8671 | 10.4044 | 9.8468 | 8.3154 | 1.3451 | -4.2912 | -7.5802 | -6.7928 | 357891 | 395944 | GOLBORNE | BOLD
| Newtongate T11 & T12 | 5.9 | 5.3438 | 4.9619 | 4.6524 | 4.3501 | 4.0584 | 3.4847 | 3.2336 | 2.8924 | 2.2847 | -4.8329 | -10.4498 | -12.3836 | -13.3145 | 9.9 | 9.3438 | 8.9619 | 8.6524 | 8.3501 | 8.0584 | 7.4847 | 7.2336 | 6.8924 | 6.2847 | -0.83291 | -6.4498 | -8.3836 | -9.3145 | 6.4024 | 6.2738 | 5.824 | 5.4567 | 5.1315 | 4.8458 | 4.2773 | 3.9707 | 3.5912 | 2.9952 | 1.3687 | -0.41421 | -1.9472 | -3.0483 | 10.4024 | 10.2738 | 9.824 | 9.4567 | 9.1315 | 8.8458 | 8.2773 | 7.9707 | 7.5912 | 6.9952 | 5.3687 | 3.5858 | 2.0528 | 0.95167 | 5.9082 | 5.3674 | 5.0037 | 4.7094 | 4.4224 | 4.145 | 3.5887 | 3.3506 | 3.0328 | 2.4651 | -4.2531 | -9.0088 | -10.4918 | -10.7414 | 9.9082 | 9.3674 | 9.0037 | 8.7094 | 8.4224 | 8.145 | 7.5887 | 7.3506 | 7.0328 | 6.4651 | -0.25312 | -5.0088 | -6.4918 | -6.7414 | 5.9167 | 5.3666 | 4.9847 | 4.6614 | 4.3278 | 3.9601 | 3.2433 | 2.8251 | 2.328 | 1.5716 | -10.5334 | -19.7211 | -24.1361 | -26.0072 | 9.9167 | 9.3666 | 8.9847 | 8.6614 | 8.3278 | 7.9601 | 7.2433 | 6.8251 | 6.328 | 5.5716 | -6.5334 | -15.7211 | -20.1361 | -22.0072 | 5.8985 | 5.3015 | 4.8924 | 4.5543 | 4.1798 | 3.7665 | 2.9898 | 2.5008 | 1.8563 | -0.53903 | -17.8476 | -22.8472 | -25.9144 | -24.8848 | 9.8985 | 9.3015 | 9.3015 | 8.5543 | 8.1798 | 7.7665 | 6.9898 | 6.5008 | 5.8563 | 3.461 | -13.8476 | -18.8472 | -21.9144 | -20.8848 | 349973 | 530340 | PENRITH & SHAP | HUTTON
| Newtongate T13 | 6.2147 | 5.8693 | 5.8891 | 5.7326 | 5.7501 | 5.5342 | 5.3559 | 5.3138 | 5.0801 | 4.8756 | 4.0696 | 3.2988 | 2.7152 | 2.3208 | 10.9647 | 10.6193 | 10.6391 | 10.4826 | 10.5001 | 10.2842 | 10.1059 | 10.0638 | 9.8301 | 9.6256 | 8.8196 | 8.0488 | 7.4652 | 7.0708 | 6.2936 | 6.0151 | 5.9859 | 5.7921 | 5.7763 | 5.5289 | 5.3115 | 5.2267 | 4.9419 | 4.7141 | 4.164 | 3.594 | 3.0452 | 2.6483 | 11.0436 | 10.7651 | 10.7359 | 10.5421 | 10.5263 | 10.2789 | 10.0615 | 9.9767 | 9.6919 | 9.4641 | 8.914 | 8.344 | 7.7952 | 7.3983 | 6.2203 | 5.8906 | 5.921 | 5.776 | 5.8029 | 5.6014 | 5.4366 | 5.4047 | 5.189 | 5.0092 | 4.3176 | 3.7609 | 3.2968 | 3.0694 | 10.9703 | 10.6406 | 10.671 | 10.526 | 10.5529 | 10.3514 | 10.1866 | 10.1547 | 9.939 | 9.7592 | 9.0676 | 8.5109 | 8.0468 | 7.8194 | 6.2172 | 5.8737 | 5.8934 | 5.7292 | 5.7447 | 5.516 | 5.3041 | 5.2214 | 4.9632 | 4.762 | 3.3727 | 0.56234 | -1.7557 | -3.2677 | 10.9672 | 10.6237 | 10.6434 | 10.4792 | 10.4947 | 10.266 | 10.0541 | 9.9714 | 9.7132 | 9.512 | 8.1227 | 5.3123 | 2.9943 | 1.4823 | 6.2435 | 5.9194 | 5.9521 | 5.8071 | 5.8342 | 5.619 | 5.4186 | 5.3406 | 5.0289 | 4.4214 | 1.4796 | -1.0974 | -2.7376 | -2.6283 | 10.9935 | 10.6694 | 10.6694 | 10.5571 | 10.5842 | 10.369 | 10.1686 | 10.0906 | 9.7789 | 9.1714 | 6.2296 | 3.6526 | 2.0124 | 2.1217 | 349973 | 530340 | PENRITH & SHAP | HUTTON
| Norbreck | 18.2699 | 18.2072 | 18.1534 | 18.0457 | 17.9503 | 17.8097 | 17.6687 | 17.511 | 17.3614 | 17.1658 | 16.5758 | 16.3395 | 16.3729 | 16.5617 | 22.9069 | 22.8442 | 22.7904 | 22.6827 | 22.5873 | 22.4467 | 22.3057 | 22.148 | 21.9984 | 21.8028 | 21.2128 | 20.9765 | 21.0099 | 21.1987 | 18.3174 | 18.2949 | 18.2204 | 18.1252 | 18.0563 | 17.9457 | 17.8346 | 17.7079 | 17.5905 | 17.4579 | 17.0745 | 16.7917 | 16.6533 | 16.5935 | 22.9544 | 22.9319 | 22.8574 | 22.7622 | 22.6933 | 22.5827 | 22.4716 | 22.3449 | 22.2275 | 22.0949 | 21.7115 | 21.4287 | 21.2903 | 21.2305 | 18.271 | 18.213 | 18.164 | 18.0592 | 17.967 | 17.83 | 17.6921 | 17.5372 | 17.3935 | 17.2159 | 16.6912 | 16.4954 | 16.5408 | 16.7208 | 22.908 | 22.85 | 22.801 | 22.6962 | 22.604 | 22.467 | 22.3291 | 22.1742 | 22.0305 | 21.8529 | 21.3282 | 21.1324 | 21.1778 | 21.3578 | 18.2763 | 18.2211 | 18.1799 | 18.0889 | 18.0159 | 17.8978 | 17.7703 | 17.6311 | 17.5232 | 17.4017 | 16.5683 | 14.5768 | 13.0085 | 11.9409 | 22.9133 | 22.8581 | 22.8169 | 22.7259 | 22.6529 | 22.5348 | 22.4073 | 22.2681 | 22.1602 | 22.0387 | 21.2053 | 19.2138 | 17.6455 | 16.5779 | 18.2757 | 18.2057 | 18.1574 | 18.0703 | 17.9928 | 17.8831 | 17.7735 | 17.6586 | 17.5035 | 17.0111 | 14.785 | 12.9823 | 11.9734 | 12.3477 | 22.9127 | 22.8427 | 22.8427 | 22.7073 | 22.6298 | 22.5201 | 22.4105 | 22.2956 | 22.1405 | 21.6481 | 19.422 | 17.6193 | 16.6104 | 16.9847 | 331831 | 441463 | BISPHAM | PENWORTHAM
| Norbury | 11.5928 | 11.1634 | 10.9589 | 10.6447 | 10.2971 | 9.8509 | 9.3869 | 8.7834 | 8.2722 | 7.6147 | 5.8194 | 4.0966 | 4.0322 | 3.8264 | 16.2298 | 15.8004 | 15.5959 | 15.2817 | 14.9341 | 14.4879 | 14.0239 | 13.4204 | 12.9092 | 12.2517 | 10.4564 | 8.7336 | 8.6692 | 8.4634 | 11.8627 | 11.6411 | 11.3914 | 11.0918 | 10.8049 | 10.4401 | 10.086 | 9.6248 | 9.2478 | 8.8503 | 7.5259 | 6.8108 | 6.4301 | 6.3884 | 16.4997 | 16.2781 | 16.0284 | 15.7288 | 15.4419 | 15.0771 | 14.723 | 14.2618 | 13.8848 | 13.4873 | 12.1629 | 11.4478 | 11.0671 | 11.0254 | 11.5964 | 11.1706 | 10.9751 | 10.6651 | 10.324 | 9.8861 | 9.4133 | 8.8169 | 8.3212 | 7.7111 | 6.0695 | 4.4905 | 4.4731 | 4.5261 | 16.2334 | 15.8076 | 15.6121 | 15.3021 | 14.961 | 14.5231 | 14.0503 | 13.4539 | 12.9582 | 12.3481 | 10.7065 | 9.1275 | 9.1101 | 9.1631 | 11.618 | 11.2237 | 11.0751 | 10.84 | 10.5961 | 10.2779 | 9.9836 | 9.6055 | 9.3462 | 8.8193 | 3.0566 | 0.87447 | -1.1102 | -2.456 | 16.255 | 15.8607 | 15.7121 | 15.477 | 15.2331 | 14.9149 | 14.6206 | 14.2425 | 13.9832 | 13.4563 | 7.6936 | 5.5115 | 3.5268 | 2.181 | 11.5821 | 11.1135 | 10.9426 | 10.73 | 10.5099 | 10.1261 | 5.7731 | 5.6417 | 5.5717 | 5.2414 | 2.1454 | -0.72368 | -2.0791 | -1.1519 | 16.2191 | 15.7505 | 15.7505 | 15.367 | 15.1469 | 14.7631 | 10.4101 | 10.2787 | 10.2087 | 9.8784 | 6.7824 | 3.9133 | 2.5579 | 3.4851 | 392447 | 385492 | HAZEL GROVE | BREDBURY
| Northenden | 7.3994 | 6.9944 | 6.7167 | 6.5122 | 6.2074 | 5.8699 | 5.4612 | 5.0719 | 4.6765 | 4.192 | 2.2229 | 0.91805 | 0.3675 | -0.17769 | 10.8994 | 10.4944 | 10.2167 | 10.0122 | 9.7074 | 9.3699 | 8.9612 | 8.5719 | 8.1765 | 7.692 | 5.7229 | 4.418 | 3.8675 | 3.3223 | 7.5752 | 7.3324 | 7.0527 | 6.8561 | 6.5797 | 6.2734 | 5.8977 | 5.5401 | 5.1744 | 4.7736 | 3.3334 | 2.1539 | 1.4673 | 1.0363 | 11.0752 | 10.8324 | 10.5527 | 10.3561 | 10.0797 | 9.7734 | 9.3977 | 9.0401 | 8.6744 | 8.2736 | 6.8334 | 5.6539 | 4.9673 | 4.5363 | 7.4098 | 7.0181 | 6.7542 | 6.5605 | 6.2716 | 5.9517 | 5.5625 | 5.1928 | 4.8245 | 4.3916 | 2.6103 | 1.582 | 1.2456 | 1.2724 | 10.9098 | 10.5181 | 10.2542 | 10.0605 | 9.7716 | 9.4517 | 9.0625 | 8.6928 | 8.3245 | 7.8916 | 6.1103 | 5.082 | 4.7456 | 4.7724 | 7.397 | 6.9932 | 6.7195 | 6.5158 | 6.2288 | 5.9011 | 5.4753 | 5.0682 | 4.7032 | 4.3039 | 1.917 | -2.5549 | -6.7556 | -9.2963 | 10.897 | 10.4932 | 10.2195 | 10.0158 | 9.7288 | 9.4011 | 8.9753 | 8.5682 | 8.2032 | 7.8039 | 5.417 | 0.94508 | -3.2556 | -5.7963 | 7.4004 | 6.974 | 6.6983 | 6.5112 | 6.2297 | 5.9205 | 5.5196 | 5.141 | 4.7389 | 3.7937 | -0.65553 | -4.2859 | -6.5675 | -7.6352 | 10.9004 | 10.474 | 10.474 | 10.0112 | 9.7297 | 9.4205 | 9.0196 | 8.641 | 8.2389 | 7.2937 | 2.8445 | -0.78588 | -3.0675 | -4.1352 | 382555 | 390327 | WEST DIDSBURY | SOUTH MANCHESTER
| NWGB Partington | 10.8581 | 10.4837 | 10.2384 | 10.1409 | 10.0979 | 9.9614 | 9.8072 | 9.6676 | 8.3832 | 8.223 | 4.4327 | 1.4641 | 1.3693 | 0.99748 | 15.7981 | 15.4237 | 15.1784 | 15.0809 | 15.0379 | 14.9014 | 14.7472 | 14.6076 | 13.3232 | 13.163 | 9.3727 | 6.4041 | 6.3093 | 5.9375 | 11.0432 | 10.854 | 10.6632 | 10.5682 | 10.5286 | 10.4038 | 10.2605 | 10.1297 | 9.977 | 9.8367 | 9.2367 | 8.638 | 8.1619 | 7.7139 | 15.9832 | 15.794 | 15.6032 | 15.5082 | 15.4686 | 15.3438 | 15.2005 | 15.0697 | 14.917 | 14.7767 | 14.1767 | 13.578 | 13.1019 | 12.6539 | 10.8628 | 10.4736 | 10.236 | 10.1419 | 10.0939 | 9.9605 | 9.8185 | 9.6781 | 8.4018 | 8.2495 | 4.5613 | 1.8497 | 1.9204 | 1.7603 | 15.8028 | 15.4136 | 15.176 | 15.0819 | 15.0339 | 14.9005 | 14.7585 | 14.6181 | 13.3418 | 13.1895 | 9.5013 | 6.7897 | 6.8604 | 6.7003 | 10.8548 | 10.477 | 10.2254 | 10.1195 | 10.0709 | 9.9167 | 9.7218 | 9.5302 | 8.2262 | 8.0318 | -0.70988 | -7.3311 | -9.0284 | -10.3146 | 15.7948 | 15.417 | 15.1654 | 15.0595 | 15.0109 | 14.8567 | 14.6618 | 14.4702 | 13.1662 | 12.9718 | 4.2301 | -2.3911 | -4.0884 | -5.3746 | 10.8666 | 10.4774 | 10.2204 | 10.1143 | 7.0115 | 7.0372 | 7.0176 | 6.9651 | 5.7394 | 5.3614 | -5.0203 | -6.4982 | -7.6073 | -7.526 | 15.8066 | 15.4174 | 15.4174 | 15.0543 | 11.9515 | 11.9772 | 11.9576 | 11.9051 | 10.6794 | 10.3014 | -0.080257 | -1.5582 | -2.6673 | -2.586 | 372569 | 392079 | CARRINGTON BSP | CARRINGTON
| Offerton | 8.8126 | 8.7322 | 8.5179 | 8.3498 | 8.1647 | 7.9317 | 7.551 | 7.3124 | 7.0763 | 6.7039 | 5.486 | 4.9701 | 4.9216 | 5.1553 | 18.8126 | 18.7322 | 18.5179 | 18.3498 | 18.1647 | 17.9317 | 17.551 | 17.3124 | 17.0763 | 16.7039 | 15.486 | 14.9701 | 14.9216 | 15.1553 | 8.8645 | 8.8247 | 8.5786 | 8.4295 | 8.2822 | 8.0886 | 7.75 | 7.551 | 7.3493 | 7.0494 | 6.2424 | 5.7498 | 5.3865 | 5.3045 | 18.8645 | 18.8247 | 18.5786 | 18.4295 | 18.2822 | 18.0886 | 17.75 | 17.551 | 17.3493 | 17.0494 | 16.2424 | 15.7498 | 15.3865 | 15.3045 | 8.8171 | 8.7461 | 8.5427 | 8.3811 | 8.2037 | 7.9787 | 7.6071 | 7.3753 | 7.1155 | 6.8102 | 5.7333 | 5.3189 | 5.3025 | 5.4685 | 18.8171 | 18.7461 | 18.5427 | 18.3811 | 18.2037 | 17.9787 | 17.6071 | 17.3753 | 17.1155 | 16.8102 | 15.7333 | 15.3189 | 15.3025 | 15.4685 | 8.8216 | 8.7499 | 8.5498 | 8.3977 | 8.2395 | 8.0332 | 7.6786 | 7.4675 | 7.2971 | 7.0291 | 5.4247 | 1.8808 | -1.0588 | -2.7875 | 18.8216 | 18.7499 | 18.5498 | 18.3977 | 18.2395 | 18.0332 | 17.6786 | 17.4675 | 17.2971 | 17.0291 | 15.4247 | 11.8808 | 8.9412 | 7.2125 | 8.8247 | 8.7318 | 8.5254 | 8.3921 | 8.2578 | 8.0891 | 7.7693 | 7.601 | 7.3503 | 6.4369 | 2.3882 | -0.78145 | -2.7284 | -1.9431 | 18.8247 | 18.7318 | 18.7318 | 18.3921 | 18.2578 | 18.0891 | 17.7693 | 17.601 | 17.3503 | 16.4369 | 12.3882 | 9.2185 | 7.2716 | 8.0569 | 391010 | 389489 | VERNON PARK | BREDBURY
| Openshaw | 2.0172 | 1.4241 | 1.2792 | 1.0218 | 0.8584 | 0.40727 | 0.013846 | -0.33676 | -0.85361 | -1.4027 | -3.6801 | -5.1362 | -5.7545 | -5.9443 | 5.5172 | 4.9241 | 4.7792 | 4.5218 | 4.3584 | 3.9073 | 3.5138 | 3.1632 | 2.6464 | 2.0973 | -0.18006 | -1.6362 | -2.2545 | -2.4443 | 2.299 | 1.9407 | 1.6985 | 1.3954 | 1.2092 | 0.75968 | 0.35712 | -0.016108 | -0.54467 | -1.0419 | -2.6477 | -3.8818 | -4.7066 | -5.2563 | 5.799 | 5.4407 | 5.1985 | 4.8954 | 4.7092 | 4.2597 | 3.8571 | 3.4839 | 2.9553 | 2.4581 | 0.85225 | -0.38176 | -1.2066 | -1.7563 | 2.0343 | 1.4607 | 1.3325 | 1.091 | 0.9456 | 0.51631 | 0.14337 | -0.1976 | -0.68623 | -1.1837 | -3.2099 | -4.3769 | -4.8645 | -4.919 | 5.5343 | 4.9607 | 4.8325 | 4.591 | 4.4456 | 4.0163 | 3.6434 | 3.3024 | 2.8138 | 2.3163 | 0.29012 | -0.87691 | -1.3645 | -1.419 | 2.02 | 1.4256 | 1.2725 | 0.99573 | 0.82281 | 0.34607 | -0.10607 | -0.52583 | -1.0477 | -1.544 | -4.5304 | -10.8519 | -15.9878 | -19.4287 | 5.52 | 4.9256 | 4.7725 | 4.4957 | 4.3228 | 3.8461 | 3.3939 | 2.9742 | 2.4523 | 1.956 | -1.0304 | -7.3519 | -12.4878 | -15.9287 | 2.0452 | 1.4594 | 1.3208 | 1.0727 | 0.92421 | 0.48408 | 0.068698 | -0.31182 | -0.92419 | -2.4022 | -9.3679 | -15.335 | -18.7898 | -18.1846 | 5.5452 | 4.9594 | 4.9594 | 4.5727 | 4.4242 | 3.9841 | 3.5687 | 3.1882 | 2.5758 | 1.0978 | -5.8679 | -11.835 | -15.2898 | -14.6846 | 388606 | 397346 | DROYLSDEN | STALYBRIDGE
| Ormskirk | 8.6546 | 8.2199 | 8.0333 | 7.8346 | 7.5734 | 7.2623 | 6.9208 | 6.5934 | 6.2364 | 5.7869 | 4.105 | 3.214 | 2.9081 | 3.1417 | 13.2916 | 12.8569 | 12.6703 | 12.4716 | 12.2104 | 11.8993 | 11.5578 | 11.2304 | 10.8734 | 10.4239 | 8.742 | 7.851 | 7.5451 | 7.7787 | 8.9106 | 8.6901 | 8.4424 | 8.1985 | 7.9111 | 7.5819 | 7.2097 | 6.835 | 6.434 | 5.6748 | 5.0235 | 4.068 | 3.384 | 2.9726 | 13.5476 | 13.3271 | 13.0794 | 12.8355 | 12.5481 | 12.2189 | 11.8467 | 11.472 | 11.071 | 10.3118 | 9.6605 | 8.705 | 8.021 | 7.6096 | 8.6665 | 8.2523 | 8.0866 | 7.9053 | 7.6637 | 7.372 | 7.05 | 6.7414 | 6.4077 | 6.0125 | 4.5305 | 3.803 | 3.5779 | 3.8346 | 13.3035 | 12.8893 | 12.7236 | 12.5423 | 12.3007 | 12.009 | 11.687 | 11.3784 | 11.0447 | 10.6495 | 9.1675 | 8.44 | 8.2149 | 8.4716 | 8.6675 | 8.2407 | 8.0633 | 7.8674 | 7.6075 | 7.2826 | 6.8902 | 6.5131 | 6.1548 | 5.8023 | 3.9452 | 0.46919 | -2.0912 | -3.7545 | 13.3045 | 12.8777 | 12.7003 | 12.5044 | 12.2445 | 11.9196 | 11.5272 | 11.1501 | 10.7918 | 10.4393 | 8.5822 | 5.1062 | 2.5458 | 0.88249 | 8.658 | 8.2242 | 8.0722 | 7.9095 | 7.6519 | 7.3549 | 7.0192 | 6.7089 | 6.3337 | 5.4187 | 1.3141 | -1.785 | -3.408 | -2.7126 | 13.295 | 12.8612 | 12.8612 | 12.5465 | 12.2889 | 11.9919 | 11.6562 | 11.3459 | 10.9707 | 10.0557 | 5.9511 | 2.852 | 1.229 | 1.9244 | 341294 | 408158 | SKELMERSDALE | WASHWAY FARM
| Padiham | 15.3735 | 13.6231 | 12.9127 | 12.6347 | 12.3246 | 11.9124 | 11.4718 | 11.0133 | 10.5895 | 10.0747 | 8.2389 | 7.0853 | 6.7611 | 6.7502 | 22.3735 | 20.6231 | 19.9127 | 19.6347 | 19.3246 | 18.9124 | 18.4718 | 18.0133 | 17.5895 | 17.0747 | 15.2389 | 14.0853 | 13.7611 | 13.7502 | 16.4885 | 15.7558 | 15.1654 | 14.7986 | 14.4454 | 14.0357 | 13.5842 | 13.1085 | 12.6509 | 12.1768 | 10.7657 | 9.6002 | 8.913 | 8.5306 | 23.4885 | 22.7558 | 22.1654 | 21.7986 | 21.4454 | 21.0357 | 20.5842 | 20.1085 | 19.6509 | 19.1768 | 17.7657 | 16.6002 | 15.913 | 15.5306 | 15.3829 | 13.6471 | 12.9514 | 12.6864 | 12.3911 | 11.9943 | 11.5689 | 11.1253 | 10.7233 | 10.2558 | 8.6358 | 7.7961 | 7.6114 | 7.8015 | 22.3829 | 20.6471 | 19.9514 | 19.6864 | 19.3911 | 18.9943 | 18.5689 | 18.1253 | 17.7233 | 17.2558 | 15.6358 | 14.7961 | 14.6114 | 14.8015 | 15.4122 | 13.7005 | 13.0341 | 12.8052 | 12.5506 | 12.2 | 11.8066 | 11.3947 | 11.065 | 10.7097 | 8.3015 | 3.6111 | 0.41955 | -1.3678 | 22.4122 | 20.7005 | 20.0341 | 19.8052 | 19.5506 | 19.2 | 18.8066 | 18.3947 | 18.065 | 17.7097 | 15.3015 | 10.6111 | 7.4195 | 5.6322 | 15.427 | 13.7003 | 13.0342 | 12.8312 | 12.6012 | 12.2867 | 11.9229 | 11.5456 | 11.1333 | 9.9916 | 4.5883 | 0.38293 | -1.5334 | -0.31349 | 22.427 | 20.7003 | 20.7003 | 19.8312 | 19.6012 | 19.2867 | 18.9229 | 18.5456 | 18.1333 | 16.9916 | 11.5883 | 7.3829 | 5.4666 | 6.6865 | 378428 | 433238 | PADIHAM | PADIHAM
| Peel St & Ribblesdale T13 | 0.85744 | 0.50807 | 0.23457 | 0.0069749 | -0.24934 | -0.5366 | -0.85612 | -1.2196 | -2.8437 | -3.2747 | -5.5981 | -9.9405 | -10.3342 | -10.4869 | 10.6574 | 10.3081 | 10.0346 | 9.807 | 9.5507 | 9.2634 | 8.9439 | 8.5804 | 6.9563 | 6.5253 | 4.2019 | -0.14049 | -0.5342 | -0.68694 | 0.96283 | 0.71459 | 0.44339 | 0.22193 | -0.021054 | -0.29712 | -0.61727 | -1.0032 | -1.4093 | -1.8294 | -2.9491 | -3.7605 | -4.311 | -4.764 | 10.7628 | 10.5146 | 10.2434 | 10.0219 | 9.7789 | 9.5029 | 9.1827 | 8.7968 | 8.3907 | 7.9706 | 6.8509 | 6.0395 | 5.489 | 5.036 | 0.86361 | 0.52365 | 0.25997 | 0.042257 | -0.20284 | -0.47828 | -0.78593 | -1.1314 | -2.7287 | -3.1168 | -5.2661 | -9.5014 | -9.8565 | -9.9273 | 10.6636 | 10.3236 | 10.06 | 9.8423 | 9.5972 | 9.3217 | 9.0141 | 8.6686 | 7.0713 | 6.6832 | 4.5339 | 0.29864 | -0.056523 | -0.12734 | 0.85894 | 0.50749 | 0.23466 | 0.004382 | -0.24402 | -0.5251 | -0.84647 | -1.188 | -2.6931 | -3.0928 | -8.25 | -11.9196 | -14.188 | -15.7203 | 10.6589 | 10.3075 | 10.0347 | 9.8044 | 9.556 | 9.2749 | 8.9535 | 8.612 | 7.1069 | 6.7072 | 1.55 | -2.1196 | -4.388 | -5.9203 | 0.85803 | 0.48792 | 0.22341 | 0.019334 | -0.20484 | -0.46387 | -0.74715 | -1.1624 | -2.1632 | -2.8828 | -10.9129 | -13.7709 | -15.2479 | -14.9934 | 10.658 | 10.2879 | 10.2879 | 9.8193 | 9.5952 | 9.3361 | 9.0528 | 8.6376 | 7.6368 | 6.9172 | -1.1129 | -3.9709 | -5.4479 | -5.1934 | 374463 | 441514 | PADIHAM | PADIHAM
| Pendleton | 8.6023 | 7.7395 | 7.4386 | 7.2729 | 7.1267 | 6.772 | 6.4535 | 6.1919 | 5.8759 | 5.5513 | 3.9859 | 2.6083 | 1.5918 | 1.0384 | 13.2393 | 12.3765 | 12.0756 | 11.9099 | 11.7637 | 11.409 | 11.0905 | 10.8289 | 10.5129 | 10.1883 | 8.6229 | 7.2453 | 6.2288 | 5.6754 | 9.0118 | 8.5514 | 8.3028 | 8.061 | 7.8655 | 7.4779 | 7.143 | 6.8059 | 6.4773 | 6.0566 | 4.988 | 3.8951 | 2.9052 | 2.0573 | 13.6488 | 13.1884 | 12.9398 | 12.698 | 12.5025 | 12.1149 | 11.78 | 11.4429 | 11.1143 | 10.6936 | 9.625 | 8.5321 | 7.5422 | 6.6943 | 8.6106 | 7.765 | 7.4771 | 7.3233 | 7.1908 | 6.8519 | 6.5489 | 6.3022 | 6.0069 | 5.7208 | 4.3274 | 3.1803 | 2.3051 | 1.8985 | 13.2476 | 12.402 | 12.1141 | 11.9603 | 11.8278 | 11.4889 | 11.1859 | 10.9392 | 10.6439 | 10.3578 | 8.9644 | 7.8173 | 6.9421 | 6.5355 | 8.6151 | 7.7683 | 7.4774 | 7.3102 | 7.1609 | 6.781 | 6.3888 | 6.0426 | 5.6612 | 5.2828 | 3.0514 | -0.87261 | -3.9264 | -5.9585 | 13.2521 | 12.4053 | 12.1144 | 11.9472 | 11.7979 | 11.418 | 11.0258 | 10.6796 | 10.2982 | 9.9198 | 7.6884 | 3.7644 | 0.71062 | -1.3215 | 8.6354 | 7.7861 | 7.5005 | 7.341 | 7.1725 | 6.7318 | 6.36 | 6.0342 | 5.6278 | 4.8482 | 0.54356 | -3.1751 | -5.2699 | -5.0517 | 13.2724 | 12.4231 | 12.4231 | 11.978 | 11.8095 | 11.3688 | 10.997 | 10.6712 | 10.2648 | 9.4852 | 5.1806 | 1.4619 | -0.63291 | -0.41466 | 381161 | 398842 | FREDERICK RD | KEARSLEY
| Petteril Bank | 8.5084 | 8.2926 | 8.024 | 7.6701 | 7.3878 | 6.9044 | 6.3638 | 5.908 | 5.3206 | 4.676 | 2.2969 | 1.1739 | 0.94008 | 1.1956 | 12.6454 | 12.4296 | 12.161 | 11.8071 | 11.5248 | 11.0414 | 10.5008 | 10.045 | 9.4576 | 8.813 | 6.4339 | 5.3109 | 5.0771 | 5.3326 | 8.5657 | 8.4072 | 8.099 | 7.7895 | 7.5653 | 7.1396 | 6.6602 | 6.2658 | 5.8346 | 5.326 | 3.789 | 2.7025 | 2.0862 | 1.7358 | 12.7027 | 12.5442 | 12.236 | 11.9265 | 11.7023 | 11.2766 | 10.7972 | 10.4028 | 9.9716 | 9.463 | 7.926 | 6.8395 | 6.2232 | 5.8728 | 8.521 | 8.3258 | 8.0669 | 7.7318 | 7.4803 | 7.0185 | 6.4998 | 6.0637 | 5.5205 | 4.9378 | 2.8311 | 1.8569 | 1.6885 | 1.9778 | 12.658 | 12.4628 | 12.2039 | 11.8688 | 11.6173 | 11.1555 | 10.6368 | 10.2007 | 9.6575 | 9.0748 | 6.9681 | 5.9939 | 5.8255 | 6.1148 | 8.5075 | 8.2778 | 7.9817 | 7.5924 | 7.2965 | 6.7817 | 6.1827 | 5.6621 | 5.2039 | 4.6617 | 1.8517 | -3.3693 | -7.3656 | -10.3105 | 12.6445 | 12.4148 | 12.1187 | 11.7294 | 11.4335 | 10.9187 | 10.3197 | 9.7991 | 9.3409 | 8.7987 | 5.9887 | 0.76768 | -3.2286 | -6.1735 | 8.5538 | 8.3298 | 8.0464 | 7.6948 | 7.4455 | 7.0067 | 6.488 | 6.0635 | 5.5682 | 4.2561 | -1.909 | -6.563 | -9.2578 | -8.5852 | 12.6908 | 12.4668 | 12.4668 | 11.8318 | 11.5825 | 11.1437 | 10.625 | 10.2005 | 9.7052 | 8.3931 | 2.228 | -2.426 | -5.1208 | -4.4482 | 341768 | 553686 | CARLISLE | HARKER
| Phillips Lane | 3.3689 | 3.2642 | 3.2255 | 3.1468 | 3.0537 | 2.9275 | 2.7987 | 2.66 | 2.5073 | 2.3306 | 1.7443 | 1.4277 | 1.3685 | 1.4106 | 12.3689 | 12.2642 | 12.2255 | 12.1468 | 12.0537 | 11.9275 | 11.7987 | 11.66 | 11.5073 | 11.3306 | 10.7443 | 10.4277 | 10.3685 | 10.4106 | 3.4534 | 3.4118 | 3.3206 | 3.2113 | 3.1 | 2.9646 | 2.8159 | 2.6535 | 2.4844 | 2.3084 | 1.9281 | 1.6552 | 1.5271 | 1.4573 | 12.4534 | 12.4118 | 12.3206 | 12.2113 | 12.1 | 11.9646 | 11.8159 | 11.6535 | 11.4844 | 11.3084 | 10.9281 | 10.6552 | 10.5271 | 10.4573 | 3.3733 | 3.2731 | 3.2392 | 3.1656 | 3.0782 | 2.9584 | 2.8361 | 2.7103 | 2.5751 | 2.4175 | 1.8909 | 1.6346 | 1.5987 | 1.662 | 12.3733 | 12.2731 | 12.2392 | 12.1656 | 12.0782 | 11.9584 | 11.8361 | 11.7103 | 11.5751 | 11.4175 | 10.8909 | 10.6346 | 10.5987 | 10.662 | 3.3763 | 3.278 | 3.2443 | 3.1694 | 3.0787 | 2.9514 | 2.813 | 2.651 | 2.503 | 2.3517 | 1.4355 | -0.51407 | -1.9592 | -2.8616 | 12.3763 | 12.278 | 12.2443 | 12.1694 | 12.0787 | 11.9514 | 11.813 | 11.651 | 11.503 | 11.3517 | 10.4355 | 8.4859 | 7.0408 | 6.1384 | 3.379 | 3.2751 | 3.2449 | 3.1841 | 3.1081 | 3.0017 | 2.8844 | 2.7661 | 2.598 | 2.1084 | -0.10845 | -1.8402 | -2.7222 | -2.304 | 12.379 | 12.2751 | 12.2751 | 12.1841 | 12.1081 | 12.0017 | 11.8844 | 11.7661 | 11.598 | 11.1084 | 8.8916 | 7.1598 | 6.2778 | 6.696 | 387571 | 439522 | NELSON | PADIHAM
| Piccadilly | 12.7799 | 11.8561 | 11.6677 | 11.6164 | 11.526 | 11.3596 | 11.2329 | 11.1294 | 11.0151 | 10.8913 | 10.6225 | 10.5174 | 10.5738 | 10.6803 | 17.4169 | 16.4931 | 16.3047 | 16.2534 | 16.163 | 15.9966 | 15.8699 | 15.7664 | 15.6521 | 15.5283 | 15.2595 | 15.1544 | 15.2108 | 15.3173 | 13.3714 | 12.9871 | 12.7642 | 12.5839 | 12.3831 | 12.128 | 11.8915 | 11.664 | 11.3973 | 11.1041 | 10.7858 | 10.5887 | 10.565 | 10.6435 | 18.0084 | 17.6241 | 17.4012 | 17.2209 | 17.0201 | 16.765 | 16.5285 | 16.301 | 16.0343 | 15.7411 | 15.4228 | 15.2257 | 15.202 | 15.2805 | 12.7886 | 11.8756 | 11.6969 | 11.6565 | 11.5776 | 11.4241 | 11.3101 | 11.2197 | 11.1199 | 11.0132 | 10.7524 | 10.6525 | 10.7096 | 10.8159 | 17.4256 | 16.5126 | 16.3339 | 16.2935 | 16.2146 | 16.0611 | 15.9471 | 15.8567 | 15.7569 | 15.6502 | 15.3894 | 15.2895 | 15.3466 | 15.4529 | 12.8028 | 11.9034 | 11.7382 | 11.7108 | 11.643 | 11.501 | 11.3987 | 11.3196 | 11.2306 | 11.1372 | 10.9701 | 10.6933 | 10.5525 | 10.4161 | 17.4398 | 16.5404 | 16.3752 | 16.3478 | 16.28 | 16.138 | 16.0357 | 15.9566 | 15.8676 | 15.7742 | 15.6071 | 15.3303 | 15.1895 | 15.0531 | 12.8149 | 11.9265 | 11.7775 | 11.7697 | 11.7236 | 11.6064 | 11.5293 | 11.4783 | 11.4212 | 11.2858 | 10.8374 | 10.4697 | 10.2834 | 10.5997 | 17.4519 | 16.5635 | 16.5635 | 16.4067 | 16.3606 | 16.2434 | 16.1663 | 16.1153 | 16.0582 | 15.9228 | 15.4744 | 15.1067 | 14.9204 | 15.2367 | 384427 | 398261 | BLOOM ST | SOUTH MANCHESTER
| Pimbo | 9.4483 | 9.0533 | 9.0785 | 8.987 | 8.8002 | 8.3032 | 8.0613 | 7.8223 | 7.5914 | 7.3409 | 6.0855 | 5.0986 | 4.4955 | 3.8573 | 24.4483 | 24.0533 | 24.0785 | 23.987 | 23.8002 | 23.3032 | 23.0613 | 22.8223 | 22.5914 | 22.3409 | 21.0855 | 20.0986 | 19.4955 | 18.8573 | 9.9852 | 10.0045 | 9.8439 | 9.6329 | 9.3733 | 9.1091 | 8.8193 | 8.5246 | 8.2264 | 7.9271 | 7.0055 | 6.1658 | 5.5825 | 5.2614 | 24.9852 | 25.0045 | 24.8439 | 24.6329 | 24.3733 | 24.1091 | 23.8193 | 23.5246 | 23.2264 | 22.9271 | 22.0055 | 21.1658 | 20.5825 | 20.2614 | 9.4528 | 9.0619 | 9.0914 | 9.004 | 8.822 | 8.3306 | 8.0945 | 7.8614 | 7.6392 | 7.4072 | 6.4256 | 5.7513 | 5.2528 | 4.991 | 24.4528 | 24.0619 | 24.0914 | 24.004 | 23.822 | 23.3306 | 23.0945 | 22.8614 | 22.6392 | 22.4072 | 21.4256 | 20.7513 | 20.2528 | 19.991 | 9.4842 | 9.1256 | 9.1825 | 9.1168 | 8.9554 | 8.4801 | 8.2208 | 7.9451 | 7.6796 | 7.4056 | 5.2529 | 0.53494 | -3.2466 | -5.6245 | 24.4842 | 24.1256 | 24.1825 | 24.1168 | 23.9554 | 23.4801 | 23.2208 | 22.9451 | 22.6796 | 22.4056 | 20.2529 | 15.5349 | 11.7534 | 9.3755 | 9.489 | 9.1179 | 9.1688 | 9.1088 | 8.9527 | 8.473 | 8.1893 | 7.8789 | 7.5379 | 6.6497 | 1.5774 | -3.0015 | -5.5186 | -4.8965 | 24.489 | 24.1179 | 24.1179 | 24.1088 | 23.9527 | 23.473 | 23.1893 | 22.8789 | 22.5379 | 21.6497 | 16.5774 | 11.9985 | 9.4814 | 10.1035 | 349148 | 404549 | SKELMERSDALE | WASHWAY FARM
| Portwood | 3.8755 | 0.02965 | -2.4679 | -4.7227 | -6.484 | -9.4482 | -11.8516 | -1.9459 | -1.5774 | -1.8944 | -2.6897 | -2.9933 | -3.4975 | -3.4393 | 8.5125 | 4.6667 | 2.1691 | -0.085726 | -1.847 | -4.8112 | -7.2146 | -7.2459 | -6.8774 | -7.1944 | -7.9897 | -8.2933 | -8.7975 | -8.7393 | 4.5849 | 1.3232 | -1.2269 | -3.6378 | -5.5135 | -8.3942 | -10.8301 | -0.97937 | -1.0458 | -1.4797 | -1.864 | -2.3552 | -2.9215 | -2.8378 | 9.2219 | 5.9602 | 3.4101 | 0.99925 | -0.87651 | -3.7572 | -6.1931 | -6.2794 | -6.3458 | -6.7797 | -7.164 | -7.6552 | -8.2215 | -8.1378 | 3.8818 | 0.13144 | -2.4717 | -4.7264 | -6.4892 | -9.4482 | -11.8493 | -1.932 | -1.3579 | -1.639 | -2.538 | -2.6412 | -3.2499 | -3.1985 | 8.5188 | 4.7684 | 2.1653 | -0.089432 | -1.8522 | -4.8112 | -7.2123 | -7.232 | -6.6579 | -6.939 | -7.838 | -7.9412 | -8.5499 | -8.4985 | 3.9058 | 0.090406 | -2.381 | -4.6097 | -6.3565 | -9.3064 | -11.7172 | -1.8221 | -1.422 | -1.6932 | -2.6611 | -4.2827 | -6.2512 | -7.2128 | 8.5428 | 4.7274 | 2.256 | 0.02735 | -1.7195 | -4.6694 | -7.0802 | -7.1221 | -6.722 | -6.9932 | -7.9611 | -9.5827 | -11.5512 | -12.5128 | 3.8913 | 0.079467 | -2.4345 | -4.653 | -6.3954 | -9.3221 | -11.6985 | -1.754 | -1.2197 | -1.7908 | -4.1882 | -5.4394 | -6.8856 | -6.2838 | 8.5283 | 4.7165 | 4.7165 | -0.015996 | -1.7584 | -4.6851 | -7.0615 | -7.054 | -6.5197 | -7.0908 | -9.4882 | -10.7394 | -12.1856 | -11.5838 | 389826 | 390619 | VERNON PARK | BREDBURY
| Poulton | 9.3126 | 8.87 | 8.6147 | 8.3409 | 8.1133 | 7.8638 | 7.525 | 7.1807 | 6.7192 | 6.2401 | 4.1757 | 2.8665 | 2.3948 | 2.2313 | 15.8526 | 15.41 | 15.1547 | 14.8809 | 14.6533 | 14.4038 | 14.065 | 13.7207 | 13.2592 | 12.7801 | 10.7157 | 9.4065 | 8.9348 | 8.7713 | 9.5841 | 9.3672 | 9.0583 | 8.6201 | 8.1754 | 7.6759 | 7.0693 | 6.4616 | 5.785 | 4.9919 | 4.3121 | 3.8617 | 3.6296 | 3.4446 | 16.1241 | 15.9072 | 15.5983 | 15.1601 | 14.7154 | 14.2159 | 13.6093 | 13.0016 | 12.325 | 11.5319 | 10.8521 | 10.4017 | 10.1696 | 9.9846 | 9.2824 | 8.8308 | 8.5835 | 8.3663 | 8.1163 | 7.8843 | 7.574 | 7.1622 | 6.7196 | 6.284 | 4.5771 | 3.5544 | 3.2265 | 3.216 | 15.8224 | 15.3708 | 15.1235 | 14.9063 | 14.6563 | 14.4243 | 14.114 | 13.7022 | 13.2596 | 12.824 | 11.1171 | 10.0944 | 9.7665 | 9.756 | 9.3301 | 8.9027 | 8.6462 | 8.3976 | 8.1433 | 7.8796 | 7.5183 | 7.142 | 6.803 | 6.4199 | 3.7939 | -0.60669 | -3.96 | -6.6105 | 15.8701 | 15.4427 | 15.1862 | 14.9376 | 14.6833 | 14.4196 | 14.0583 | 13.682 | 13.343 | 12.9599 | 10.3339 | 5.9333 | 2.58 | -0.070546 | 9.3192 | 8.8562 | 8.5894 | 8.3639 | 8.1077 | 7.8661 | 7.5227 | 7.172 | 6.7729 | 5.8663 | 0.91783 | -3.2765 | -5.8153 | -5.5241 | 15.8592 | 15.3962 | 15.3962 | 14.9039 | 14.6477 | 14.4061 | 14.0627 | 13.712 | 13.3129 | 12.4063 | 7.4578 | 3.2635 | 0.72471 | 1.0159 | 335679 | 439130 | BISPHAM | PENWORTHAM
| Poynton | 8.0585 | 7.5948 | 7.4174 | 7.1147 | 7.0024 | 6.7107 | 6.3332 | 6.2518 | 5.9442 | 5.5483 | 4.3137 | 3.4527 | 3.0012 | 2.8739 | 11.5585 | 11.0948 | 10.9174 | 10.6147 | 10.5024 | 10.2107 | 9.8332 | 9.7518 | 9.4442 | 9.0483 | 7.8137 | 6.9527 | 6.5012 | 6.3739 | 8.2118 | 7.8913 | 7.6959 | 7.3826 | 7.2691 | 6.9843 | 6.6101 | 6.5211 | 6.2052 | 5.8367 | 4.8914 | 4.0875 | 3.4115 | 3.0094 | 11.7118 | 11.3913 | 11.1959 | 10.8826 | 10.7691 | 10.4843 | 10.1101 | 10.0211 | 9.7052 | 9.3367 | 8.3914 | 7.5875 | 6.9115 | 6.5094 | 8.0627 | 7.6188 | 7.4592 | 7.1687 | 7.0703 | 6.7953 | 6.4358 | 6.3667 | 6.0805 | 5.7232 | 4.5858 | 3.8964 | 3.5186 | 3.4781 | 11.5627 | 11.1188 | 10.9592 | 10.6687 | 10.5703 | 10.2953 | 9.9358 | 9.8667 | 9.5805 | 9.2232 | 8.0858 | 7.3964 | 7.0186 | 6.9781 | 8.0696 | 7.6216 | 7.4627 | 7.171 | 7.0933 | 6.8367 | 6.4849 | 6.4261 | 6.175 | 5.8741 | 4.2459 | 0.7795 | -2.0108 | -3.7576 | 11.5696 | 11.1216 | 10.9627 | 10.671 | 10.5933 | 10.3367 | 9.9849 | 9.9261 | 9.675 | 9.3741 | 7.7459 | 4.2795 | 1.4892 | -0.25762 | 8.0572 | 7.5939 | 7.4476 | 7.1817 | 7.129 | 6.9061 | 6.5875 | 6.5616 | 6.2349 | 5.3944 | 1.7455 | -1.4157 | -3.3196 | -2.9254 | 11.5572 | 11.0939 | 11.0939 | 10.6817 | 10.629 | 10.4061 | 10.0875 | 10.0616 | 9.7349 | 8.8944 | 5.2455 | 2.0843 | 0.18042 | 0.57457 | 392096 | 383493 | HAZEL GROVE | BREDBURY
| Preesall | 11.9266 | 11.5218 | 11.1955 | 10.7675 | 10.498 | 10.0554 | 9.6078 | 9.1148 | 8.6609 | 7.9798 | 5.6763 | 4.5362 | 4.3373 | 4.8317 | 16.4266 | 16.0218 | 15.6955 | 15.2675 | 14.998 | 14.5554 | 14.1078 | 13.6148 | 13.1609 | 12.4798 | 10.1763 | 9.0362 | 8.8373 | 9.3317 | 12.095 | 11.8401 | 11.4972 | 11.1454 | 10.9496 | 10.5848 | 10.2131 | 9.7916 | 9.3854 | 8.9242 | 7.681 | 6.5172 | 5.7397 | 5.2217 | 16.595 | 16.3401 | 15.9972 | 15.6454 | 15.4496 | 15.0848 | 14.7131 | 14.2916 | 13.8854 | 13.4242 | 12.181 | 11.0172 | 10.2397 | 9.7217 | 11.9329 | 11.5431 | 11.2349 | 10.8313 | 10.5828 | 10.1642 | 9.7398 | 9.2703 | 8.8431 | 8.2326 | 6.1962 | 5.1758 | 5.0619 | 5.4956 | 16.4329 | 16.0431 | 15.7349 | 15.3313 | 15.0828 | 14.6642 | 14.2398 | 13.7703 | 13.3431 | 12.7326 | 10.6962 | 9.6758 | 9.5619 | 9.9956 | 11.942 | 11.5232 | 11.1848 | 10.7628 | 10.4791 | 9.9995 | 9.479 | 8.9109 | 8.4576 | 7.9486 | 6.0436 | 3.6829 | 2.602 | 1.6413 | 16.442 | 16.0232 | 15.6848 | 15.2628 | 14.9791 | 14.4995 | 13.979 | 13.4109 | 12.9576 | 12.4486 | 10.5436 | 8.1829 | 7.102 | 6.1413 | 11.9071 | 11.4345 | 11.0887 | 10.6663 | 10.3738 | 9.9246 | 9.4731 | 9.0073 | 8.6665 | 7.957 | 4.9228 | 3.1445 | 2.5744 | 3.0739 | 16.4071 | 15.9345 | 15.9345 | 15.1663 | 14.8738 | 14.4246 | 13.9731 | 13.5073 | 13.1665 | 12.457 | 9.4228 | 7.6445 | 7.0744 | 7.5739 | 336965 | 446547 | THORNTON | STANAH
| Preston East | 13.4609 | 12.258 | 11.739 | 11.7062 | 11.1838 | 10.952 | 10.637 | 10.3705 | 9.9157 | 9.5319 | 8.1548 | 6.7469 | 6.1173 | 5.4427 | 19.4609 | 18.258 | 17.739 | 17.7062 | 17.1838 | 16.952 | 16.637 | 16.3705 | 15.9157 | 15.5319 | 14.1548 | 12.7469 | 12.1173 | 11.4427 | 14.2573 | 13.7644 | 13.2872 | 13.1591 | 12.6223 | 12.3923 | 12.0733 | 11.7904 | 11.3187 | 10.925 | 9.9815 | 9.009 | 8.4217 | 7.9955 | 20.2573 | 19.7644 | 19.2872 | 19.1591 | 18.6223 | 18.3923 | 18.0733 | 17.7904 | 17.3187 | 16.925 | 15.9815 | 15.009 | 14.4217 | 13.9955 | 13.4659 | 12.2692 | 11.7563 | 11.7278 | 11.2143 | 10.9898 | 10.6826 | 10.4233 | 9.9823 | 9.6281 | 8.4444 | 7.5141 | 7.1048 | 6.8406 | 19.4659 | 18.2692 | 17.7563 | 17.7278 | 17.2143 | 16.9898 | 16.6826 | 16.4233 | 15.9823 | 15.6281 | 14.4444 | 13.5141 | 13.1048 | 12.8406 | 13.4941 | 12.3262 | 11.8421 | 11.8445 | 11.3633 | 11.1537 | 10.844 | 10.5685 | 10.102 | 9.7151 | 7.6814 | 4.9368 | 1.6535 | -0.50923 | 19.4941 | 18.3262 | 17.8421 | 17.8445 | 17.3633 | 17.1537 | 16.844 | 16.5685 | 16.102 | 15.7151 | 13.6814 | 10.9368 | 7.6535 | 5.4908 | 13.4582 | 12.2286 | 11.7174 | 11.7138 | 11.227 | 11.0087 | 10.6645 | 10.3516 | 9.8213 | 9.1783 | 6.1452 | 2.6422 | 0.20151 | 0.59889 | 19.4582 | 18.2286 | 18.2286 | 17.7138 | 17.227 | 17.0087 | 16.6645 | 16.3516 | 15.8213 | 15.1783 | 12.1452 | 8.6422 | 6.2015 | 6.5989 | 356777 | 432926 | PRESTON EAST | PENWORTHAM
| Preston Old Rd | 11.1718 | 10.9226 | 10.7668 | 10.5612 | 10.362 | 10.1219 | 9.8176 | 9.5191 | 9.2172 | 8.8195 | 7.6238 | 7.0974 | 7.1197 | 7.5235 | 15.8088 | 15.5596 | 15.4038 | 15.1982 | 14.999 | 14.7589 | 14.4546 | 14.1561 | 13.8542 | 13.4565 | 12.2608 | 11.7344 | 11.7567 | 12.1605 | 11.3652 | 11.2766 | 11.0669 | 10.857 | 10.6806 | 10.4712 | 10.1935 | 9.9175 | 9.6379 | 9.3273 | 8.5735 | 7.9625 | 7.6491 | 7.5485 | 16.0022 | 15.9136 | 15.7039 | 15.494 | 15.3176 | 15.1082 | 14.8305 | 14.5545 | 14.2749 | 13.9643 | 13.2105 | 12.5995 | 12.2861 | 12.1855 | 11.1776 | 10.9425 | 10.8016 | 10.6068 | 10.4193 | 10.1907 | 9.8977 | 9.6096 | 9.3251 | 8.9707 | 7.9234 | 7.4976 | 7.5593 | 7.9519 | 15.8146 | 15.5795 | 15.4386 | 15.2438 | 15.0563 | 14.8277 | 14.5347 | 14.2466 | 13.9621 | 13.6077 | 12.5604 | 12.1346 | 12.1963 | 12.5889 | 11.1885 | 10.9576 | 10.8287 | 10.6563 | 10.4974 | 10.2933 | 9.9973 | 9.7124 | 9.474 | 9.2078 | 7.4462 | 3.2354 | 0.026099 | -2.0121 | 15.8255 | 15.5946 | 15.4657 | 15.2933 | 15.1344 | 14.9303 | 14.6343 | 14.3494 | 14.111 | 13.8448 | 12.0832 | 7.8724 | 4.6631 | 2.6249 | 11.1842 | 10.9273 | 10.7978 | 10.6442 | 10.4787 | 10.2953 | 10.045 | 9.8181 | 9.4935 | 8.4469 | 3.7268 | -0.044045 | -2.0497 | -1.0726 | 15.8212 | 15.5643 | 15.5643 | 15.2812 | 15.1157 | 14.9323 | 14.682 | 14.4551 | 14.1305 | 13.0839 | 8.3638 | 4.593 | 2.5873 | 3.5644 | 332562 | 434929 | BLACKPOOL | PENWORTHAM
| Prestwich | 6.9497 | 6.2533 | 6.2442 | 5.7424 | 5.5229 | 4.8468 | 4.3284 | 3.769 | 3.2037 | 2.4676 | 0.41824 | -0.49622 | -0.70906 | -0.3323 | 11.5867 | 10.8903 | 10.8812 | 10.3794 | 10.1599 | 9.4838 | 8.9654 | 8.406 | 7.8407 | 7.1046 | 5.0552 | 4.1408 | 3.9279 | 4.3047 | 7.1092 | 6.5579 | 6.4494 | 5.9144 | 5.7637 | 5.1712 | 4.7091 | 4.2038 | 3.6966 | 3.0465 | 1.6267 | 0.65248 | 0.0080993 | -0.24019 | 11.7462 | 11.1949 | 11.0864 | 10.5514 | 10.4007 | 9.8082 | 9.3461 | 8.8408 | 8.3336 | 7.6835 | 6.2637 | 5.2895 | 4.6451 | 4.3968 | 6.961 | 6.3008 | 6.3316 | 5.8522 | 5.5912 | 4.9199 | 4.4041 | 3.8607 | 3.321 | 2.6498 | 0.79744 | 0.080494 | -0.073989 | 0.29949 | 11.598 | 10.9378 | 10.9686 | 10.4892 | 10.2282 | 9.5569 | 9.0411 | 8.4977 | 7.958 | 7.2868 | 5.4344 | 4.7175 | 4.563 | 4.9365 | 6.9688 | 6.2916 | 6.313 | 5.841 | 5.6758 | 5.0658 | 4.6032 | 4.1128 | 3.7055 | 3.1667 | 0.6449 | -4.2302 | -8.1269 | -10.6272 | 11.6058 | 10.9286 | 10.95 | 10.478 | 10.3128 | 9.7028 | 9.2402 | 8.7498 | 8.3425 | 7.8037 | 5.2819 | 0.40683 | -3.4899 | -5.9902 | 6.956 | 6.2361 | 6.2299 | 5.7979 | 5.6471 | 5.0979 | 4.7035 | 4.3083 | 3.8581 | 2.4918 | -3.3302 | -7.7061 | -10.2621 | -9.1985 | 11.593 | 10.8731 | 10.8731 | 10.4349 | 10.2841 | 9.7349 | 9.3405 | 8.9453 | 8.4951 | 7.1288 | 1.3068 | -3.0691 | -5.6251 | -4.5615 | 381392 | 404001 | AGECROFT | KEARSLEY
| Pringle St | 8.315 | 7.9451 | 7.9326 | 7.4934 | 7.5492 | 7.1352 | 6.9108 | 6.7253 | 6.3572 | 5.9548 | 4.8751 | 4.2439 | 3.4319 | 2.7592 | 15.875 | 15.5051 | 15.4926 | 15.0534 | 15.1092 | 14.6952 | 14.4708 | 14.2853 | 13.9172 | 13.5148 | 12.4351 | 11.8039 | 10.9919 | 10.3192 | 8.4411 | 8.1706 | 8.0734 | 7.6119 | 7.6604 | 7.2533 | 7.0271 | 6.8336 | 6.4492 | 6.0625 | 5.3462 | 4.8171 | 4.4509 | 4.396 | 16.0011 | 15.7306 | 15.6334 | 15.1719 | 15.2204 | 14.8133 | 14.5871 | 14.3936 | 14.0092 | 13.6225 | 12.9062 | 12.3771 | 12.0109 | 11.956 | 8.329 | 7.9744 | 7.9734 | 7.5516 | 7.6172 | 7.2217 | 7.0117 | 6.8397 | 6.4936 | 6.1285 | 5.1527 | 4.616 | 4.378 | 4.5375 | 15.889 | 15.5344 | 15.5334 | 15.1116 | 15.1772 | 14.7817 | 14.5717 | 14.3997 | 14.0536 | 13.6885 | 12.7127 | 12.176 | 11.938 | 12.0975 | 8.3143 | 7.9416 | 7.9239 | 7.4747 | 7.5226 | 7.0947 | 6.8466 | 6.6291 | 6.2618 | 5.8968 | 4.1413 | -0.09911 | -3.7598 | -6.2608 | 15.8743 | 15.5016 | 15.4839 | 15.0347 | 15.0826 | 14.6547 | 14.4066 | 14.1891 | 13.8218 | 13.4568 | 11.7013 | 7.4609 | 3.8002 | 1.2992 | 8.328 | 7.9608 | 7.9634 | 7.5583 | 7.6541 | 7.2875 | 7.087 | 6.923 | 6.5084 | 5.3956 | 0.73514 | -3.0976 | -5.5997 | -5.0399 | 15.888 | 15.5208 | 15.5208 | 15.1183 | 15.2141 | 14.8475 | 14.647 | 14.483 | 14.0684 | 12.9556 | 8.2951 | 4.4624 | 1.9603 | 2.5201 | 369088 | 427387 | BLACKBURN | PENWORTHAM
| Queens Park | 4.0555 | 3.1503 | -0.097086 | -5.9619 | -11.6923 | -17.5393 | -23.5671 | 1.1082 | 0.7643 | 0.11628 | -1.8257 | -3.4911 | -4.5425 | -5.2003 | 5.8555 | 4.9503 | 1.7029 | -4.1619 | -9.8923 | -15.7393 | -21.7671 | -22.0918 | -22.4357 | -23.0837 | -25.0257 | -26.6911 | -27.7425 | -28.4003 | 4.5895 | 4.1763 | 0.9658 | -4.9186 | -10.6474 | -16.4675 | -22.4709 | -3.7789 | -4.1053 | -4.6665 | -5.9318 | -7.1401 | -8.108 | -8.7499 | 6.3895 | 5.9763 | 2.7658 | -3.1186 | -8.8474 | -14.6675 | -20.6709 | -20.9789 | -21.3053 | -21.8665 | -23.1318 | -24.3401 | -25.308 | -25.9499 | 4.067 | 3.1759 | -0.056525 | -5.9083 | -11.6234 | -17.4546 | -23.4657 | -4.7747 | -5.0963 | -5.6946 | -7.3703 | -8.6079 | -9.4432 | -9.8182 | 5.867 | 4.9759 | 1.7435 | -4.1083 | -9.8234 | -15.6546 | -21.6657 | -21.9747 | -22.2963 | -22.8946 | -24.5703 | -25.8079 | -26.6432 | -27.0182 | 4.0628 | 3.1588 | -0.095505 | -5.9797 | -11.7307 | -17.6287 | -23.7585 | -5.2127 | -5.6596 | -6.3624 | -9.3607 | -14.4109 | -18.1971 | -20.81 | 5.8628 | 4.9588 | 1.7045 | -4.1797 | -9.9307 | -15.8287 | -21.9585 | -22.4127 | -22.8596 | -23.5624 | -26.5607 | -31.6109 | -35.3971 | -38.01 | 4.0716 | 3.1526 | -0.10689 | -5.9843 | -11.7414 | -17.6373 | -23.762 | -5.2127 | -5.7261 | -7.0911 | -12.6142 | -17.2238 | -20.0495 | -19.5523 | 5.8716 | 4.9526 | 4.9526 | -4.1843 | -9.9414 | -15.8373 | -21.962 | -22.4127 | -22.9261 | -24.2911 | -29.8142 | -34.4238 | -37.2495 | -36.7523 | 385893 | 400645 | STUART ST | STALYBRIDGE
| Radcliffe | 10.2551 | 8.5023 | 8.391 | 7.0166 | 6.651 | 5.2972 | 4.0409 | 3.0408 | 1.4401 | 0.035633 | -5.0357 | -7.0026 | -7.3478 | -6.7042 | 17.2551 | 15.5023 | 15.391 | 14.0166 | 13.651 | 12.2972 | 11.0409 | 10.0408 | 8.4401 | 7.0356 | 1.9643 | -0.0025578 | -0.34781 | 0.29583 | 10.9642 | 9.8366 | 9.559 | 8.3126 | 8.1337 | 7.0074 | 5.963 | 5.1495 | 3.7444 | 2.6294 | -0.5921 | -2.5818 | -3.8374 | -4.1957 | 17.9642 | 16.8366 | 16.559 | 15.3126 | 15.1337 | 14.0074 | 12.963 | 12.1495 | 10.7444 | 9.6294 | 6.4079 | 4.4182 | 3.1626 | 2.8043 | 10.2718 | 8.5634 | 8.4856 | 7.0795 | 6.7318 | 5.4125 | 4.1868 | 3.2114 | 1.6637 | 0.38394 | -4.2348 | -5.8459 | -6.0199 | -5.2428 | 17.2718 | 15.5634 | 15.4856 | 14.0795 | 13.7318 | 12.4125 | 11.1868 | 10.2114 | 8.6637 | 7.3839 | 2.7652 | 1.1541 | 0.98009 | 1.7572 | 10.309 | 8.6185 | 8.5901 | 7.3708 | 7.1619 | 6.002 | 4.9275 | 4.1267 | 2.877 | 1.9623 | -4.2207 | -14.4186 | -21.8718 | -26.6398 | 17.309 | 15.6185 | 15.5901 | 14.3708 | 14.1619 | 13.002 | 11.9275 | 11.1267 | 9.877 | 8.9623 | 2.7793 | -7.4186 | -14.8718 | -19.6398 | 10.2413 | 8.3943 | 8.3048 | 6.9981 | 6.7853 | 5.3239 | 3.9719 | 3.3931 | 2.0599 | -0.42968 | -12.1979 | -21.0069 | -26.0949 | -23.6307 | 17.2413 | 15.3943 | 15.3943 | 13.9981 | 13.7853 | 12.3239 | 10.9719 | 10.3931 | 9.0599 | 6.5703 | -5.1979 | -14.0069 | -19.0949 | -16.6307 | 377524 | 406160 | - | KEARSLEY
| Randal St | 5.1312 | 4.8529 | 4.6555 | 4.2871 | 4.225 | 4.0359 | 3.6606 | 3.3651 | 3.0353 | 2.5266 | 1.1564 | 0.65266 | 0.59801 | 1.0094 | 17.8312 | 17.5529 | 17.3555 | 16.9871 | 16.925 | 16.7359 | 16.3606 | 16.0651 | 15.7353 | 15.2266 | 13.8564 | 13.3527 | 13.298 | 13.7094 | 5.4576 | 5.393 | 5.1128 | 4.6127 | 4.5484 | 4.2117 | 3.8649 | 3.5238 | 3.0815 | 2.5374 | 1.5197 | 0.92884 | 0.55132 | 0.54799 | 18.1576 | 18.093 | 17.8128 | 17.3127 | 17.2484 | 16.9117 | 16.5649 | 16.2238 | 15.7815 | 15.2374 | 14.2197 | 13.6288 | 13.2513 | 13.248 | 5.1423 | 4.8768 | 4.6957 | 4.3387 | 4.2977 | 4.1208 | 3.7694 | 3.4921 | 3.2176 | 2.7588 | 1.5276 | 1.0998 | 1.0651 | 1.3937 | 17.8423 | 17.5768 | 17.3957 | 17.0387 | 16.9977 | 16.8208 | 16.4694 | 16.1921 | 15.9176 | 15.4588 | 14.2276 | 13.7998 | 13.7651 | 14.0937 | 5.1505 | 4.89 | 4.7088 | 4.3447 | 4.304 | 4.1177 | 3.7553 | 3.4605 | 3.2426 | 2.8649 | 1.2552 | -2.5493 | -5.731 | -7.4677 | 17.8505 | 17.59 | 17.4088 | 17.0447 | 17.004 | 16.8177 | 16.4553 | 16.1605 | 15.9426 | 15.5649 | 13.9552 | 10.1507 | 6.969 | 5.2323 | 5.1558 | 4.8832 | 4.7124 | 4.406 | 4.379 | 4.2543 | 3.9358 | 3.7056 | 3.4583 | 2.5292 | -1.8344 | -5.3368 | -7.3604 | -6.2713 | 17.8558 | 17.5832 | 17.5832 | 17.106 | 17.079 | 16.9543 | 16.6358 | 16.4056 | 16.1583 | 15.2292 | 10.8656 | 7.3632 | 5.3396 | 6.4287 | 368092 | 428515 | BLACKBURN | PENWORTHAM
| Rawtenstall Rd | 9.808 | 9.4381 | 9.2071 | 8.9749 | 8.6741 | 8.3274 | 7.9592 | 7.5761 | 7.1746 | 6.7051 | 4.9927 | 3.93 | 3.4901 | 3.4063 | 14.445 | 14.0751 | 13.8441 | 13.6119 | 13.3111 | 12.9644 | 12.5962 | 12.2131 | 11.8116 | 11.3421 | 9.6297 | 8.567 | 8.1271 | 8.0433 | 9.9459 | 9.7071 | 9.4048 | 9.1275 | 8.8053 | 8.4352 | 8.0322 | 7.6037 | 7.133 | 6.5871 | 5.5118 | 4.5317 | 3.9081 | 3.4517 | 14.5829 | 14.3441 | 14.0418 | 13.7645 | 13.4423 | 13.0722 | 12.6692 | 12.2407 | 11.77 | 11.2241 | 10.1488 | 9.1687 | 8.5451 | 8.0887 | 9.8195 | 9.4797 | 9.265 | 9.0421 | 8.7629 | 8.4394 | 8.0945 | 7.7348 | 7.3635 | 6.9476 | 5.4175 | 4.5127 | 4.1443 | 4.1002 | 14.4565 | 14.1167 | 13.902 | 13.6791 | 13.3999 | 13.0764 | 12.7315 | 12.3718 | 12.0005 | 11.5846 | 10.0545 | 9.1497 | 8.7813 | 8.7372 | 9.814 | 9.453 | 9.2288 | 8.9984 | 8.7157 | 8.3811 | 7.9941 | 7.5883 | 7.2186 | 6.8492 | 4.0673 | -2.4353 | -7.6234 | -11.0807 | 14.451 | 14.09 | 13.8658 | 13.6354 | 13.3527 | 13.0181 | 12.6311 | 12.2253 | 11.8556 | 11.4862 | 8.7043 | 2.2017 | -2.9864 | -6.4437 | 9.8537 | 9.4967 | 9.2998 | 9.1071 | 8.854 | 8.5704 | 8.2498 | 7.918 | 7.4026 | 5.8886 | -1.2417 | -7.1425 | -10.5667 | -9.6994 | 14.4907 | 14.1337 | 14.1337 | 13.7441 | 13.491 | 13.2074 | 12.8868 | 12.555 | 12.0396 | 10.5256 | 3.3953 | -2.5055 | -5.9297 | -5.0624 | 379395 | 422143 | ROSSENDALE | PADIHAM
| Reddish Vale | 7.6243 | 7.5328 | 7.2372 | 6.891 | 6.6177 | 6.2607 | 5.7107 | 5.2861 | 4.8439 | 4.2717 | 2.4111 | 1.6119 | 1.48 | 1.8238 | 16.6243 | 16.5328 | 16.2372 | 15.891 | 15.6177 | 15.2607 | 14.7107 | 14.2861 | 13.8439 | 13.2717 | 11.4111 | 10.6119 | 10.48 | 10.8238 | 7.6714 | 7.6153 | 7.2593 | 6.9687 | 6.7509 | 6.4493 | 5.9265 | 5.6208 | 5.259 | 4.8298 | 3.5413 | 2.6794 | 2.1496 | 1.9047 | 16.6714 | 16.6153 | 16.2593 | 15.9687 | 15.7509 | 15.4493 | 14.9265 | 14.6208 | 14.259 | 13.8298 | 12.5413 | 11.6794 | 11.1496 | 10.9047 | 7.631 | 7.565 | 7.274 | 6.9413 | 6.6826 | 6.3411 | 5.7882 | 5.3762 | 4.9552 | 4.4365 | 2.7608 | 2.076 | 1.9797 | 2.3055 | 16.631 | 16.565 | 16.274 | 15.9413 | 15.6826 | 15.3411 | 14.7882 | 14.3762 | 13.9552 | 13.4365 | 11.7608 | 11.076 | 10.9797 | 11.3055 | 7.6296 | 7.5432 | 7.2606 | 6.9342 | 6.6969 | 6.3767 | 5.8518 | 5.4865 | 5.165 | 4.7813 | 2.3553 | -2.7978 | -6.9394 | -9.5722 | 16.6296 | 16.5432 | 16.2606 | 15.9342 | 15.6969 | 15.3767 | 14.8518 | 14.4865 | 14.165 | 13.7813 | 11.3553 | 6.2022 | 2.0606 | -0.57219 | 7.6479 | 7.5406 | 7.2375 | 6.9345 | 6.7127 | 6.4384 | 5.9741 | 5.6792 | 5.2646 | 3.9739 | -1.9458 | -6.5868 | -9.3115 | -8.3205 | 16.6479 | 16.5406 | 16.5406 | 15.9345 | 15.7127 | 15.4384 | 14.9741 | 14.6792 | 14.2646 | 12.9739 | 7.0542 | 2.4132 | -0.31145 | 0.67949 | 390147 | 393309 | VERNON PARK | BREDBURY
| Ribblesdale T14 | 2.6933 | 2.3665 | 2.072 | 1.7688 | 1.4366 | 1.0587 | 0.63832 | 0.13522 | -2.0019 | -2.5698 | -5.6433 | -11.3766 | -11.8883 | -12.0898 | 5.4933 | 5.1665 | 4.872 | 4.5688 | 4.2366 | 3.8587 | 3.4383 | 2.9352 | 0.79811 | 0.23022 | -2.8433 | -8.5766 | -9.0883 | -9.2898 | 2.7666 | 2.5075 | 2.1826 | 1.8875 | 1.5728 | 1.2098 | 0.77621 | 0.26825 | -0.26613 | -0.81964 | -2.2885 | -3.3724 | -4.0814 | -4.6773 | 5.5666 | 5.3075 | 4.9826 | 4.6875 | 4.3728 | 4.0098 | 3.5762 | 3.0683 | 2.5339 | 1.9804 | 0.51154 | -0.5724 | -1.2814 | -1.8773 | 2.7014 | 2.387 | 2.1054 | 1.8153 | 1.4977 | 1.1354 | 0.73064 | 0.25773 | -1.8453 | -2.3547 | -5.2042 | -10.8053 | -11.258 | -11.3517 | 5.5014 | 5.187 | 4.9054 | 4.6153 | 4.2977 | 3.9354 | 3.5306 | 3.0577 | 0.95471 | 0.44533 | -2.4042 | -8.0053 | -8.458 | -8.5517 | 2.6953 | 2.3657 | 2.0721 | 1.7654 | 1.4436 | 1.0739 | 0.65101 | 0.20151 | -1.7863 | -2.3236 | -9.1442 | -13.9893 | -16.9344 | -18.9507 | 5.4953 | 5.1657 | 4.8721 | 4.5654 | 4.2436 | 3.8739 | 3.451 | 3.0015 | 1.0137 | 0.47638 | -6.3442 | -11.1893 | -14.1344 | -16.1507 | 2.6941 | 2.34 | 2.0573 | 1.7851 | 1.4951 | 1.1544 | 0.7817 | 0.21634 | -1.1018 | -2.0474 | -12.6253 | -16.4292 | -18.3291 | -17.9942 | 5.4941 | 5.14 | 5.14 | 4.5851 | 4.2951 | 3.9544 | 3.5817 | 3.0163 | 1.6982 | 0.75264 | -9.8253 | -13.6292 | -15.5291 | -15.1942 | 374759 | 443587 | PADIHAM | PADIHAM
| Ribbleton | 13.9831 | 13.6646 | 13.7209 | 13.4154 | 13.4065 | 13.0947 | 12.9375 | 12.7476 | 12.5188 | 12.1167 | 10.8544 | 9.9006 | 9.2322 | 8.621 | 18.1201 | 17.8016 | 17.8579 | 17.5524 | 17.5435 | 17.2317 | 17.0745 | 16.8846 | 16.6558 | 16.2537 | 14.9914 | 14.0376 | 13.3692 | 12.758 | 14.0814 | 13.9041 | 13.8323 | 13.5583 | 13.5363 | 13.2317 | 13.0226 | 12.7773 | 12.5583 | 12.184 | 11.2733 | 10.5993 | 9.9704 | 9.6 | 18.2184 | 18.0411 | 17.9693 | 17.6953 | 17.6733 | 17.3687 | 17.1596 | 16.9143 | 16.6953 | 16.321 | 15.4103 | 14.7363 | 14.1074 | 13.737 | 13.9932 | 13.6868 | 13.7514 | 13.4567 | 13.4561 | 13.1569 | 13.0136 | 12.8175 | 12.6092 | 12.2287 | 11.127 | 10.4845 | 10.0365 | 9.7262 | 18.1302 | 17.8238 | 17.8884 | 17.5937 | 17.5931 | 17.2939 | 17.1506 | 16.9545 | 16.7462 | 16.3657 | 15.264 | 14.6215 | 14.1735 | 13.8632 | 13.9908 | 13.6772 | 13.7313 | 13.4147 | 13.3956 | 13.0517 | 12.8432 | 12.5838 | 12.2697 | 11.9077 | 9.881 | 6.0197 | 2.6877 | 0.48898 | 18.1278 | 17.8142 | 17.8683 | 17.5517 | 17.5326 | 17.1887 | 16.9802 | 16.7208 | 16.4067 | 16.0447 | 14.018 | 10.1567 | 6.8247 | 4.626 | 13.9975 | 13.6755 | 13.7286 | 13.4228 | 13.4156 | 13.0791 | 12.8641 | 12.6469 | 12.1936 | 11.3746 | 7.1133 | 3.5404 | 1.1405 | 1.3503 | 18.1345 | 17.8125 | 17.8125 | 17.5598 | 17.5526 | 17.2161 | 17.0011 | 16.7839 | 16.3306 | 15.5116 | 11.2503 | 7.6774 | 5.2775 | 5.4873 | 356730 | 431506 | PRESTON EAST | PENWORTHAM
| Ringley | 15.2761 | 15.2126 | 15.1263 | 15.0011 | 14.8893 | 14.7304 | 14.5376 | 14.3709 | 14.1934 | 13.9808 | 13.2039 | 12.7348 | 12.5493 | 12.518 | 19.2761 | 19.2126 | 19.1263 | 19.0011 | 18.8893 | 18.7304 | 18.5376 | 18.3709 | 18.1934 | 17.9808 | 17.2039 | 16.7348 | 16.5493 | 16.518 | 15.3487 | 15.3431 | 15.2277 | 15.1005 | 15.0019 | 14.8613 | 14.6862 | 14.5364 | 14.3716 | 14.1946 | 13.6484 | 13.2525 | 12.9836 | 12.8301 | 19.3487 | 19.3431 | 19.2277 | 19.1005 | 19.0019 | 18.8613 | 18.6862 | 18.5364 | 18.3716 | 18.1946 | 17.6484 | 17.2525 | 16.9836 | 16.8301 | 15.2806 | 15.2235 | 15.1441 | 15.0232 | 14.9165 | 14.7632 | 14.576 | 14.4143 | 14.245 | 14.052 | 13.362 | 13.0058 | 12.8686 | 12.9028 | 19.2806 | 19.2235 | 19.1441 | 19.0232 | 18.9165 | 18.7632 | 18.576 | 18.4143 | 18.245 | 18.052 | 17.362 | 17.0058 | 16.8686 | 16.9028 | 15.2828 | 15.2277 | 15.1528 | 15.0385 | 14.9437 | 14.8006 | 14.6169 | 14.4581 | 14.3119 | 14.1522 | 13.0365 | 10.7769 | 9.0312 | 7.5583 | 19.2828 | 19.2277 | 19.1528 | 19.0385 | 18.9437 | 18.8006 | 18.6169 | 18.4581 | 18.3119 | 18.1522 | 17.0365 | 14.7769 | 13.0312 | 11.5583 | 15.2968 | 15.2349 | 15.1535 | 15.0501 | 14.9672 | 14.8439 | 14.6769 | 14.538 | 14.352 | 13.834 | 11.3467 | 9.3167 | 7.8601 | 8.0821 | 19.2968 | 19.2349 | 19.2349 | 19.0501 | 18.9672 | 18.8439 | 18.6769 | 18.538 | 18.352 | 17.834 | 15.3467 | 13.3167 | 11.8601 | 12.0821 | 376120 | 405531 | KEARSLEY LOCAL | KEARSLEY
| Risley | 2.7169 | 1.7041 | 1.1966 | 0.93226 | 0.71765 | 0.44325 | 0.0385 | -0.41938 | -0.74173 | -1.19 | -3.0526 | -4.5154 | -5.3395 | -5.9608 | 13.4169 | 12.4041 | 11.8966 | 11.6323 | 11.4176 | 11.1432 | 10.7385 | 10.2806 | 9.9583 | 9.51 | 7.6474 | 6.1846 | 5.3605 | 4.7392 | 3.382 | 2.964 | 2.4924 | 2.2042 | 2 | 1.7711 | 1.4174 | 0.9874 | 0.73458 | 0.38561 | -0.8041 | -1.7465 | -2.4556 | -2.9769 | 14.082 | 13.664 | 13.1924 | 12.9042 | 12.7 | 12.4711 | 12.1174 | 11.6874 | 11.4346 | 11.0856 | 9.8959 | 8.9535 | 8.2444 | 7.7231 | 2.7246 | 1.7208 | 1.2229 | 0.96722 | 0.76393 | 0.50151 | 0.10957 | -0.33521 | -0.63992 | -1.0425 | -2.6519 | -3.7244 | -4.3529 | -4.7154 | 13.4246 | 12.4208 | 11.9229 | 11.6672 | 11.4639 | 11.2015 | 10.8096 | 10.3648 | 10.0601 | 9.6575 | 8.0481 | 6.9756 | 6.3471 | 5.9846 | 2.7248 | 1.7173 | 1.2081 | 0.9331 | 0.70366 | 0.39905 | -0.066322 | -0.60587 | -0.99758 | -1.4823 | -4.3909 | -9.5384 | -13.5723 | -16.3654 | 13.4248 | 12.4173 | 11.9081 | 11.6331 | 11.4037 | 11.0991 | 10.6337 | 10.0941 | 9.7024 | 9.2177 | 6.3091 | 1.1616 | -2.8723 | -5.6654 | 2.6955 | 1.6356 | 1.1059 | 0.82736 | 0.59758 | 0.29823 | -0.23469 | -0.77455 | -1.2325 | -2.4579 | -8.1282 | -12.7398 | -15.4756 | -15.154 | 13.3955 | 12.3356 | 12.3356 | 11.5274 | 11.2976 | 10.9982 | 10.4653 | 9.9255 | 9.4675 | 8.2421 | 2.5718 | -2.0398 | -4.7756 | -4.454 | 365181 | 392989 | - | BOLD
| Robert Hall St | 7.1816 | 6.2153 | 6.0453 | 5.7932 | 5.6712 | 5.2268 | 5.0332 | 4.6863 | 4.4246 | 3.9403 | 2.5327 | 1.4791 | 0.76141 | 0.53657 | 14.1816 | 13.2153 | 13.0453 | 12.7932 | 12.6712 | 12.2268 | 12.0332 | 11.6863 | 11.4246 | 10.9403 | 9.5327 | 8.4791 | 7.7614 | 7.5366 | 7.6195 | 7.1463 | 6.9715 | 6.6165 | 6.4861 | 6.0543 | 5.7685 | 5.3829 | 5.0784 | 4.6121 | 3.6508 | 2.6024 | 1.6206 | 0.9347 | 14.6195 | 14.1463 | 13.9715 | 13.6165 | 13.4861 | 13.0543 | 12.7685 | 12.3829 | 12.0784 | 11.6121 | 10.6508 | 9.6024 | 8.6206 | 7.9347 | 7.2303 | 6.1816 | 6.0242 | 5.8051 | 5.6707 | 5.2384 | 5.0506 | 4.713 | 4.4702 | 4.0312 | 2.7443 | 1.8053 | 1.156 | 0.93067 | 14.2303 | 13.1816 | 13.0242 | 12.8051 | 12.6707 | 12.2384 | 12.0506 | 11.713 | 11.4702 | 11.0312 | 9.7443 | 8.8053 | 8.156 | 7.9307 | 7.1928 | 6.2412 | 6.0775 | 5.8281 | 5.6897 | 5.2128 | 4.9289 | 4.4805 | 4.14 | 3.6858 | 1.8733 | -1.2876 | -3.7997 | -5.722 | 14.1928 | 13.2412 | 13.0775 | 12.8281 | 12.6897 | 12.2128 | 11.9289 | 11.4805 | 11.14 | 10.6858 | 8.8733 | 5.7124 | 3.2003 | 1.278 | 7.2109 | 6.24 | 6.0656 | 5.8289 | 5.6434 | 5.1511 | 4.8753 | 4.4565 | 4.1231 | 3.2379 | -0.33393 | -3.2213 | -5.0843 | -4.9748 | 14.2109 | 13.24 | 13.24 | 12.8289 | 12.6434 | 12.1511 | 11.8753 | 11.4565 | 11.1231 | 10.2379 | 6.6661 | 3.7787 | 1.9157 | 2.0252 | 381359 | 397718 | FREDERICK RD | KEARSLEY
| Rochdale Central | 18.0424 | 17.2904 | 16.5957 | 16.568 | 16.2302 | 15.4743 | 14.6153 | 14.0369 | 13.6278 | 12.6906 | 10.4332 | 8.8879 | 8.1526 | 7.7681 | 31.0424 | 30.2904 | 29.5957 | 29.568 | 29.2302 | 28.4743 | 27.6153 | 27.0369 | 26.6278 | 25.6906 | 23.4332 | 21.8879 | 21.1526 | 20.7681 | 18.6472 | 18.3366 | 17.6042 | 17.291 | 16.8414 | 16.0448 | 15.1244 | 14.4623 | 13.9368 | 12.9382 | 11.1882 | 9.7373 | 8.7281 | 7.9626 | 31.6472 | 31.3366 | 30.6042 | 30.291 | 29.8414 | 29.0448 | 28.1244 | 27.4623 | 26.9368 | 25.9382 | 24.1882 | 22.7373 | 21.7281 | 20.9626 | 18.0591 | 17.3259 | 16.6584 | 16.6473 | 16.3703 | 15.645 | 14.8187 | 14.2682 | 13.893 | 13.0325 | 10.9985 | 9.7416 | 9.1492 | 8.9093 | 31.0591 | 30.3259 | 29.6584 | 29.6473 | 29.3703 | 28.645 | 27.8187 | 27.2682 | 26.893 | 26.0325 | 23.9985 | 22.7416 | 22.1492 | 21.9093 | 18.0704 | 17.3433 | 16.6689 | 16.6467 | 16.401 | 15.5979 | 14.6886 | 14.2894 | 13.9979 | 13.1701 | 10.1069 | 3.6315 | -1.3904 | -4.7234 | 31.0704 | 30.3433 | 29.6689 | 29.6467 | 29.401 | 28.5979 | 27.6886 | 27.2894 | 26.9979 | 26.1701 | 23.1069 | 16.6315 | 11.6096 | 8.2766 | 18.0877 | 17.3529 | 16.6953 | 16.7204 | 16.5544 | 15.7936 | 14.9384 | 14.5693 | 14.2235 | 12.5448 | 5.509 | -0.31151 | -3.6886 | -2.883 | 31.0877 | 30.3529 | 30.3529 | 29.7204 | 29.5544 | 28.7936 | 27.9384 | 27.5693 | 27.2235 | 25.5448 | 18.509 | 12.6885 | 9.3114 | 10.117 | 389111 | 413393 | ROCHDALE CENTRAL | ROCHDALE
| Roman Rd | 6.0379 | 5.2204 | 5.2407 | 4.9866 | 4.9239 | 4.7738 | 4.601 | 4.616 | 4.3915 | 4.1462 | 3.5953 | 3.1416 | 2.7469 | 2.6527 | 13.0379 | 12.2204 | 12.2407 | 11.9866 | 11.9239 | 11.7738 | 11.601 | 11.616 | 11.3915 | 11.1462 | 10.5953 | 10.1416 | 9.7469 | 9.6527 | 6.6032 | 6.3042 | 6.2585 | 5.9244 | 5.8233 | 5.6705 | 5.4844 | 5.4597 | 5.22 | 4.9615 | 4.566 | 4.2368 | 3.8794 | 3.9003 | 13.6032 | 13.3042 | 13.2585 | 12.9244 | 12.8233 | 12.6705 | 12.4844 | 12.4597 | 12.22 | 11.9615 | 11.566 | 11.2368 | 10.8794 | 10.9003 | 6.0541 | 5.2254 | 5.2475 | 5.0237 | 4.9368 | 4.7901 | 4.6209 | 4.6509 | 4.4198 | 4.1876 | 3.7484 | 3.4582 | 3.1794 | 3.232 | 13.0541 | 12.2254 | 12.2475 | 12.0237 | 11.9368 | 11.7901 | 11.6209 | 11.6509 | 11.4198 | 11.1876 | 10.7484 | 10.4582 | 10.1794 | 10.232 | 6.0627 | 5.2732 | 5.3165 | 5.0721 | 5.0442 | 4.9082 | 4.7405 | 4.7021 | 4.526 | 4.2863 | 3.1331 | 0.60742 | -1.5843 | -2.7718 | 13.0627 | 12.2732 | 12.3165 | 12.0721 | 12.0442 | 11.9082 | 11.7405 | 11.7021 | 11.526 | 11.2863 | 10.1331 | 7.6074 | 5.4157 | 4.2282 | 6.0525 | 5.2494 | 5.2939 | 5.0613 | 5.0415 | 4.9151 | 4.7453 | 4.7155 | 4.4973 | 3.8995 | 1.1332 | -1.2317 | -2.6719 | -2.0831 | 13.0525 | 12.2494 | 12.2494 | 12.0613 | 12.0415 | 11.9151 | 11.7453 | 11.7155 | 11.4973 | 10.8995 | 8.1332 | 5.7683 | 4.3281 | 4.9169 | 369058 | 426505 | LOWER DARWEN | ROCHDALE
| Romiley | 2.7808 | 2.5641 | 2.291 | 1.8914 | 1.6631 | 1.2704 | 0.52778 | 0.2113 | -0.15511 | -0.80824 | -6.0478 | -6.8929 | -8.477 | -7.953 | 6.2808 | 6.0641 | 5.791 | 5.3914 | 5.1631 | 4.7704 | 4.0278 | 3.7113 | 3.3449 | 2.6918 | -2.5478 | -3.3929 | -4.977 | -4.453 | 2.9168 | 2.8122 | 2.448 | 2.0833 | 1.8609 | 1.5399 | 0.81705 | 0.52162 | 0.23364 | -0.35478 | -1.6551 | -2.6403 | -3.3772 | -3.6548 | 6.4168 | 6.3122 | 5.948 | 5.5833 | 5.3609 | 5.0399 | 4.3171 | 4.0216 | 3.7336 | 3.1452 | 1.8449 | 0.85966 | 0.12282 | -0.15481 | 2.7907 | 2.6026 | 2.3364 | 1.9726 | 1.7371 | 1.387 | 0.64696 | 0.33399 | 0.022026 | -0.59262 | -5.6499 | -6.3473 | -7.8443 | -7.3285 | 6.2907 | 6.1026 | 5.8364 | 5.4726 | 5.2371 | 4.887 | 4.147 | 3.834 | 3.522 | 2.9074 | -2.1499 | -2.8473 | -4.3443 | -3.8285 | 2.7958 | 2.5944 | 2.3432 | 1.975 | 1.7803 | 1.4411 | 0.6943 | -1.5277 | -1.6444 | -2.0493 | -7.8135 | -13.7871 | -18.291 | -21.3212 | 6.2958 | 6.0944 | 5.8432 | 5.475 | 5.2803 | 4.9411 | 4.1943 | 1.9723 | 1.8556 | 1.4507 | -4.3135 | -10.2871 | -14.791 | -17.8212 | 2.7996 | 2.5416 | 2.3107 | 1.9369 | 1.7913 | -3.1167 | -3.5354 | -3.3862 | -3.5207 | -4.8383 | -11.7617 | -17.0555 | -20.0601 | -18.749 | 6.2996 | 6.0416 | 6.0416 | 5.4369 | 5.2913 | 0.38334 | -0.035417 | 0.11375 | -0.02073 | -1.3383 | -8.2617 | -13.5555 | -16.5601 | -15.249 | 393626 | 390716 | VERNON PARK | BREDBURY
| Rossall | -0.42491 | -0.60152 | -0.58104 | -0.62475 | -0.67448 | -0.76292 | -0.83809 | -0.90434 | -0.99634 | -1.0648 | -1.3383 | -1.5351 | -1.5851 | -1.6353 | 6.0751 | 5.8985 | 5.919 | 5.8753 | 5.8255 | 5.7371 | 5.6619 | 5.5957 | 5.5037 | 5.4352 | 5.1617 | 4.9649 | 4.9149 | 4.8647 | -0.25984 | -0.30966 | -0.34373 | -0.42133 | -0.4909 | -0.58165 | -0.66466 | -0.74165 | -0.84713 | -0.94655 | -1.1533 | -1.344 | -1.4203 | -1.4782 | 6.2402 | 6.1903 | 6.1563 | 6.0787 | 6.0091 | 5.9183 | 5.8353 | 5.7583 | 5.6529 | 5.5534 | 5.3467 | 5.156 | 5.0797 | 5.0218 | -0.42396 | -0.59929 | -0.57794 | -0.62064 | -0.66918 | -0.75618 | -0.82995 | -0.89488 | -0.98468 | -1.0485 | -1.3014 | -1.46 | -1.4933 | -1.5141 | 6.076 | 5.9007 | 5.9221 | 5.8794 | 5.8308 | 5.7438 | 5.6701 | 5.6051 | 5.5153 | 5.4515 | 5.1986 | 5.04 | 5.0067 | 4.9859 | -0.41098 | -0.58025 | -0.54917 | -0.58222 | -0.62105 | -0.69837 | -0.76484 | -0.8234 | -0.90552 | -0.95734 | -1.3062 | -2.0317 | -2.5477 | -2.9575 | 6.089 | 5.9198 | 5.9508 | 5.9178 | 5.8789 | 5.8016 | 5.7352 | 5.6766 | 5.5945 | 5.5427 | 5.1938 | 4.4683 | 3.9523 | 3.5425 | -0.41307 | -0.58752 | -0.55766 | -0.58878 | -0.62532 | -0.69911 | -0.7636 | -0.81945 | -0.90843 | -1.0844 | -1.9066 | -2.5803 | -2.9684 | -2.7808 | 6.0869 | 5.9125 | 5.9125 | 5.9112 | 5.8747 | 5.8009 | 5.7364 | 5.6806 | 5.5916 | 5.4156 | 4.5934 | 3.9197 | 3.5316 | 3.7192 | 331916 | 445505 | THORNTON | STANAH
| Royton | 11.1731 | 10.8069 | 10.5663 | 10.2779 | 10.0252 | 9.6768 | 9.3509 | 8.9661 | 8.5537 | 8.1072 | 6.56 | 5.7024 | 5.4471 | 5.4974 | 15.8101 | 15.4439 | 15.2033 | 14.9149 | 14.6622 | 14.3138 | 13.9879 | 13.6031 | 13.1907 | 12.7442 | 11.197 | 10.3394 | 10.0841 | 10.1344 | 11.3007 | 11.0519 | 10.786 | 10.506 | 10.281 | 9.9615 | 9.6587 | 9.2968 | 8.8976 | 8.5116 | 7.3957 | 6.609 | 6.1343 | 5.8083 | 15.9377 | 15.6889 | 15.423 | 15.143 | 14.918 | 14.5985 | 14.2957 | 13.9338 | 13.5346 | 13.1486 | 12.0327 | 11.246 | 10.7713 | 10.4453 | 11.1824 | 10.8293 | 10.602 | 10.325 | 10.0844 | 9.7495 | 9.436 | 9.0642 | 8.6708 | 8.2664 | 6.8775 | 6.1557 | 5.9265 | 5.9565 | 15.8194 | 15.4663 | 15.239 | 14.962 | 14.7214 | 14.3865 | 14.073 | 13.7012 | 13.3078 | 12.9034 | 11.5145 | 10.7927 | 10.5635 | 10.5935 | 11.1773 | 10.814 | 10.58 | 10.2976 | 10.0632 | 9.7303 | 9.4076 | 9.0241 | 8.6649 | 8.3208 | 6.0359 | 0.84132 | -3.3508 | -6.2643 | 15.8143 | 15.451 | 15.217 | 14.9346 | 14.7002 | 14.3673 | 14.0446 | 13.6611 | 13.3019 | 12.9578 | 10.6729 | 5.4783 | 1.2862 | -1.6273 | 11.2097 | 10.8465 | 10.6171 | 10.3709 | 10.1777 | 9.9046 | 9.6381 | 9.3217 | 8.8755 | 7.6409 | 1.9027 | -2.8175 | -5.6277 | -4.9767 | 15.8467 | 15.4835 | 15.4835 | 15.0079 | 14.8147 | 14.5416 | 14.2751 | 13.9587 | 13.5125 | 12.2779 | 6.5397 | 1.8195 | -0.99069 | -0.33969 | 392426 | 407533 | ROYTON | WHITEGATE
| S.E. Macclesfield | 10.5428 | 9.9039 | 9.5235 | 9.1988 | 8.6873 | 8.2246 | 7.6578 | 7.0124 | 6.286 | 5.6638 | 3.0688 | 1.535 | 1.2134 | 1.3261 | 14.6798 | 14.0409 | 13.6605 | 13.3358 | 12.8243 | 12.3616 | 11.7948 | 11.1494 | 10.423 | 9.8008 | 7.2058 | 5.672 | 5.3504 | 5.4631 | 10.7994 | 10.3904 | 9.9643 | 9.6298 | 9.1275 | 8.6722 | 8.1666 | 7.5201 | 6.8734 | 6.3493 | 4.5189 | 2.961 | 2.1074 | 1.4872 | 14.9364 | 14.5274 | 14.1013 | 13.7668 | 13.2645 | 12.8092 | 12.3036 | 11.6571 | 11.0104 | 10.4863 | 8.6559 | 7.098 | 6.2444 | 5.6242 | 10.5556 | 9.9368 | 9.5764 | 9.2703 | 8.7822 | 8.3416 | 7.8234 | 7.1706 | 6.5414 | 5.9378 | 3.5818 | 2.3104 | 2.054 | 2.1925 | 14.6926 | 14.0738 | 13.7134 | 13.4073 | 12.9192 | 12.4786 | 11.9604 | 11.3076 | 10.6784 | 10.0748 | 7.7188 | 6.4474 | 6.191 | 6.3295 | 10.5546 | 9.92 | 9.5452 | 9.2208 | 8.7239 | 8.269 | 7.7488 | 7.1002 | 6.485 | 6.0581 | 3.1074 | -1.7388 | -4.9297 | -7.0345 | 14.6916 | 14.057 | 13.6822 | 13.3578 | 12.8609 | 12.406 | 11.8858 | 11.2372 | 10.622 | 10.1951 | 7.2444 | 2.3982 | -0.79267 | -2.8975 | 10.516 | 9.8364 | 9.4761 | 9.1834 | 8.7078 | 8.3009 | 7.7906 | 7.2452 | 6.5788 | 5.4557 | -0.22942 | -4.5042 | -6.478 | -5.6817 | 14.653 | 13.9734 | 13.9734 | 13.3204 | 12.8448 | 12.4379 | 11.9276 | 11.3822 | 10.7158 | 9.5927 | 3.9076 | -0.36716 | -2.341 | -1.5447 | 392001 | 372504 | MACCLESFIELD | MACCLESFIELD
| S.W. Macclesfield | 4.3901 | 3.62 | 3.0983 | 2.6798 | 1.8717 | 1.1835 | 0.38165 | -0.49593 | -1.134 | -2.2214 | -5.6913 | -7.749 | -8.1418 | -8.0269 | 8.5271 | 7.757 | 7.2353 | 6.8168 | 6.0087 | 5.3205 | 4.5186 | 3.6411 | 3.003 | 1.9156 | -1.5543 | -3.612 | -4.0048 | -3.8899 | 4.627 | 4.0786 | 3.5305 | 3.156 | 2.4454 | 1.8713 | 1.16 | 0.37289 | -0.18347 | -1.0457 | -3.4966 | -5.6351 | -6.6775 | -7.5566 | 8.764 | 8.2156 | 7.6675 | 7.293 | 6.5824 | 6.0083 | 5.297 | 4.5099 | 3.9535 | 3.0913 | 0.64044 | -1.4981 | -2.5405 | -3.4196 | 4.4052 | 3.6719 | 3.1858 | 2.787 | 1.9971 | 1.3436 | 0.57645 | -0.26649 | -0.85963 | -1.8442 | -4.934 | -6.7089 | -6.9921 | -6.8422 | 8.5422 | 7.8089 | 7.3228 | 6.924 | 6.1341 | 5.4806 | 4.7135 | 3.8705 | 3.2774 | 2.2928 | -0.79696 | -2.5719 | -2.8551 | -2.7052 | 4.4031 | 3.6365 | 3.1209 | 2.6951 | 1.9236 | 1.2601 | 0.46457 | -0.3942 | -0.91595 | -1.7451 | -5.7593 | -12.7623 | -17.457 | -20.8552 | 8.5401 | 7.7735 | 7.2579 | 6.8321 | 6.0606 | 5.3971 | 4.6016 | 3.7428 | 3.221 | 2.3919 | -1.6223 | -8.6253 | -13.32 | -16.7182 | 4.3747 | 3.5459 | 3.0353 | 2.6528 | 1.8996 | 1.3254 | 0.62728 | -0.10713 | -0.69041 | -2.5354 | -10.5002 | -16.7557 | -19.6767 | -18.7785 | 8.5117 | 7.6829 | 7.6829 | 6.7898 | 6.0366 | 5.4624 | 4.7643 | 4.0299 | 3.4466 | 1.6016 | -6.3632 | -12.6187 | -15.5397 | -14.6415 | 390968 | 373004 | MACCLESFIELD | MACCLESFIELD
| Sale | 11.441 | 10.7847 | 10.4891 | 10.4539 | 10.2734 | 9.6567 | 9.2866 | 9.1585 | 8.3741 | 7.9524 | 6.6071 | 5.8489 | 5.6781 | 5.7824 | 16.081 | 15.4247 | 15.1291 | 15.0939 | 14.9134 | 14.2967 | 13.9266 | 13.7985 | 13.0141 | 12.5924 | 11.2471 | 10.4889 | 10.3181 | 10.4224 | 11.5756 | 11.0045 | 10.6529 | 10.5974 | 10.4171 | 9.8022 | 9.3915 | 9.2448 | 8.4122 | 7.993 | 7.1666 | 6.3624 | 5.7433 | 5.4096 | 16.2156 | 15.6445 | 15.2929 | 15.2374 | 15.0571 | 14.4422 | 14.0315 | 13.8848 | 13.0522 | 12.633 | 11.8066 | 11.0024 | 10.3833 | 10.0496 | 11.4503 | 10.8281 | 10.5622 | 10.5418 | 10.38 | 9.7915 | 9.4361 | 9.3267 | 8.5787 | 8.2099 | 7.0061 | 6.3392 | 6.2187 | 6.3269 | 16.0903 | 15.4681 | 15.2022 | 15.1818 | 15.02 | 14.4315 | 14.0761 | 13.9667 | 13.2187 | 12.8499 | 11.6461 | 10.9792 | 10.8587 | 10.9669 | 11.4492 | 10.7996 | 10.5171 | 10.4925 | 10.3218 | 9.7067 | 9.3346 | 9.1769 | 8.4159 | 8.0734 | 6.4156 | 2.6055 | -0.41092 | -2.3417 | 16.0892 | 15.4396 | 15.1571 | 15.1325 | 14.9618 | 14.3467 | 13.9746 | 13.8169 | 13.0559 | 12.7134 | 11.0556 | 7.2455 | 4.2291 | 2.2983 | 11.4274 | 10.7399 | 10.4735 | 10.4924 | 10.3579 | 9.8024 | 9.4956 | 9.4136 | 8.6698 | 7.6748 | 3.4123 | -0.013485 | -2.0718 | -1.3129 | 16.0674 | 15.3799 | 15.3799 | 15.1324 | 14.9979 | 14.4424 | 14.1356 | 14.0536 | 13.3098 | 12.3148 | 8.0523 | 4.6265 | 2.5682 | 3.3271 | 378952 | 392177 | SALE | CARRINGTON
| Sale Moor | 1.7748 | 1.6535 | 1.4396 | 1.1506 | 1.0819 | 0.80283 | 0.45718 | 0.2674 | -0.053109 | -0.3451 | -1.3633 | -1.9054 | -1.9702 | -1.8844 | 1.7748 | 1.6535 | 1.4396 | 1.1506 | 1.0819 | 0.80283 | 0.45718 | 0.2674 | -0.053109 | -0.3451 | -1.3633 | -1.9054 | -1.9702 | -1.8844 | 1.8217 | 1.7386 | 1.4867 | 1.2178 | 1.1809 | 0.9326 | 0.61315 | 0.44505 | 0.14087 | -0.10511 | -0.84682 | -1.4019 | -1.6743 | -1.8587 | 1.8217 | 1.7386 | 1.4867 | 1.2178 | 1.1809 | 0.9326 | 0.61315 | 0.44505 | 0.14087 | -0.10511 | -0.84682 | -1.4019 | -1.6743 | -1.8587 | 1.7815 | 1.671 | 1.4695 | 1.19 | 1.1289 | 0.86009 | 0.52505 | 0.34292 | 0.036595 | -0.22483 | -1.1223 | -1.5956 | -1.648 | -1.5611 | 1.7815 | 1.671 | 1.4695 | 1.19 | 1.1289 | 0.86009 | 0.52505 | 0.34292 | 0.036595 | -0.22483 | -1.1223 | -1.5956 | -1.648 | -1.5611 | 1.781 | 1.6647 | 1.4581 | 1.1738 | 1.1175 | 0.84634 | 0.49883 | 0.30401 | 0.018685 | -0.20783 | -1.7198 | -5.2646 | -8.0365 | -10.0206 | 1.781 | 1.6647 | 1.4581 | 1.1738 | 1.1175 | 0.84634 | 0.49883 | 0.30401 | 0.018685 | -0.20783 | -1.7198 | -5.2646 | -8.0365 | -10.0206 | 1.7784 | 1.6397 | 1.4358 | 1.178 | 1.1542 | 0.92851 | 0.62358 | 0.47752 | 0.14528 | -0.69437 | -4.6165 | -7.8389 | -9.6834 | -9.1828 | 1.7784 | 1.6397 | 1.6397 | 1.178 | 1.1542 | 0.92851 | 0.62358 | 0.47752 | 0.14528 | -0.69437 | -4.6165 | -7.8389 | -9.6834 | -9.1828 | 379671 | 391133 | SALE | CARRINGTON
| Salford Quays | 9.7696 | 8.5296 | 8.1202 | 7.9569 | 7.895 | 7.5587 | 7.4589 | 7.2419 | 7.0907 | 6.8689 | 6.1787 | 5.7305 | 5.4275 | 5.2692 | 16.7696 | 15.5296 | 15.1202 | 14.9569 | 14.895 | 14.5587 | 14.4589 | 14.2419 | 14.0907 | 13.8689 | 13.1787 | 12.7305 | 12.4275 | 12.2692 | 10.4757 | 9.9155 | 9.5915 | 9.3316 | 9.2239 | 8.9309 | 8.7706 | 8.5627 | 8.3174 | 8.0585 | 7.4841 | 7.085 | 6.7568 | 6.6227 | 17.4757 | 16.9155 | 16.5915 | 16.3316 | 16.2239 | 15.9309 | 15.7706 | 15.5627 | 15.3174 | 15.0585 | 14.4841 | 14.085 | 13.7568 | 13.6227 | 9.7369 | 8.5007 | 8.0949 | 7.9456 | 7.8775 | 7.5466 | 7.4511 | 7.2391 | 7.0942 | 6.8855 | 6.2408 | 5.8496 | 5.5745 | 5.4446 | 16.7369 | 15.5007 | 15.0949 | 14.9456 | 14.8775 | 14.5466 | 14.4511 | 14.2391 | 14.0942 | 13.8855 | 13.2408 | 12.8496 | 12.5745 | 12.4446 | 9.7855 | 8.5614 | 8.1667 | 8.0188 | 7.9643 | 7.6391 | 7.5459 | 7.3336 | 7.1922 | 6.9955 | 6.1322 | 4.4931 | 3.0617 | 2.0897 | 16.7855 | 15.5614 | 15.1667 | 15.0188 | 14.9643 | 14.6391 | 14.5459 | 14.3336 | 14.1922 | 13.9955 | 13.1322 | 11.4931 | 10.0617 | 9.0897 | 9.7865 | 8.5562 | 8.1627 | 8.031 | 7.9809 | 7.6708 | 7.5886 | 7.3903 | 7.239 | 6.7809 | 4.8854 | 3.3349 | 2.2961 | 2.4897 | 16.7865 | 15.5562 | 15.5562 | 15.031 | 14.9809 | 14.6708 | 14.5886 | 14.3903 | 14.239 | 13.7809 | 11.8854 | 10.3349 | 9.2961 | 9.4897 | 380334 | 397555 | FREDERICK RD | KEARSLEY
| Sandgate | 9.3916 | 9.1067 | 8.9499 | 8.6596 | 8.5662 | 8.2376 | 7.8459 | 7.6259 | 7.2958 | 6.9014 | 5.6595 | 5.058 | 4.9554 | 5.2683 | 13.8916 | 13.6067 | 13.4499 | 13.1596 | 13.0662 | 12.7376 | 12.3459 | 12.1259 | 11.7958 | 11.4014 | 10.1595 | 9.558 | 9.4554 | 9.7683 | 9.5877 | 9.4676 | 9.2138 | 8.8806 | 8.7607 | 8.4144 | 7.9931 | 7.7331 | 7.3456 | 6.9435 | 6.185 | 5.6696 | 5.3873 | 5.3726 | 14.0877 | 13.9676 | 13.7138 | 13.3806 | 13.2607 | 12.9144 | 12.4931 | 12.2331 | 11.8456 | 11.4435 | 10.685 | 10.1696 | 9.8873 | 9.8726 | 9.4043 | 9.1644 | 8.9914 | 8.7186 | 8.6392 | 8.3288 | 7.9563 | 7.7517 | 7.4973 | 7.1429 | 6.0255 | 5.5314 | 5.4941 | 5.8252 | 13.9043 | 13.6644 | 13.4914 | 13.2186 | 13.1392 | 12.8288 | 12.4563 | 12.2517 | 11.9973 | 11.6429 | 10.5255 | 10.0314 | 9.9941 | 10.3252 | 9.3957 | 9.1112 | 8.9547 | 8.6676 | 8.5756 | 8.2445 | 7.8291 | 7.579 | 7.3169 | 7.0067 | 4.6506 | -1.5207 | -6.4747 | -9.4855 | 13.8957 | 13.6112 | 13.4547 | 13.1676 | 13.0756 | 12.7445 | 12.3291 | 12.079 | 11.8169 | 11.5067 | 9.1506 | 2.9793 | -1.9747 | -4.9855 | 9.4442 | 9.169 | 9.0439 | 8.808 | 8.7602 | 8.4933 | 8.1452 | 7.9674 | 7.5688 | 6.0861 | -0.76001 | -6.3238 | -9.5438 | -8.1341 | 13.9442 | 13.669 | 13.669 | 13.308 | 13.2602 | 12.9933 | 12.6452 | 12.4674 | 12.0688 | 10.5861 | 3.74 | -1.8238 | -5.0438 | -3.6341 | 321492 | 468870 | BARROW & SANDGATE | HARKER
| Scarisbrick | 0.75469 | 0.6525 | 0.59273 | 0.5137 | 0.41347 | 0.3066 | 0.16857 | 0.036921 | -0.14481 | -0.40678 | -1.3786 | -1.8842 | -2.0681 | -1.9132 | 2.2547 | 2.1525 | 2.0927 | 2.0137 | 1.9135 | 1.8066 | 1.6686 | 1.5369 | 1.3552 | 1.0932 | 0.1214 | -0.38419 | -0.56809 | -0.41315 | 0.83217 | 0.79288 | 0.70932 | 0.64393 | 0.55866 | 0.4704 | 0.35269 | 0.24876 | 0.12709 | -0.016474 | -0.52033 | -1.0238 | -1.4216 | -1.6626 | 2.3322 | 2.2929 | 2.2093 | 2.1439 | 2.0587 | 1.9704 | 1.8527 | 1.7488 | 1.6271 | 1.4835 | 0.97967 | 0.47622 | 0.078377 | -0.16263 | 0.75674 | 0.65943 | 0.60576 | 0.53509 | 0.4428 | 0.34368 | 0.2183 | 0.11164 | -0.067346 | -0.31473 | -1.2113 | -1.6196 | -1.7109 | -1.5253 | 2.2567 | 2.1594 | 2.1058 | 2.0351 | 1.9428 | 1.8437 | 1.7183 | 1.6116 | 1.4327 | 1.1853 | 0.28865 | -0.11959 | -0.21094 | -0.025311 | 0.75956 | 0.64931 | 0.57703 | 0.4857 | 0.35868 | 0.19302 | -0.016471 | -0.21167 | -0.40175 | -0.60144 | -1.5459 | -2.8647 | -3.6638 | -4.2779 | 2.2596 | 2.1493 | 2.077 | 1.9857 | 1.8587 | 1.693 | 1.4835 | 1.2883 | 1.0982 | 0.89856 | -0.04594 | -1.3647 | -2.1638 | -2.7779 | 0.75546 | 0.63406 | 0.55861 | 0.4651 | 0.32954 | 0.16195 | -0.033734 | -0.20718 | -0.37356 | -0.68416 | -2.2322 | -3.3492 | -3.8352 | -3.6905 | 2.2555 | 2.1341 | 2.1341 | 1.9651 | 1.8295 | 1.6619 | 1.4663 | 1.2928 | 1.1264 | 0.81584 | -0.73217 | -1.8492 | -2.3352 | -2.1905 | 338069 | 412086 | SKELMERSDALE | WASHWAY FARM
| Sebergham | 0.21906 | 0.13439 | 0.095952 | 0.0067219 | -0.066491 | -0.12496 | -0.2417 | -0.33326 | -0.43241 | -0.5432 | -1.0156 | -1.3995 | -1.6088 | -1.47 | 1.2191 | 1.1344 | 1.096 | 1.0067 | 0.93351 | 0.87504 | 0.7583 | 0.66674 | 0.56759 | 0.4568 | -0.015604 | -0.39946 | -0.60878 | -0.47001 | 0.32789 | 0.32889 | 0.24401 | 0.12831 | 0.03228 | -0.042586 | -0.18082 | -0.30012 | -0.42635 | -0.54054 | -0.80179 | -1.0919 | -1.3523 | -1.6371 | 1.3279 | 1.3289 | 1.244 | 1.1283 | 1.0323 | 0.95741 | 0.81918 | 0.69988 | 0.57365 | 0.45946 | 0.19821 | -0.091945 | -0.35229 | -0.63714 | 0.22282 | 0.14121 | 0.10685 | 0.022372 | -0.046152 | -0.10017 | -0.21114 | -0.29737 | -0.38985 | -0.49021 | -0.93282 | -1.1776 | -1.325 | -1.2549 | 1.2228 | 1.1412 | 1.1069 | 1.0224 | 0.95385 | 0.89983 | 0.78886 | 0.70263 | 0.61015 | 0.50979 | 0.067177 | -0.17757 | -0.32503 | -0.25488 | 0.22612 | 0.14372 | 0.10692 | 0.017769 | -0.063729 | -0.13629 | -0.2761 | -0.3909 | -0.50432 | -0.59934 | -1.0963 | -1.5797 | -1.8282 | -1.8715 | 1.2261 | 1.1437 | 1.1069 | 1.0178 | 0.93627 | 0.86371 | 0.7239 | 0.6091 | 0.49568 | 0.40066 | -0.096349 | -0.57972 | -0.82822 | -0.87146 | 0.22508 | 0.13631 | 0.099821 | 0.014007 | -0.07115 | -0.14107 | -0.27308 | -0.37719 | -0.47921 | -0.61745 | -1.2987 | -1.6996 | -1.8167 | -1.6163 | 1.2251 | 1.1363 | 1.1363 | 1.014 | 0.92885 | 0.85893 | 0.72692 | 0.62281 | 0.52079 | 0.38255 | -0.29875 | -0.69964 | -0.81673 | -0.6163 | 335344 | 542653 | CARLISLE | HARKER
| Sedbergh | 2.9542 | 2.8227 | 2.6595 | 2.457 | 2.3302 | 2.1099 | 1.8567 | 1.6103 | 1.342 | 0.95669 | -0.3267 | -0.98827 | -1.2289 | -1.0398 | 12.8334 | 12.7019 | 12.5387 | 12.3362 | 12.2094 | 11.9891 | 11.7359 | 11.4895 | 11.2212 | 10.8359 | 9.5525 | 8.8909 | 8.6503 | 8.8394 | 2.9829 | 2.8873 | 2.7001 | 2.5232 | 2.4238 | 2.2238 | 1.9908 | 1.7632 | 1.504 | 1.1467 | 0.51602 | -0.15753 | -0.69753 | -1.0269 | 12.8621 | 12.7665 | 12.5793 | 12.4024 | 12.303 | 12.103 | 11.87 | 11.6424 | 11.3832 | 11.0259 | 10.3952 | 9.7217 | 9.1817 | 8.8523 | 2.9628 | 2.8347 | 2.6809 | 2.4891 | 2.3703 | 2.1603 | 1.914 | 1.6682 | 1.4115 | 1.0603 | -0.11031 | -0.68407 | -0.87956 | -0.68839 | 12.842 | 12.7139 | 12.5601 | 12.3683 | 12.2495 | 12.0395 | 11.7932 | 11.5474 | 11.2907 | 10.9395 | 9.7689 | 9.1951 | 8.9996 | 9.1908 | 2.9557 | 2.8129 | 2.6402 | 2.4305 | 2.2833 | 2.0332 | 1.7368 | 1.4539 | 1.2007 | 0.9091 | -0.26101 | -1.7141 | -2.5466 | -3.0521 | 12.8349 | 12.6921 | 12.5194 | 12.3097 | 12.1625 | 11.9124 | 11.616 | 11.3331 | 11.0799 | 10.7883 | 9.6182 | 8.1651 | 7.3326 | 6.8271 | 2.9504 | 2.7797 | 2.6068 | 2.4085 | 2.2581 | 2.0233 | 1.7568 | 1.5154 | 1.2927 | 0.87065 | -0.90741 | -2.0622 | -2.5211 | -2.2684 | 12.8296 | 12.6589 | 12.6589 | 12.2877 | 12.1373 | 11.9025 | 11.636 | 11.3946 | 11.1719 | 10.7498 | 8.9718 | 7.817 | 7.3581 | 7.6108 | 365151 | 491747 | KENDAL (PARKSIDE RD) | HUTTON
| Selsmire | 1.8621 | 1.7425 | 1.727 | 1.6447 | 1.6442 | 1.5512 | 1.4729 | 1.4635 | 1.3626 | 1.2437 | 0.72081 | 0.35913 | 0.15648 | 0.15543 | 1.8621 | 1.7425 | 1.727 | 1.6447 | 1.6442 | 1.5512 | 1.4729 | 1.4635 | 1.3626 | 1.2437 | 0.72081 | 0.35913 | 0.15648 | 0.15543 | 1.8928 | 1.8013 | 1.7755 | 1.7002 | 1.7033 | 1.6156 | 1.5414 | 1.5334 | 1.4453 | 1.3756 | 1.1539 | 0.84441 | 0.55203 | 0.35745 | 1.8928 | 1.8013 | 1.7755 | 1.7002 | 1.7033 | 1.6156 | 1.5414 | 1.5334 | 1.4453 | 1.3756 | 1.1539 | 0.84441 | 0.55203 | 0.35745 | 1.8631 | 1.7481 | 1.7366 | 1.6587 | 1.6602 | 1.5703 | 1.4944 | 1.4859 | 1.3906 | 1.2867 | 0.81095 | 0.50705 | 0.34073 | 0.34874 | 1.8631 | 1.7481 | 1.7366 | 1.6587 | 1.6602 | 1.5703 | 1.4944 | 1.4859 | 1.3906 | 1.2867 | 0.81095 | 0.50705 | 0.34073 | 0.34874 | 1.8656 | 1.7437 | 1.7257 | 1.638 | 1.6228 | 1.5086 | 1.3997 | 1.3644 | 1.2502 | 1.1571 | 0.56622 | 0.20639 | 0.10123 | 0.089139 | 1.8656 | 1.7437 | 1.7257 | 1.638 | 1.6228 | 1.5086 | 1.3997 | 1.3644 | 1.2502 | 1.1571 | 0.56622 | 0.20639 | 0.10123 | 0.089139 | 1.8588 | 1.7265 | 1.7068 | 1.6196 | 1.5939 | 1.4766 | 1.3738 | 1.3483 | 1.2446 | 1.1274 | 0.56362 | 0.31993 | 0.32072 | 0.41779 | 1.8588 | 1.7265 | 1.7265 | 1.6196 | 1.5939 | 1.4766 | 1.3738 | 1.3483 | 1.2446 | 1.1274 | 0.56362 | 0.31993 | 0.32072 | 0.41779 | 361018 | 507505 | PENRITH & SHAP | HUTTON
| Settle | 0.60295 | 0.47032 | 0.44739 | 0.39323 | 0.32322 | 0.23895 | 0.14358 | 0.067944 | -0.016831 | -0.12498 | -0.49375 | -1.0484 | -1.4358 | -1.5039 | 8.103 | 7.9703 | 7.9474 | 7.8932 | 7.8232 | 7.7389 | 7.6436 | 7.5679 | 7.4832 | 7.375 | 7.0062 | 6.4516 | 6.0642 | 5.9961 | 0.70121 | 0.6449 | 0.55422 | 0.44961 | 0.33126 | 0.20496 | 0.056473 | -0.081622 | -0.23864 | -0.40701 | -0.64491 | -0.90193 | -1.1438 | -1.5348 | 8.2012 | 8.1449 | 8.0542 | 7.9496 | 7.8313 | 7.705 | 7.5565 | 7.4184 | 7.2614 | 7.093 | 6.8551 | 6.5981 | 6.3562 | 5.9652 | 0.60869 | 0.48225 | 0.46569 | 0.41818 | 0.35539 | 0.27865 | 0.19151 | 0.12383 | 0.048184 | -0.048839 | -0.40095 | -0.79377 | -1.1189 | -1.1611 | 8.1087 | 7.9822 | 7.9657 | 7.9182 | 7.8554 | 7.7786 | 7.6915 | 7.6238 | 7.5482 | 7.4512 | 7.099 | 6.7062 | 6.3811 | 6.3389 | 0.60962 | 0.47961 | 0.45838 | 0.40601 | 0.33178 | 0.23846 | 0.12645 | 0.032001 | -0.066757 | -0.16671 | -1.0668 | -2.5638 | -3.537 | -4.2647 | 8.1096 | 7.9796 | 7.9584 | 7.906 | 7.8318 | 7.7385 | 7.6264 | 7.532 | 7.4332 | 7.3333 | 6.4332 | 4.9362 | 3.963 | 3.2353 | 0.62291 | 0.50444 | 0.49517 | 0.45557 | 0.39095 | 0.31021 | 0.21411 | 0.13637 | 0.051548 | -0.20838 | -2.0009 | -3.3355 | -3.9953 | -3.8746 | 8.1229 | 8.0044 | 8.0044 | 7.9556 | 7.891 | 7.8102 | 7.7141 | 7.6364 | 7.5515 | 7.2916 | 5.4991 | 4.1645 | 3.5047 | 3.6254 | 381588 | 463721 | PADIHAM | PADIHAM
| Shannon St South | 6.9048 | 6.6016 | 6.5346 | 6.19 | 6.0159 | 5.6166 | 5.258 | 4.8778 | 4.4208 | 3.8818 | 2.0544 | 0.8308 | 0.34913 | 0.47349 | 12.4048 | 12.1016 | 12.0346 | 11.69 | 11.5159 | 11.1166 | 10.758 | 10.3778 | 9.9208 | 9.3818 | 7.5544 | 6.3308 | 5.8491 | 5.9735 | 6.9586 | 6.6819 | 6.4728 | 6.0729 | 5.8488 | 5.3814 | 4.9329 | 4.4448 | 3.8544 | 2.7986 | 2.1001 | 1.0567 | 0.44029 | 0.096927 | 12.4586 | 12.1819 | 11.9728 | 11.5729 | 11.3488 | 10.8814 | 10.4329 | 9.9448 | 9.3544 | 8.2986 | 7.6001 | 6.5567 | 5.9403 | 5.5969 | 6.9178 | 6.6489 | 6.6145 | 6.3007 | 6.1532 | 5.7859 | 5.4581 | 5.1098 | 4.6963 | 4.2288 | 2.5428 | 1.5453 | 1.2643 | 1.4726 | 12.4178 | 12.1489 | 12.1145 | 11.8007 | 11.6532 | 11.2859 | 10.9581 | 10.6098 | 10.1963 | 9.7288 | 8.0428 | 7.0453 | 6.7643 | 6.9726 | 6.8986 | 6.5927 | 6.5357 | 6.1988 | 6.0171 | 5.5992 | 5.1786 | 4.7338 | 4.272 | 3.8104 | 0.93722 | -6.0157 | -11.3222 | -14.7767 | 12.3986 | 12.0927 | 12.0357 | 11.6988 | 11.5171 | 11.0992 | 10.6786 | 10.2338 | 9.772 | 9.3104 | 6.4372 | -0.51572 | -5.8222 | -9.2767 | 6.8989 | 6.5797 | 6.5865 | 6.3437 | 6.2199 | 5.8786 | 5.5479 | 5.1977 | 4.7053 | 3.0806 | -4.307 | -10.6155 | -14.291 | -13.3126 | 12.3989 | 12.0797 | 12.0797 | 11.8437 | 11.7199 | 11.3786 | 11.0479 | 10.6977 | 10.2053 | 8.5806 | 1.193 | -5.1155 | -8.791 | -7.8126 | 330806 | 435291 | BLACKPOOL | PENWORTHAM
| Shap | 4.3105 | 4.1808 | 4.1988 | 4.201 | 4.1079 | 4.0529 | 3.9664 | 3.9673 | 3.8797 | 3.8085 | 1.5721 | -0.75113 | -0.96411 | -1.1555 | 7.1105 | 6.9808 | 6.9988 | 7.001 | 6.9079 | 6.8529 | 6.7664 | 6.7673 | 6.6797 | 6.6085 | 4.3721 | 2.0489 | 1.8359 | 1.6445 | 4.3893 | 4.3228 | 4.302 | 4.2776 | 4.1659 | 4.0986 | 3.9962 | 3.977 | 3.8644 | 3.7718 | 3.6411 | 3.4862 | 3.3824 | 3.3052 | 7.1893 | 7.1228 | 7.102 | 7.0776 | 6.9659 | 6.8986 | 6.7962 | 6.777 | 6.6644 | 6.5718 | 6.4411 | 6.2862 | 6.1824 | 6.1052 | 4.3128 | 4.1862 | 4.2062 | 4.2104 | 4.1209 | 4.069 | 3.9861 | 3.9891 | 3.9061 | 3.8415 | 1.6223 | -0.63582 | -0.74959 | -0.88392 | 7.1128 | 6.9862 | 7.0062 | 7.0104 | 6.9209 | 6.869 | 6.7861 | 6.7891 | 6.7061 | 6.6415 | 4.4223 | 2.1642 | 2.0504 | 1.9161 | 4.3159 | 4.1915 | 4.2149 | 4.2219 | 4.133 | 4.0791 | 3.9905 | 3.9572 | 3.8942 | 3.8137 | 3.2608 | -0.27356 | -0.91819 | -1.3028 | 7.1159 | 6.9915 | 7.0149 | 7.0219 | 6.933 | 6.8791 | 6.7905 | 6.7572 | 6.6942 | 6.6137 | 6.0608 | 2.5264 | 1.8818 | 1.4972 | 4.3166 | 4.1904 | 4.2149 | 4.2252 | 4.1395 | 4.0881 | 2.6797 | 2.6947 | 2.6891 | 2.5527 | 0.41396 | -0.5347 | -0.96162 | -0.84708 | 7.1166 | 6.9904 | 6.9904 | 7.0252 | 6.9395 | 6.8881 | 5.4797 | 5.4947 | 5.4891 | 5.3527 | 3.214 | 2.2653 | 1.8384 | 1.9529 | 356910 | 513357 | PENRITH & SHAP | HUTTON
| Shaw | 9.785 | 9.4886 | 9.3054 | 8.9672 | 8.6675 | 8.2813 | 7.9544 | 7.5246 | 7.0565 | 6.487 | 4.4094 | 3.2957 | 2.9611 | 2.9703 | 14.422 | 14.1256 | 13.9424 | 13.6042 | 13.3045 | 12.9183 | 12.5914 | 12.1616 | 11.6935 | 11.124 | 9.0464 | 7.9327 | 7.5981 | 7.6073 | 9.9046 | 9.7075 | 9.4611 | 9.1202 | 8.8463 | 8.4948 | 8.1979 | 7.7993 | 7.3569 | 6.9264 | 5.6176 | 4.5355 | 3.8492 | 3.3946 | 14.5416 | 14.3445 | 14.0981 | 13.7572 | 13.4833 | 13.1318 | 12.8349 | 12.4363 | 11.9939 | 11.5634 | 10.2546 | 9.1725 | 8.4862 | 8.0316 | 9.7924 | 9.5067 | 9.334 | 9.0054 | 8.7164 | 8.3421 | 8.0256 | 7.607 | 7.1574 | 6.6567 | 4.7955 | 3.9051 | 3.6562 | 3.7573 | 14.4294 | 14.1437 | 13.971 | 13.6424 | 13.3534 | 12.9791 | 12.6626 | 12.244 | 11.7944 | 11.2937 | 9.4325 | 8.5421 | 8.2932 | 8.3943 | 9.7931 | 9.508 | 9.3435 | 9.0272 | 8.7686 | 8.4266 | 8.1291 | 7.7325 | 7.3515 | 6.9836 | 4.3235 | -1.5752 | -6.3134 | -9.4576 | 14.4301 | 14.145 | 13.9805 | 13.6642 | 13.4056 | 13.0636 | 12.7661 | 12.3695 | 11.9885 | 11.6206 | 8.9605 | 3.0618 | -1.6764 | -4.8206 | 9.8191 | 9.525 | 9.3633 | 9.0818 | 8.8555 | 8.5644 | 8.3165 | 7.9778 | 7.4638 | 6.0853 | -0.39379 | -5.7918 | -8.9325 | -8.1299 | 14.4561 | 14.162 | 14.162 | 13.7188 | 13.4925 | 13.2014 | 12.9535 | 12.6148 | 12.1008 | 10.7223 | 4.2432 | -1.1548 | -4.2955 | -3.4929 | 394298 | 409450 | ROYTON | WHITEGATE
| Siddick | 15.752 | 15.5713 | 15.4373 | 15.3504 | 15.3246 | 15.3797 | 15.2655 | 15.2799 | 15.2206 | 15.1601 | 14.9349 | 14.819 | 14.797 | 14.8011 | 22.252 | 22.0713 | 21.9373 | 21.8504 | 21.8246 | 21.8797 | 21.7655 | 21.7799 | 21.7206 | 21.6601 | 21.4349 | 21.319 | 21.297 | 21.3011 | 16.0007 | 16.0217 | 15.822 | 15.6837 | 15.6223 | 15.6637 | 15.5348 | 15.5257 | 15.4396 | 15.3511 | 15.1405 | 15.0241 | 14.9647 | 14.9985 | 22.5007 | 22.5217 | 22.322 | 22.1837 | 22.1223 | 22.1637 | 22.0348 | 22.0257 | 21.9396 | 21.8511 | 21.6405 | 21.5241 | 21.4647 | 21.4985 | 15.7531 | 15.5739 | 15.4423 | 15.3576 | 15.3337 | 15.3905 | 15.279 | 15.2956 | 15.2397 | 15.1855 | 14.9922 | 14.9512 | 14.9652 | 15.0346 | 22.2531 | 22.0739 | 21.9423 | 21.8576 | 21.8337 | 21.8905 | 21.779 | 21.7956 | 21.7397 | 21.6855 | 21.4922 | 21.4512 | 21.4652 | 21.5346 | 15.7708 | 15.6098 | 15.4963 | 15.4307 | 15.4259 | 15.4982 | 15.4018 | 15.4299 | 15.3841 | 15.3381 | 15.1021 | 14.5195 | 13.938 | 13.5705 | 22.2708 | 22.1098 | 21.9963 | 21.9307 | 21.9259 | 21.9982 | 21.9018 | 21.9299 | 21.8841 | 21.8381 | 21.6021 | 21.0195 | 20.438 | 20.0705 | 15.7666 | 15.5967 | 15.4778 | 15.4104 | 15.405 | 15.4768 | 15.3753 | 15.3987 | 15.3473 | 15.2739 | 14.6545 | 13.9543 | 13.5949 | 13.7726 | 22.2666 | 22.0967 | 22.0967 | 21.9104 | 21.905 | 21.9768 | 21.8753 | 21.8987 | 21.8473 | 21.7739 | 21.1545 | 20.4543 | 20.0949 | 20.2726 | 300289 | 530805 | STAINBURN & SIDDICK | HARKER
| Silloth | 24.3551 | 24.1078 | 24.0461 | 23.8814 | 23.8171 | 23.5769 | 23.3759 | 23.2873 | 23.0038 | 22.6934 | 21.5623 | 20.9726 | 20.7971 | 20.9785 | 41.6651 | 41.4178 | 41.3561 | 41.1914 | 41.1271 | 40.8869 | 40.6859 | 40.5973 | 40.3138 | 40.0034 | 38.8723 | 38.2826 | 38.1071 | 38.2885 | 24.4597 | 24.2975 | 24.1908 | 24.0297 | 23.9713 | 23.746 | 23.5553 | 23.4695 | 23.2143 | 23.0041 | 22.3857 | 21.7706 | 21.3405 | 21.1032 | 41.7697 | 41.6075 | 41.5008 | 41.3397 | 41.2813 | 41.056 | 40.8653 | 40.7795 | 40.5243 | 40.3141 | 39.6957 | 39.0806 | 38.6505 | 38.4132 | 24.3585 | 24.1219 | 24.0698 | 23.9159 | 23.8597 | 23.6302 | 23.4387 | 23.3397 | 23.0669 | 22.7874 | 21.7739 | 21.2896 | 21.1704 | 21.3774 | 41.6685 | 41.4319 | 41.3798 | 41.2259 | 41.1697 | 40.9402 | 40.7487 | 40.6497 | 40.3769 | 40.0974 | 39.0839 | 38.5996 | 38.4804 | 38.6874 | 24.3581 | 24.102 | 24.0314 | 23.8605 | 23.7799 | 23.5132 | 23.2716 | 23.1453 | 22.8718 | 22.6787 | 21.675 | 20.1061 | 19.153 | 18.4758 | 41.6681 | 41.412 | 41.3414 | 41.1705 | 41.0899 | 40.8232 | 40.5816 | 40.4553 | 40.1818 | 39.9887 | 38.985 | 37.4161 | 36.463 | 35.7858 | 24.3658 | 24.1048 | 24.0333 | 23.8659 | 23.7817 | 23.5261 | 23.3088 | 23.2148 | 22.9621 | 22.5546 | 20.6884 | 19.37 | 18.7758 | 19.0435 | 41.6758 | 41.4148 | 41.4148 | 41.1759 | 41.0917 | 40.8361 | 40.6188 | 40.5248 | 40.2721 | 39.8646 | 37.9984 | 36.68 | 36.0858 | 36.3535 | 311307 | 553464 | CARLISLE | HARKER
| Skelmersdale | 7.7311 | 7.4475 | 7.3702 | 7.141 | 6.9718 | 6.7091 | 6.407 | 6.1251 | 5.7793 | 5.2803 | 3.1195 | 1.3709 | 0.27961 | -0.48252 | 12.3681 | 12.0845 | 12.0072 | 11.778 | 11.6088 | 11.3461 | 11.044 | 10.7621 | 10.4163 | 9.9173 | 7.7565 | 6.0079 | 4.9166 | 4.1545 | 7.9029 | 7.7629 | 7.6192 | 7.4013 | 7.2497 | 7.0141 | 6.7337 | 6.4694 | 6.1627 | 5.8693 | 4.6357 | 3.2148 | 1.9234 | 0.93029 | 12.5399 | 12.3999 | 12.2562 | 12.0383 | 11.8867 | 11.6511 | 11.3707 | 11.1064 | 10.7997 | 10.5063 | 9.2727 | 7.8518 | 6.5604 | 5.5673 | 7.7411 | 7.4735 | 7.4122 | 7.1973 | 7.0416 | 6.792 | 6.5026 | 6.2163 | 5.8883 | 5.4407 | 3.5935 | 2.3799 | 1.5501 | 1.2847 | 12.3781 | 12.1105 | 12.0492 | 11.8343 | 11.6786 | 11.429 | 11.1396 | 10.8533 | 10.5253 | 10.0777 | 8.2305 | 7.0169 | 6.1871 | 5.9217 | 7.743 | 7.4554 | 7.3701 | 7.1268 | 6.9311 | 6.6063 | 6.1828 | 5.7615 | 5.3413 | 4.9172 | 1.9098 | -3.3145 | -7.1033 | -9.5927 | 12.38 | 12.0924 | 12.0071 | 11.7638 | 11.5681 | 11.2433 | 10.8198 | 10.3985 | 9.9783 | 9.5542 | 6.5468 | 1.3225 | -2.4663 | -4.9557 | 7.7702 | 7.4739 | 7.4081 | 7.1746 | 6.9617 | 6.5869 | 6.1394 | 5.6903 | 5.1468 | 4.1428 | -1.456 | -6.2202 | -8.689 | -8.4581 | 12.4072 | 12.1109 | 12.1109 | 11.8116 | 11.5987 | 11.2239 | 10.7764 | 10.3273 | 9.7838 | 8.7798 | 3.181 | -1.5832 | -4.052 | -3.8211 | 347198 | 407434 | SKELMERSDALE | WASHWAY FARM
| Slipway | 5.4358 | 5.3123 | 5.3159 | 5.1747 | 5.075 | 4.8913 | 4.6827 | 4.5141 | 4.3765 | 4.1154 | 3.4087 | 3.0577 | 2.9825 | 3.1805 | 7.4358 | 7.3123 | 7.3159 | 7.1747 | 7.075 | 6.8913 | 6.6827 | 6.5141 | 6.3765 | 6.1154 | 5.4087 | 5.0577 | 4.9825 | 5.1805 | 5.5212 | 5.4761 | 5.3845 | 5.2102 | 5.0861 | 4.8782 | 4.6346 | 4.4231 | 4.2163 | 3.9371 | 3.5365 | 3.2385 | 3.0743 | 3.0687 | 7.5212 | 7.4761 | 7.3845 | 7.2102 | 7.0861 | 6.8782 | 6.6346 | 6.4231 | 6.2163 | 5.9371 | 5.5365 | 5.2385 | 5.0743 | 5.0687 | 5.447 | 5.3408 | 5.3491 | 5.22 | 5.1313 | 4.9606 | 4.7654 | 4.609 | 4.4862 | 4.256 | 3.6274 | 3.3287 | 3.2743 | 3.4611 | 7.447 | 7.3408 | 7.3491 | 7.22 | 7.1313 | 6.9606 | 6.7654 | 6.609 | 6.4862 | 6.256 | 5.6274 | 5.3287 | 5.2743 | 5.4611 | 5.4366 | 5.3099 | 5.308 | 5.1569 | 5.047 | 4.8458 | 4.5882 | 4.3557 | 4.183 | 3.9346 | 2.7382 | -0.25458 | -2.6695 | -4.2898 | 7.4366 | 7.3099 | 7.308 | 7.1569 | 7.047 | 6.8458 | 6.5882 | 6.3557 | 6.183 | 5.9346 | 4.7382 | 1.7454 | -0.66945 | -2.2898 | 5.4601 | 5.3373 | 5.3493 | 5.2178 | 5.1232 | 4.9368 | 4.7252 | 4.537 | 4.3304 | 3.5447 | 0.13207 | -2.5711 | -4.178 | -3.5948 | 7.4601 | 7.3373 | 7.3373 | 7.2178 | 7.1232 | 6.9368 | 6.7252 | 6.537 | 6.3304 | 5.5447 | 2.1321 | -0.57105 | -2.178 | -1.5948 | 297180 | 518183 | EGREMONT | HARKER
| Snipe | 9.2533 | 8.7411 | 8.783 | 8.5723 | 8.4958 | 8.1358 | 7.9081 | 7.6683 | 7.2993 | 7.0005 | 5.7954 | 4.9356 | 4.5227 | 4.3238 | 13.8903 | 13.3781 | 13.42 | 13.2093 | 13.1328 | 12.7728 | 12.5451 | 12.3053 | 11.9363 | 11.6375 | 10.4324 | 9.5726 | 9.1597 | 8.9608 | 9.5478 | 9.2867 | 9.2339 | 8.9881 | 8.9083 | 8.5819 | 8.3791 | 8.1623 | 7.8157 | 7.5623 | 6.7492 | 6.0737 | 5.6817 | 5.4912 | 14.1848 | 13.9237 | 13.8709 | 13.6251 | 13.5453 | 13.2189 | 13.0161 | 12.7993 | 12.4527 | 12.1993 | 11.3862 | 10.7107 | 10.3187 | 10.1282 | 9.2594 | 8.7569 | 8.8067 | 8.6027 | 8.5337 | 8.183 | 7.9633 | 7.731 | 7.3749 | 7.104 | 6.0266 | 5.3395 | 5.0067 | 4.9125 | 13.8964 | 13.3939 | 13.4437 | 13.2397 | 13.1707 | 12.82 | 12.6003 | 12.368 | 12.0119 | 11.741 | 10.6636 | 9.9765 | 9.6437 | 9.5495 | 9.2724 | 8.7796 | 8.8379 | 8.6399 | 8.5741 | 8.2187 | 7.9821 | 7.7257 | 7.3529 | 7.0684 | 5.26 | 1.4604 | -1.5347 | -3.4359 | 13.9094 | 13.4166 | 13.4749 | 13.2769 | 13.2111 | 12.8557 | 12.6191 | 12.3627 | 11.9899 | 11.7054 | 9.897 | 6.0974 | 3.1023 | 1.2011 | 9.2675 | 8.7467 | 8.7937 | 8.6051 | 8.5533 | 8.2214 | 7.9999 | 7.7634 | 7.3544 | 6.5789 | 2.5664 | -0.93526 | -2.849 | -2.2427 | 13.9045 | 13.3837 | 13.3837 | 13.2421 | 13.1903 | 12.8584 | 12.6369 | 12.4004 | 11.9914 | 11.2159 | 7.2034 | 3.7017 | 1.788 | 2.3943 | 391844 | 398322 | DROYLSDEN | STALYBRIDGE
| South Park | 14.6486 | 14.4062 | 14.2807 | 14.0617 | 13.9106 | 13.6622 | 13.4336 | 13.1744 | 12.9591 | 12.682 | 11.8466 | 11.3612 | 11.2168 | 11.182 | 19.1486 | 18.9062 | 18.7807 | 18.5617 | 18.4106 | 18.1622 | 17.9336 | 17.6744 | 17.4591 | 17.182 | 16.3466 | 15.8612 | 15.7168 | 15.682 | 14.7711 | 14.6335 | 14.4361 | 14.1847 | 14.0122 | 13.7487 | 13.4939 | 13.201 | 12.939 | 12.627 | 11.918 | 11.4008 | 11.1283 | 10.9394 | 19.2711 | 19.1335 | 18.9361 | 18.6847 | 18.5122 | 18.2487 | 17.9939 | 17.701 | 17.439 | 17.127 | 16.418 | 15.9008 | 15.6283 | 15.4394 | 14.6538 | 14.4227 | 14.3087 | 14.0996 | 13.9584 | 13.7213 | 13.5034 | 13.2556 | 13.054 | 12.8023 | 12.0364 | 11.6059 | 11.4789 | 11.454 | 19.1538 | 18.9227 | 18.8087 | 18.5996 | 18.4584 | 18.2213 | 18.0034 | 17.7556 | 17.554 | 17.3023 | 16.5364 | 16.1059 | 15.9789 | 15.954 | 14.6621 | 14.4334 | 14.323 | 14.1154 | 13.9833 | 13.7565 | 13.5477 | 13.3089 | 13.1349 | 12.9159 | 11.7548 | 9.3093 | 7.4511 | 6.2004 | 19.1621 | 18.9334 | 18.823 | 18.6154 | 18.4833 | 18.2565 | 18.0477 | 17.8089 | 17.6349 | 17.4159 | 16.2548 | 13.8093 | 11.9511 | 10.7004 | 14.6581 | 14.419 | 14.3195 | 14.1365 | 14.0366 | 13.8491 | 13.6746 | 13.476 | 13.2749 | 12.648 | 9.8721 | 7.6495 | 6.4291 | 6.8232 | 19.1581 | 18.919 | 18.919 | 18.6365 | 18.5366 | 18.3491 | 18.1746 | 17.976 | 17.7749 | 17.148 | 14.3721 | 12.1495 | 10.9291 | 11.3232 | 336410 | 427512 | LYTHAM | PENWORTHAM
| Spa Rd | 7.1997 | 6.2144 | 6.6311 | 6.1591 | 6.1394 | 5.2628 | 5.1758 | 4.5377 | 4.1614 | 3.4794 | 1.4642 | 0.29021 | -0.44194 | -0.6665 | 7.1997 | 6.2144 | 6.6311 | 6.1591 | 6.1394 | 5.2628 | 5.1758 | 4.5377 | 4.1614 | 3.4794 | 1.4642 | 0.29021 | -0.44194 | -0.6665 | 7.7148 | 7.1554 | 7.384 | 6.7152 | 6.6628 | 5.9437 | 5.6024 | 4.9534 | 4.2359 | 3.6716 | 2.5054 | 1.8023 | 1.2364 | 1.1117 | 7.7148 | 7.1554 | 7.384 | 6.7152 | 6.6628 | 5.9437 | 5.6024 | 4.9534 | 4.2359 | 3.6716 | 2.5054 | 1.8023 | 1.2364 | 1.1117 | 7.2146 | 6.2575 | 6.6213 | 6.1383 | 6.2604 | 5.2505 | 5.1761 | 4.5563 | 4.203 | 3.5784 | 1.8141 | 0.9604 | 0.38298 | 0.33441 | 7.2146 | 6.2575 | 6.6213 | 6.1383 | 6.2604 | 5.2505 | 5.1761 | 4.5563 | 4.203 | 3.5784 | 1.8141 | 0.9604 | 0.38298 | 0.33441 | 7.2286 | 6.2693 | 6.7132 | 6.2484 | 6.241 | 5.3024 | 5.1446 | 4.4185 | 3.9767 | 3.2335 | 0.20481 | -4.8895 | -8.8595 | -11.2171 | 7.2286 | 6.2693 | 6.7132 | 6.2484 | 6.241 | 5.3024 | 5.1446 | 4.4185 | 3.9767 | 3.2335 | 0.20481 | -4.8895 | -8.8595 | -11.2171 | 7.2347 | 6.2518 | 6.651 | 6.1728 | 6.2616 | 5.2523 | 5.1228 | 4.4408 | 3.9938 | 2.3911 | -3.6969 | -8.0667 | -10.5695 | -9.4541 | 7.2347 | 6.2518 | 6.2518 | 6.1728 | 6.2616 | 5.2523 | 5.1228 | 4.4408 | 3.9938 | 2.3911 | -3.6969 | -8.0667 | -10.5695 | -9.4541 | 371065 | 409109 | BOLTON | KEARSLEY
| Spadeadam 11/33kV | 25.9546 | 25.6331 | 25.77 | 25.8492 | 25.7407 | 25.6543 | 25.6293 | 25.7623 | 25.6974 | 25.6763 | 25.7239 | 25.828 | 25.9889 | 26.1745 | 32.9546 | 32.6331 | 32.77 | 32.8492 | 32.7407 | 32.6543 | 32.6293 | 32.7623 | 32.6974 | 32.6763 | 32.7239 | 32.828 | 32.9889 | 33.1745 | 26.2297 | 26.1377 | 26.1751 | 26.1808 | 26.0291 | 25.9253 | 25.8723 | 25.9691 | 25.8687 | 25.8146 | 25.7845 | 25.7769 | 25.8477 | 25.9947 | 33.2297 | 33.1377 | 33.1751 | 33.1808 | 33.0291 | 32.9253 | 32.8723 | 32.9691 | 32.8687 | 32.8146 | 32.7845 | 32.7769 | 32.8477 | 32.9947 | 25.9552 | 25.6346 | 25.772 | 25.8518 | 25.7443 | 25.6589 | 25.6348 | 25.7683 | 25.7047 | 25.686 | 25.7383 | 25.8447 | 26.0053 | 26.1897 | 32.9552 | 32.6346 | 32.772 | 32.8518 | 32.7443 | 32.6589 | 32.6348 | 32.7683 | 32.7047 | 32.686 | 32.7383 | 32.8447 | 33.0053 | 33.1897 | 25.9791 | 25.6869 | 25.8525 | 25.9612 | 25.8858 | 25.8396 | 25.8551 | 26.0246 | 26.0042 | 26.0249 | 26.2025 | 26.3763 | 26.6102 | 26.8817 | 32.9791 | 32.6869 | 32.8525 | 32.9612 | 32.8858 | 32.8396 | 32.8551 | 33.0246 | 33.0042 | 33.0249 | 33.2025 | 33.3763 | 33.6102 | 33.8817 | 25.9773 | 25.6826 | 25.8485 | 25.9587 | 25.8853 | 25.8421 | 25.8602 | 26.0333 | 26.0158 | 26.026 | 26.1571 | 26.3431 | 26.5966 | 26.9194 | 32.9773 | 32.6826 | 32.6826 | 32.9587 | 32.8853 | 32.8421 | 32.8602 | 33.0333 | 33.0158 | 33.026 | 33.1571 | 33.3431 | 33.5966 | 33.9194 | 361282 | 570359 | - | HARKER
| Spadeadam 132/11kV | 4.6682 | 4.558 | 4.4499 | 4.3205 | 4.1773 | 4.0164 | 3.8241 | 3.6241 | 3.4075 | 3.1375 | 2.178 | 1.7514 | 1.6377 | 1.8312 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7025 | 4.6193 | 4.4895 | 4.3651 | 4.2274 | 4.0684 | 3.8692 | 3.6037 | 3.313 | 2.9987 | 2.5503 | 2.2571 | 1.8892 | 1.6312 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.673 | 4.5678 | 4.4651 | 4.3413 | 4.2048 | 4.0513 | 3.8667 | 3.6742 | 3.4683 | 3.2199 | 2.3543 | 1.9426 | 1.8283 | 2.0491 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6728 | 4.5613 | 4.4565 | 4.3333 | 4.1909 | 4.0236 | 3.8126 | 3.6065 | 3.4141 | 3.2291 | 2.4223 | 1.7408 | 1.4425 | 1.3026 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6484 | 4.5094 | 4.4051 | 4.2906 | 4.1262 | 3.9536 | 3.7589 | 3.5785 | 3.4124 | 3.2054 | 2.3479 | 2.0517 | 2.0461 | 2.1298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 361282 | 570359 | - | HARKER
| Spotland | 6.8516 | 6.6656 | 6.2197 | 6.2068 | 5.9501 | 5.2936 | 4.5108 | 4.2073 | 3.9592 | 3.241 | 1.6411 | 0.79645 | 0.60912 | 0.77639 | 10.3516 | 10.1656 | 9.7197 | 9.7068 | 9.4501 | 8.7936 | 8.0108 | 7.7073 | 7.4592 | 6.741 | 5.1411 | 4.2964 | 4.1091 | 4.2764 | 7.0593 | 7.0489 | 6.5719 | 6.5668 | 6.3581 | 5.7747 | 5.0696 | 4.8228 | 4.6292 | 4.0555 | 2.9309 | 1.9474 | 1.3255 | 0.89009 | 10.5593 | 10.5489 | 10.0719 | 10.0668 | 9.8581 | 9.2747 | 8.5696 | 8.3228 | 8.1292 | 7.5555 | 6.4309 | 5.4474 | 4.8255 | 4.3901 | 6.8586 | 6.6797 | 6.2441 | 6.2358 | 5.9887 | 5.3462 | 4.5783 | 4.2837 | 4.0518 | 3.385 | 1.9529 | 1.2137 | 1.0586 | 1.2058 | 10.3586 | 10.1797 | 9.7441 | 9.7358 | 9.4887 | 8.8462 | 8.0783 | 7.7837 | 7.5518 | 6.885 | 5.4529 | 4.7137 | 4.5586 | 4.7058 | 6.8679 | 6.7018 | 6.2847 | 6.3008 | 6.102 | 5.5115 | 4.7747 | 4.5177 | 4.3774 | 3.8528 | 1.8678 | -2.4616 | -5.8109 | -8.138 | 10.3679 | 10.2018 | 9.7847 | 9.8008 | 9.602 | 9.0115 | 8.2747 | 8.0177 | 7.8774 | 7.3528 | 5.3678 | 1.0384 | -2.3109 | -4.638 | 6.8443 | 6.6189 | 6.1816 | 6.2077 | 6.0031 | 5.436 | 4.7465 | 4.5547 | 4.3324 | 3.0509 | -1.7468 | -5.5786 | -7.7351 | -7.1018 | 10.3443 | 10.1189 | 10.1189 | 9.7077 | 9.5031 | 8.936 | 8.2465 | 8.0547 | 7.8324 | 6.5509 | 1.7532 | -2.0786 | -4.2351 | -3.6018 | 387882 | 414309 | ROCHDALE CENTRAL | ROCHDALE
| Spring Cottage | 5.0525 | 4.8504 | 4.8544 | 4.7949 | 4.7242 | 4.6216 | 4.514 | 4.4042 | 4.3009 | 4.1868 | 3.714 | 3.3853 | 3.3099 | 3.2954 | 18.8005 | 18.5984 | 18.6024 | 18.5429 | 18.4722 | 18.3696 | 18.262 | 18.1522 | 18.0489 | 17.9348 | 17.462 | 17.1333 | 17.0579 | 17.0434 | 5.2706 | 5.2464 | 5.1822 | 5.0828 | 4.9905 | 4.8877 | 4.7738 | 4.654 | 4.5326 | 4.4177 | 4.1131 | 3.8699 | 3.7701 | 3.7411 | 19.0186 | 18.9944 | 18.9302 | 18.8308 | 18.7385 | 18.6357 | 18.5218 | 18.402 | 18.2806 | 18.1657 | 17.8611 | 17.6179 | 17.5181 | 17.4891 | 5.055 | 4.8566 | 4.8646 | 4.8103 | 4.7451 | 4.6482 | 4.5466 | 4.4428 | 4.3461 | 4.247 | 3.8333 | 3.603 | 3.5533 | 3.6024 | 18.803 | 18.6046 | 18.6126 | 18.5583 | 18.4931 | 18.3962 | 18.2946 | 18.1908 | 18.0941 | 17.995 | 17.5813 | 17.351 | 17.3013 | 17.3504 | 5.0663 | 4.876 | 4.8904 | 4.842 | 4.7786 | 4.6785 | 4.5653 | 4.4439 | 4.3335 | 4.2296 | 3.4265 | 1.4805 | 0.17622 | -0.63864 | 18.8143 | 18.624 | 18.6384 | 18.59 | 18.5266 | 18.4265 | 18.3133 | 18.1919 | 18.0815 | 17.9776 | 17.1745 | 15.2285 | 13.9242 | 13.1094 | 5.0716 | 4.8796 | 4.8949 | 4.8534 | 4.7987 | 4.7101 | 4.6061 | 4.4965 | 4.3572 | 3.9719 | 1.8845 | 0.18076 | -0.59296 | -0.12163 | 18.8196 | 18.6276 | 18.6276 | 18.6014 | 18.5467 | 18.4581 | 18.3541 | 18.2445 | 18.1052 | 17.7199 | 15.6325 | 13.9288 | 13.155 | 13.6264 | 385446 | 437481 | NELSON | PADIHAM
| Spring Garden St 11kV | 16.7529 | 16.3553 | 16.3814 | 16.2222 | 16.0252 | 15.7413 | 15.5181 | 15.2665 | 14.8913 | 12.4665 | 11.7131 | 10.8675 | 10.4106 | 10.4386 | 25.7529 | 25.3553 | 25.3814 | 25.2222 | 25.0252 | 24.7413 | 24.5181 | 24.2665 | 23.8913 | 21.4665 | 20.7131 | 19.8675 | 19.4106 | 19.4386 | 17.0072 | 16.8432 | 16.711 | 16.513 | 16.2029 | 15.8529 | 15.4747 | 15.0693 | 14.5749 | 14.159 | 13.7198 | 13.1838 | 12.9644 | 13.182 | 26.0072 | 25.8432 | 25.711 | 25.513 | 25.2029 | 24.8529 | 24.4747 | 24.0693 | 23.5749 | 23.159 | 22.7198 | 22.1838 | 21.9644 | 22.182 | 16.7603 | 16.3521 | 16.3949 | 16.2372 | 16.0506 | 15.7776 | 15.5645 | 15.3232 | 14.9634 | 12.6246 | 11.9091 | 11.1512 | 10.7307 | 10.7754 | 25.7603 | 25.3521 | 25.3949 | 25.2372 | 25.0506 | 24.7776 | 24.5645 | 24.3232 | 23.9634 | 21.6246 | 20.9091 | 20.1512 | 19.7307 | 19.7754 | 16.7686 | 16.3818 | 16.4161 | 16.2512 | 16.0481 | 15.7499 | 15.4992 | 15.2123 | 14.817 | 12.5553 | 10.1038 | 6.2632 | 3.5127 | 2.2492 | 25.7686 | 25.3818 | 25.4161 | 25.2512 | 25.0481 | 24.7499 | 24.4992 | 24.2123 | 23.817 | 21.5553 | 19.1038 | 15.2632 | 12.5127 | 11.2492 | 16.7659 | 16.3458 | 16.3775 | 16.2147 | 16.0219 | 15.1514 | 12.1542 | 10.9914 | 10.7356 | 10.3654 | 7.1235 | 3.5635 | 1.4817 | 2.8117 | 25.7659 | 25.3458 | 25.3458 | 25.2147 | 25.0219 | 24.1514 | 21.1542 | 19.9914 | 19.7356 | 19.3654 | 16.1235 | 12.5635 | 10.4817 | 11.8117 | 347661 | 461494 | LANCASTER | HEYSHAM
| Spring Garden St 6.6kV | 11.5669 | 11.0214 | 11.012 | 10.8925 | 10.6805 | 10.511 | 10.3345 | 10.1403 | 9.8552 | 9.7519 | 9.0518 | 8.4939 | 8.2793 | 8.4044 | 15.7039 | 15.1584 | 15.149 | 15.0295 | 14.8175 | 14.648 | 14.4715 | 14.2773 | 13.9922 | 13.8889 | 13.1888 | 12.6309 | 12.4163 | 12.5414 | 11.8848 | 11.6344 | 11.5311 | 11.3191 | 11.0946 | 10.8278 | 10.5685 | 10.2849 | 9.9261 | 9.3822 | 9.0597 | 8.6221 | 8.4777 | 8.5923 | 16.0218 | 15.7714 | 15.6681 | 15.4561 | 15.2316 | 14.9648 | 14.7055 | 14.4219 | 14.0631 | 13.5192 | 13.1967 | 12.7591 | 12.6147 | 12.7293 | 11.601 | 11.047 | 11.0496 | 10.934 | 10.6726 | 10.5902 | 10.3944 | 10.202 | 9.9646 | 9.834 | 9.1677 | 8.6908 | 8.5136 | 8.6723 | 15.738 | 15.184 | 15.1866 | 15.071 | 14.8096 | 14.7272 | 14.5314 | 14.339 | 14.1016 | 13.971 | 13.3047 | 12.8278 | 12.6506 | 12.8093 | 11.5783 | 11.042 | 11.0382 | 10.9205 | 10.6991 | 10.5228 | 10.3269 | 10.1074 | 9.8044 | 9.7007 | 8.596 | 6.1391 | 4.1944 | 3.0928 | 15.7153 | 15.179 | 15.1752 | 15.0575 | 14.8361 | 14.6598 | 14.4639 | 14.2444 | 13.9414 | 13.8377 | 12.733 | 10.2761 | 8.3314 | 7.2298 | 11.5901 | 11.0509 | 11.0569 | 10.9568 | 10.7267 | 10.6067 | 10.4349 | 10.2341 | 9.9424 | 9.4322 | 6.8008 | 4.2969 | 2.9468 | 3.6638 | 15.7271 | 15.1879 | 15.1879 | 15.0938 | 14.8637 | 14.7437 | 14.5719 | 14.3711 | 14.0794 | 13.5692 | 10.9378 | 8.4339 | 7.0838 | 7.8008 | 347651 | 461484 | LANCASTER | HEYSHAM
| Squires Gate | 10.0973 | 9.5383 | 9.4907 | 9.2683 | 9.1037 | 8.8394 | 8.6606 | 8.3871 | 8.0927 | 7.8557 | 6.3007 | 5.3419 | 5.0822 | 5.0748 | 14.6973 | 14.1383 | 14.0907 | 13.8683 | 13.7037 | 13.4394 | 13.2606 | 12.9871 | 12.6927 | 12.4557 | 10.9007 | 9.9419 | 9.6822 | 9.6748 | 10.5399 | 10.3605 | 10.2475 | 9.9352 | 9.7053 | 9.4024 | 9.0582 | 8.4306 | 7.7408 | 6.9465 | 6.1513 | 5.6718 | 5.4911 | 5.4704 | 15.1399 | 14.9605 | 14.8475 | 14.5352 | 14.3053 | 14.0024 | 13.6582 | 13.0306 | 12.3408 | 11.5465 | 10.7513 | 10.2718 | 10.0911 | 10.0704 | 10.1191 | 9.5709 | 9.5218 | 9.3233 | 9.1634 | 8.9184 | 8.7456 | 8.4884 | 8.222 | 8.0482 | 6.5586 | 5.8403 | 5.6797 | 5.8053 | 14.7191 | 14.1709 | 14.1218 | 13.9233 | 13.7634 | 13.5184 | 13.3456 | 13.0884 | 12.822 | 12.6482 | 11.1586 | 10.4403 | 10.2797 | 10.4053 | 10.1234 | 9.5944 | 9.5787 | 9.3902 | 9.2618 | 9.0328 | 8.8856 | 8.6455 | 8.3879 | 8.2282 | 5.9789 | 2.0621 | -0.73857 | -2.4697 | 14.7234 | 14.1944 | 14.1787 | 13.9902 | 13.8618 | 13.6328 | 13.4856 | 13.2455 | 12.9879 | 12.8282 | 10.5789 | 6.6621 | 3.8614 | 2.1303 | 10.1106 | 9.5514 | 9.5328 | 9.3663 | 9.2608 | 9.0646 | 8.9299 | 8.7155 | 8.4853 | 7.6738 | 3.2012 | -0.2132 | -2.0404 | -1.5943 | 14.7106 | 14.1514 | 14.1514 | 13.9663 | 13.8608 | 13.6646 | 13.5299 | 13.3155 | 13.0853 | 12.2738 | 7.8012 | 4.3868 | 2.5596 | 3.0057 | 332037 | 432063 | BLACKPOOL | PENWORTHAM
| St Annes | 10.2699 | 10.0322 | 9.9198 | 9.8223 | 9.6622 | 9.4488 | 9.265 | 9.0758 | 8.8939 | 8.6576 | 7.8506 | 7.3192 | 7.0824 | 6.911 | 13.7699 | 13.5322 | 13.4198 | 13.3223 | 13.1622 | 12.9488 | 12.765 | 12.5758 | 12.3939 | 12.1576 | 11.3506 | 10.8192 | 10.5824 | 10.411 | 10.4065 | 10.2855 | 10.1253 | 10.0135 | 9.8554 | 9.6562 | 9.4803 | 9.2961 | 9.1168 | 8.9013 | 8.314 | 7.8572 | 7.5903 | 7.3632 | 13.9065 | 13.7855 | 13.6253 | 13.5135 | 13.3554 | 13.1562 | 12.9803 | 12.7961 | 12.6168 | 12.4013 | 11.814 | 11.3572 | 11.0903 | 10.8632 | 10.2723 | 10.0457 | 9.9444 | 9.8526 | 9.6995 | 9.4934 | 9.3164 | 9.1338 | 8.9612 | 8.7452 | 8.0182 | 7.5673 | 7.3673 | 7.2282 | 13.7723 | 13.5457 | 13.4444 | 13.3526 | 13.1995 | 12.9934 | 12.8164 | 12.6338 | 12.4612 | 12.2452 | 11.5182 | 11.0673 | 10.8673 | 10.7282 | 10.2816 | 10.0519 | 9.9435 | 9.8444 | 9.6847 | 9.4616 | 9.2554 | 9.0386 | 8.8388 | 8.5997 | 7.4424 | 5.4589 | 3.9391 | 2.5237 | 13.7816 | 13.5519 | 13.4435 | 13.3444 | 13.1847 | 12.9616 | 12.7554 | 12.5386 | 12.3388 | 12.0997 | 10.9424 | 8.9589 | 7.4391 | 6.0237 | 10.2762 | 10.0299 | 9.9161 | 9.8191 | 9.6635 | 9.4522 | 9.2592 | 9.061 | 8.8392 | 8.3096 | 6.0314 | 4.1667 | 2.8558 | 3.0764 | 13.7762 | 13.5299 | 13.5299 | 13.3191 | 13.1635 | 12.9522 | 12.7592 | 12.561 | 12.3392 | 11.8096 | 9.5314 | 7.6667 | 6.3558 | 6.5764 | 331716 | 429849 | LYTHAM | PENWORTHAM
| St Johns | 19.9032 | 17.3832 | 14.8632 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 6.4202 | 6.4202 | 6.4202 | 6.4202 | 6.4202 | 6.4202 | 6.4202 | 24.5402 | 22.0202 | 19.5002 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 20.7432 | 19.4832 | 18.2232 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 17.3832 | 25.3802 | 24.1202 | 22.8602 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 22.0202 | 19.9032 | 17.3832 | 14.8632 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 24.5402 | 22.0202 | 19.5002 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 19.9032 | 17.3832 | 14.8632 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 24.5402 | 22.0202 | 19.5002 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 19.9032 | 17.3832 | 14.8632 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 13.1832 | 24.5402 | 22.0202 | 22.0202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 | 17.8202 |  |  | FREDERICK RD | KEARSLEY
| St Marys | 13.6822 | 13.4419 | 13.3888 | 13.3735 | 13.2052 | 13.0815 | 12.9505 | 12.8104 | 12.6321 | 12.4564 | 11.7554 | 11.2044 | 10.8724 | 10.8036 | 18.3192 | 18.0789 | 18.0258 | 18.0105 | 17.8422 | 17.7185 | 17.5875 | 17.4474 | 17.2691 | 17.0934 | 16.3924 | 15.8414 | 15.5094 | 15.4406 | 13.8998 | 13.8416 | 13.6857 | 13.5956 | 13.373 | 13.2138 | 13.034 | 12.8348 | 12.5936 | 12.3375 | 11.9113 | 11.3846 | 10.9731 | 10.7311 | 18.5368 | 18.4786 | 18.3227 | 18.2326 | 18.01 | 17.8508 | 17.671 | 17.4718 | 17.2306 | 16.9745 | 16.5483 | 16.0216 | 15.6101 | 15.3681 | 13.69 | 13.4572 | 13.4125 | 13.4045 | 13.246 | 13.1308 | 13.0087 | 12.8778 | 12.7127 | 12.5604 | 11.93 | 11.4576 | 11.1748 | 11.1258 | 18.327 | 18.0942 | 18.0495 | 18.0415 | 17.883 | 17.7678 | 17.6457 | 17.5148 | 17.3497 | 17.1974 | 16.567 | 16.0946 | 15.8118 | 15.7628 | 13.6939 | 13.4643 | 13.4209 | 13.4146 | 13.2509 | 13.1199 | 12.9478 | 12.7634 | 12.5546 | 12.3902 | 11.5553 | 10.0778 | 9.0267 | 8.218 | 18.3309 | 18.1013 | 18.0579 | 18.0516 | 17.8879 | 17.7569 | 17.5848 | 17.4004 | 17.1916 | 17.0272 | 16.1923 | 14.7148 | 13.6637 | 12.855 | 13.7035 | 13.4786 | 13.4441 | 13.4424 | 13.257 | 13.1179 | 12.9655 | 12.8041 | 12.6153 | 12.261 | 10.5932 | 9.2632 | 8.4499 | 8.6301 | 18.3405 | 18.1156 | 18.1156 | 18.0794 | 17.894 | 17.7549 | 17.6025 | 17.4411 | 17.2523 | 16.898 | 15.2302 | 13.9002 | 13.0869 | 13.2671 | 392582 | 405316 | GREENHILL | WHITEGATE
| St Marys St | 7.243 | 6.9592 | 7.011 | 6.7173 | 6.7538 | 6.4933 | 6.3515 | 6.2403 | 5.9846 | 5.6999 | 5.0314 | 4.554 | 4.26 | 4.2984 | 10.743 | 10.4592 | 10.511 | 10.2173 | 10.2538 | 9.9933 | 9.8515 | 9.7403 | 9.4846 | 9.1999 | 8.5314 | 8.054 | 7.76 | 7.7984 | 7.3957 | 7.1837 | 7.1568 | 6.775 | 6.801 | 6.4626 | 6.2675 | 6.0927 | 5.7596 | 5.4113 | 4.9223 | 4.4724 | 4.1025 | 4.0012 | 10.8957 | 10.6837 | 10.6568 | 10.275 | 10.301 | 9.9626 | 9.7675 | 9.5927 | 9.2596 | 8.9113 | 8.4223 | 7.9724 | 7.6025 | 7.5012 | 7.2529 | 6.9881 | 7.0508 | 6.7782 | 6.832 | 6.5819 | 6.4541 | 6.3565 | 6.1211 | 5.8663 | 5.2738 | 4.8937 | 4.6612 | 4.7491 | 10.7529 | 10.4881 | 10.5508 | 10.2782 | 10.332 | 10.0819 | 9.9541 | 9.8565 | 9.6211 | 9.3663 | 8.7738 | 8.3937 | 8.1612 | 8.2491 | 7.2573 | 6.9804 | 7.0473 | 6.7489 | 6.7944 | 6.5193 | 6.3574 | 6.2224 | 5.9591 | 5.6907 | 4.6771 | 2.4091 | 0.62955 | -0.35321 | 10.7573 | 10.4804 | 10.5473 | 10.2489 | 10.2944 | 10.0193 | 9.8574 | 9.7224 | 9.4591 | 9.1907 | 8.1771 | 5.9091 | 4.1295 | 3.1468 | 7.2735 | 7.0182 | 7.0822 | 6.8332 | 6.8711 | 6.6561 | 6.5339 | 6.4014 | 6.1584 | 5.5161 | 3.0206 | 0.98726 | -0.21522 | 0.34291 | 10.7735 | 10.5182 | 10.5182 | 10.3332 | 10.3711 | 10.1561 | 10.0339 | 9.9014 | 9.6584 | 9.0161 | 6.5206 | 4.4873 | 3.2848 | 3.8429 | 354932 | 429640 | RIBBLE | PENWORTHAM
| St Thomas Rd | 13.4544 | 13.1646 | 13.0318 | 12.7261 | 12.5204 | 12.2013 | 11.9206 | 11.6089 | 11.2963 | 10.9171 | 9.6481 | 8.8539 | 8.5004 | 8.4473 | 18.0914 | 17.8016 | 17.6688 | 17.3631 | 17.1574 | 16.8383 | 16.5576 | 16.2459 | 15.9333 | 15.5541 | 14.2851 | 13.4909 | 13.1374 | 13.0843 | 13.4876 | 13.2132 | 12.9915 | 12.6594 | 12.4472 | 12.0647 | 11.7233 | 11.3712 | 10.9503 | 10.5213 | 9.6168 | 8.7803 | 8.22 | 7.7628 | 18.1246 | 17.8502 | 17.6285 | 17.2964 | 17.0842 | 16.7017 | 16.3603 | 16.0082 | 15.5873 | 15.1583 | 14.2538 | 13.4173 | 12.857 | 12.3998 | 13.4595 | 13.2042 | 13.093 | 12.8188 | 12.6056 | 12.3405 | 12.0484 | 11.7578 | 11.4714 | 11.1366 | 9.9981 | 9.2946 | 8.9672 | 8.8774 | 18.0965 | 17.8412 | 17.73 | 17.4558 | 17.2426 | 16.9775 | 16.6854 | 16.3948 | 16.1084 | 15.7736 | 14.6351 | 13.9316 | 13.6042 | 13.5144 | 13.459 | 13.1663 | 13.0318 | 12.7157 | 12.5015 | 12.1419 | 11.7926 | 11.4275 | 11.0786 | 10.7194 | 8.9481 | 5.5128 | 3.0198 | 1.2258 | 18.096 | 17.8033 | 17.6688 | 17.3527 | 17.1385 | 16.7789 | 16.4296 | 16.0645 | 15.7156 | 15.3564 | 13.5851 | 10.1498 | 7.6568 | 5.8628 | 13.4825 | 13.1986 | 13.0845 | 12.8003 | 12.5803 | 12.278 | 11.9764 | 11.6635 | 11.3527 | 10.4787 | 6.4782 | 3.3397 | 1.611 | 2.0555 | 18.1195 | 17.8356 | 17.8356 | 17.4373 | 17.2173 | 16.915 | 16.6134 | 16.3005 | 15.9897 | 15.1157 | 11.1152 | 7.9767 | 6.248 | 6.6925 | 332713 | 428643 | LYTHAM | PENWORTHAM
| Stainburn | 8.3698 | 7.9703 | 8.0612 | 7.8766 | 7.7155 | 7.3967 | 6.9983 | 6.6069 | 6.2226 | 5.7478 | 4.1507 | 3.4876 | 3.4638 | 3.8002 | 10.8698 | 10.4703 | 10.5612 | 10.3766 | 10.2155 | 9.8967 | 9.4983 | 9.1069 | 8.7226 | 8.2478 | 6.6507 | 5.9876 | 5.9638 | 6.3002 | 8.5012 | 8.2197 | 8.2731 | 8.1054 | 7.9811 | 7.7361 | 7.4475 | 7.155 | 6.8632 | 6.5486 | 5.5022 | 4.8239 | 4.484 | 4.3287 | 11.0012 | 10.7197 | 10.7731 | 10.6054 | 10.4811 | 10.2361 | 9.9475 | 9.655 | 9.3632 | 9.0486 | 8.0022 | 7.3239 | 6.984 | 6.8287 | 8.3724 | 7.9818 | 8.0783 | 7.9007 | 7.7488 | 7.4434 | 7.057 | 6.6766 | 6.3094 | 5.8789 | 4.4555 | 3.9107 | 3.9261 | 4.2601 | 10.8724 | 10.4818 | 10.5783 | 10.4007 | 10.2488 | 9.9434 | 9.557 | 9.1766 | 8.8094 | 8.3789 | 6.9555 | 6.4107 | 6.4261 | 6.7601 | 8.3791 | 7.9837 | 8.0739 | 7.8868 | 7.7252 | 7.4133 | 7.124 | 6.7848 | 6.4854 | 6.1638 | 4.5632 | 2.1363 | 0.55039 | -0.49497 | 10.8791 | 10.4837 | 10.5739 | 10.3868 | 10.2252 | 9.9133 | 9.624 | 9.2848 | 8.9854 | 8.6638 | 7.0632 | 4.6363 | 3.0504 | 2.005 | 8.3712 | 7.9441 | 8.0174 | 7.8241 | 7.657 | 7.3572 | 7.0636 | 6.7767 | 6.4783 | 5.8156 | 2.8625 | 0.86595 | -0.059179 | 0.43773 | 10.8712 | 10.4441 | 10.4441 | 10.3241 | 10.157 | 9.8572 | 9.5636 | 9.2767 | 8.9783 | 8.3156 | 5.3625 | 3.366 | 2.4408 | 2.9377 | 302535 | 529330 | STAINBURN & SIDDICK | HARKER
| Standish | 6.1765 | 5.712 | 5.4724 | 5.0986 | 4.7126 | 3.967 | 3.2082 | 2.3973 | 1.6465 | 0.68896 | -2.5122 | -4.0003 | -4.0603 | -3.492 | 10.6765 | 10.212 | 9.9724 | 9.5986 | 9.2126 | 8.467 | 7.7082 | 6.8973 | 6.1465 | 5.189 | 1.9878 | 0.49974 | 0.43973 | 1.008 | 6.5933 | 6.4791 | 6.1405 | 5.7795 | 5.4811 | 4.9418 | 4.3734 | 3.7565 | 3.1485 | 2.5031 | 0.51593 | -0.79536 | -1.4406 | -1.7831 | 11.0933 | 10.9791 | 10.6405 | 10.2795 | 9.9811 | 9.4418 | 8.8734 | 8.2565 | 7.6485 | 7.0031 | 5.0159 | 3.7046 | 3.0594 | 2.7169 | 6.184 | 5.7349 | 5.5142 | 5.1662 | 4.772 | 4.0503 | 3.3147 | 2.5262 | 1.8037 | 0.9307 | -1.9411 | -3.1678 | -3.156 | -2.5659 | 10.684 | 10.2349 | 10.0142 | 9.6662 | 9.272 | 8.5503 | 7.8147 | 7.0262 | 6.3037 | 5.4307 | 2.5589 | 1.3322 | 1.344 | 1.9341 | 6.2045 | 5.7484 | 5.5095 | 5.1463 | 4.8154 | 4.2136 | 3.4971 | 2.7264 | 2.1055 | 1.4337 | -1.8625 | -7.6133 | -11.5289 | -14.54 | 10.7045 | 10.2484 | 10.0095 | 9.6463 | 9.3154 | 8.7136 | 7.9971 | 7.2264 | 6.6055 | 5.9337 | 2.6375 | -3.1133 | -7.0289 | -10.04 | 6.2009 | 5.7089 | 5.4534 | 5.09 | 4.7647 | 4.1629 | 3.5408 | 2.9102 | 2.3292 | 0.88449 | -5.6991 | -10.4505 | -12.9217 | -11.9951 | 10.7009 | 10.2089 | 10.2089 | 9.59 | 9.2647 | 8.6629 | 8.0408 | 7.4102 | 6.8292 | 5.3845 | -1.1991 | -5.9505 | -8.4217 | -7.4951 | 356139 | 410059 | WRIGHTINGTON | PENWORTHAM
| Strangeways | 6.2109 | 5.8444 | 5.6055 | 5.5637 | 5.2491 | 4.948 | 4.788 | 4.514 | 4.1506 | 3.8142 | 2.7313 | 2.0365 | 1.7277 | 1.6729 | 15.7109 | 15.3444 | 15.1055 | 15.0637 | 14.7491 | 14.448 | 14.288 | 14.014 | 13.6506 | 13.3142 | 12.2313 | 11.5365 | 11.2277 | 11.1729 | 6.5378 | 6.4292 | 6.0705 | 5.928 | 5.5404 | 5.1867 | 4.9531 | 4.5921 | 4.1253 | 3.7082 | 2.8937 | 2.2624 | 1.8825 | 1.6699 | 16.0378 | 15.9292 | 15.5705 | 15.428 | 15.0404 | 14.6867 | 14.4531 | 14.0921 | 13.6253 | 13.2082 | 12.3937 | 11.7624 | 11.3825 | 11.1699 | 6.2239 | 5.8747 | 5.6566 | 5.6281 | 5.3333 | 5.051 | 4.9068 | 4.6514 | 4.3123 | 4.0104 | 3.017 | 2.4133 | 2.1441 | 2.1263 | 15.7239 | 15.3747 | 15.1566 | 15.1281 | 14.8333 | 14.551 | 14.4068 | 14.1514 | 13.8123 | 13.5104 | 12.517 | 11.9133 | 11.6441 | 11.6263 | 6.2244 | 5.871 | 5.6442 | 5.608 | 5.2995 | 5.0001 | 4.8283 | 4.5394 | 4.182 | 3.8937 | 2.5683 | -0.12024 | -2.2167 | -3.6954 | 15.7244 | 15.371 | 15.1442 | 15.108 | 14.7995 | 14.5001 | 14.3283 | 14.0394 | 13.682 | 13.3937 | 12.0683 | 9.3798 | 7.2833 | 5.8046 | 6.2386 | 5.8889 | 5.6784 | 5.6678 | 5.3874 | 5.1248 | 4.9906 | 4.7459 | 4.4093 | 3.7128 | 0.65149 | -1.8064 | -3.2571 | -2.8924 | 15.7386 | 15.3889 | 15.3889 | 15.1678 | 14.8874 | 14.6248 | 14.4906 | 14.2459 | 13.9093 | 13.2128 | 10.1515 | 7.6936 | 6.2429 | 6.6076 | 383780 | 399743 | RED BANK | WHITEGATE
| Strawberry Bank | 10.8177 | 10.5927 | 10.5044 | 10.3346 | 10.1476 | 9.9063 | 9.6492 | 9.3772 | 9.0914 | 8.7736 | 7.7498 | 7.0777 | 6.924 | 6.9276 | 14.9547 | 14.7297 | 14.6414 | 14.4716 | 14.2846 | 14.0433 | 13.7862 | 13.5142 | 13.2284 | 12.9106 | 11.8868 | 11.2147 | 11.061 | 11.0646 | 11.0383 | 10.9822 | 10.8052 | 10.6022 | 10.4109 | 10.1818 | 9.93 | 9.6689 | 9.3811 | 9.091 | 8.3453 | 7.8463 | 7.6015 | 7.5237 | 15.1753 | 15.1192 | 14.9422 | 14.7392 | 14.5479 | 14.3188 | 14.067 | 13.8059 | 13.5181 | 13.228 | 12.4823 | 11.9833 | 11.7385 | 11.6607 | 10.8234 | 10.6043 | 10.5225 | 10.3595 | 10.1799 | 9.9467 | 9.6976 | 9.443 | 9.1713 | 8.885 | 7.9768 | 7.4986 | 7.4218 | 7.5328 | 14.9604 | 14.7413 | 14.6595 | 14.4965 | 14.3169 | 14.0837 | 13.8346 | 13.58 | 13.3083 | 13.022 | 12.1138 | 11.6356 | 11.5588 | 11.6698 | 10.8339 | 10.6268 | 10.562 | 10.4215 | 10.269 | 10.0661 | 9.8292 | 9.5879 | 9.3691 | 9.0835 | 7.5878 | 4.1135 | 1.4261 | -0.23338 | 14.9709 | 14.7638 | 14.699 | 14.5585 | 14.406 | 14.2031 | 13.9662 | 13.7249 | 13.5061 | 13.2205 | 11.7248 | 8.2505 | 5.5631 | 3.9036 | 10.8417 | 10.6166 | 10.5425 | 10.414 | 10.2761 | 10.0067 | 9.795 | 9.584 | 9.2952 | 8.4743 | 4.7463 | 1.482 | -0.16595 | 0.53079 | 14.9787 | 14.7536 | 14.7536 | 14.551 | 14.4131 | 14.1437 | 13.932 | 13.721 | 13.4322 | 12.6113 | 8.8833 | 5.619 | 3.9711 | 4.6678 | 376338 | 429396 | HUNCOAT | PADIHAM
| Stuart St | 8.2931 | 7.2343 | 6.8795 | 6.7146 | 6.6097 | 6.4539 | 6.1841 | 6.0164 | 5.8152 | 5.5453 | 4.4814 | 3.7108 | 3.3607 | 3.2634 | 15.2931 | 14.2343 | 13.8795 | 13.7146 | 13.6097 | 13.4539 | 13.1841 | 13.0164 | 12.8152 | 12.5453 | 11.4814 | 10.7108 | 10.3607 | 10.2634 | 8.8743 | 8.4177 | 8.1129 | 7.9203 | 7.8305 | 7.6264 | 7.415 | 7.2052 | 6.9418 | 6.699 | 5.845 | 5.2001 | 4.7603 | 4.465 | 15.8743 | 15.4177 | 15.1129 | 14.9203 | 14.8305 | 14.6264 | 14.415 | 14.2052 | 13.9418 | 13.699 | 12.845 | 12.2001 | 11.7603 | 11.465 | 8.3066 | 7.2461 | 6.9145 | 6.7573 | 6.6614 | 6.4967 | 6.2542 | 6.0953 | 5.8565 | 5.6084 | 4.6157 | 4.0554 | 3.7926 | 3.753 | 15.3066 | 14.2461 | 13.9145 | 13.7573 | 13.6614 | 13.4967 | 13.2542 | 13.0953 | 12.8565 | 12.6084 | 11.6157 | 11.0554 | 10.7926 | 10.753 | 8.3061 | 7.2616 | 6.9119 | 6.7488 | 6.6462 | 6.4806 | 6.18 | 5.9744 | 5.7596 | 5.4988 | 4.0659 | 1.3196 | -0.91698 | -2.3707 | 15.3061 | 14.2616 | 13.9119 | 13.7488 | 13.6462 | 13.4806 | 13.18 | 12.9744 | 12.7596 | 12.4988 | 11.0659 | 8.3196 | 6.083 | 4.6293 | 8.3101 | 7.2582 | 6.9135 | 6.7583 | 6.6582 | 6.5002 | 6.2107 | 6.0166 | 5.7647 | 5.0695 | 1.9399 | -0.63753 | -2.1484 | -1.7978 | 15.3101 | 14.2582 | 14.2582 | 13.7583 | 13.6582 | 13.5002 | 13.2107 | 13.0166 | 12.7647 | 12.0695 | 8.9399 | 6.3625 | 4.8516 | 5.2022 | 387190 | 398835 | STUART ST | STALYBRIDGE
| Stubbins | 12.2443 | 11.891 | 11.9204 | 11.8486 | 11.7401 | 11.5716 | 11.4018 | 11.2468 | 8.2123 | 8.2012 | 7.5381 | 7.1689 | 7.2559 | 7.4842 | 29.2443 | 28.891 | 28.9204 | 28.8486 | 28.7401 | 28.5716 | 28.4018 | 28.2468 | 25.2123 | 25.2012 | 24.5381 | 24.1689 | 24.2559 | 24.4842 | 12.6762 | 12.675 | 12.561 | 12.3965 | 12.2313 | 12.0559 | 11.867 | 11.6869 | 11.4497 | 11.2375 | 10.5801 | 10.1253 | 9.9252 | 9.8902 | 29.6762 | 29.675 | 29.561 | 29.3965 | 29.2313 | 29.0559 | 28.867 | 28.6869 | 28.4497 | 28.2375 | 27.5801 | 27.1253 | 26.9252 | 26.8902 | 12.2461 | 11.895 | 11.9264 | 11.8568 | 11.7508 | 11.5852 | 11.4184 | 11.2662 | 8.236 | 8.2628 | 7.7176 | 7.4444 | 7.5708 | 7.8506 | 29.2461 | 28.895 | 28.9264 | 28.8568 | 28.7508 | 28.5852 | 28.4184 | 28.2662 | 25.236 | 25.2628 | 24.7176 | 24.4444 | 24.5708 | 24.8506 | 12.2797 | 11.961 | 12.0234 | 11.987 | 11.9123 | 11.7724 | 11.6249 | 11.4865 | 8.669 | 8.7177 | 3.8643 | 2.7221 | 2.5473 | 2.4315 | 29.2797 | 28.961 | 29.0234 | 28.987 | 28.9123 | 28.7724 | 28.6249 | 28.4865 | 25.669 | 25.7177 | 20.8643 | 19.7221 | 19.5473 | 19.4315 | 12.2817 | 11.959 | 12.0214 | 11.9892 | 11.9201 | 11.7879 | 8.8052 | 8.8553 | 8.8955 | 8.8118 | 6.8534 | 5.8541 | 5.6827 | 6.4021 | 29.2817 | 28.959 | 28.959 | 28.9892 | 28.9201 | 28.7879 | 25.8052 | 25.8553 | 25.8955 | 25.8118 | 23.8534 | 22.8541 | 22.6827 | 23.4021 | 379112 | 418005 | ROSSENDALE | PADIHAM
| Swinton | 13.2478 | 12.9963 | 12.851 | 12.5617 | 12.3582 | 12.0112 | 11.6382 | 11.2698 | 10.8872 | 10.4645 | 8.8156 | 7.6112 | 6.9482 | 6.5945 | 17.7478 | 17.4963 | 17.351 | 17.0617 | 16.8582 | 16.5112 | 16.1382 | 15.7698 | 15.3872 | 14.9645 | 13.3156 | 12.1112 | 11.4482 | 11.0945 | 13.2886 | 13.068 | 12.8434 | 12.5297 | 12.3165 | 11.9591 | 11.5673 | 11.175 | 10.7183 | 10.2953 | 9.0164 | 7.9604 | 7.1905 | 6.6586 | 17.7886 | 17.568 | 17.3434 | 17.0297 | 16.8165 | 16.4591 | 16.0673 | 15.675 | 15.2183 | 14.7953 | 13.5164 | 12.4604 | 11.6905 | 11.1586 | 13.2598 | 13.0306 | 12.9061 | 12.634 | 12.4511 | 12.1279 | 11.7792 | 11.435 | 11.0821 | 10.7063 | 9.2109 | 8.2281 | 7.6856 | 7.4612 | 17.7598 | 17.5306 | 17.4061 | 17.134 | 16.9511 | 16.6279 | 16.2792 | 15.935 | 15.5821 | 15.2063 | 13.7109 | 12.7281 | 12.1856 | 11.9612 | 13.2507 | 13.0024 | 12.8584 | 12.5577 | 12.3679 | 12.0294 | 11.6502 | 11.2721 | 10.9173 | 10.5618 | 8.3163 | 4.1001 | 0.73349 | -1.5194 | 17.7507 | 17.5024 | 17.3584 | 17.0577 | 16.8679 | 16.5294 | 16.1502 | 15.7721 | 15.4173 | 15.0618 | 12.8163 | 8.6001 | 5.2335 | 2.9806 | 13.2826 | 13.0431 | 12.9068 | 12.6318 | 12.4759 | 12.1813 | 11.8419 | 11.5062 | 11.1028 | 10.1372 | 5.4964 | 1.6568 | -0.72515 | -0.46956 | 17.7826 | 17.5431 | 17.5431 | 17.1318 | 16.9759 | 16.6813 | 16.3419 | 16.0062 | 15.6028 | 14.6372 | 9.9964 | 6.1568 | 3.7749 | 4.0304 | 378367 | 401718 | AGECROFT | KEARSLEY
| Tame Valley | 8.5229 | 8.2152 | 8.0653 | 7.8582 | 7.7122 | 7.3822 | 7.0595 | 6.7584 | 6.4148 | 5.9273 | 3.7243 | 2.2886 | 1.669 | 1.0296 | 13.1599 | 12.8522 | 12.7023 | 12.4952 | 12.3492 | 12.0192 | 11.6965 | 11.3954 | 11.0518 | 10.5643 | 8.3613 | 6.9256 | 6.306 | 5.6666 | 8.7442 | 8.6149 | 8.3779 | 8.1602 | 8.0288 | 7.7361 | 7.446 | 7.0637 | 6.6061 | 6.1171 | 4.7091 | 3.5282 | 2.6692 | 2.0744 | 13.3812 | 13.2519 | 13.0149 | 12.7972 | 12.6658 | 12.3731 | 12.083 | 11.7007 | 11.2431 | 10.7541 | 9.3461 | 8.1652 | 7.3062 | 6.7114 | 8.5291 | 8.2296 | 8.0884 | 7.8902 | 7.7536 | 7.4346 | 7.1228 | 6.8325 | 6.5054 | 6.1009 | 4.2741 | 3.165 | 2.6568 | 2.2597 | 13.1661 | 12.8666 | 12.7254 | 12.5272 | 12.3906 | 12.0716 | 11.7598 | 11.4695 | 11.1424 | 10.7379 | 8.9111 | 7.802 | 7.2938 | 6.8967 | 8.5335 | 8.2278 | 8.0688 | 7.8397 | 7.6637 | 7.268 | 6.823 | 6.3713 | 5.9028 | 5.3709 | 2.0003 | -4.8695 | -10.6387 | -14.6069 | 13.1705 | 12.8648 | 12.7058 | 12.4767 | 12.3007 | 11.905 | 11.46 | 11.0083 | 10.5398 | 10.0079 | 6.6373 | -0.23246 | -6.0017 | -9.9699 | 8.5336 | 8.2066 | 8.0366 | 7.8049 | 7.6131 | 7.2097 | 6.7615 | 6.3081 | 5.6845 | 4.1093 | -3.3813 | -10.0191 | -13.9281 | -13.3434 | 13.1706 | 12.8436 | 12.8436 | 12.4419 | 12.2501 | 11.8467 | 11.3985 | 10.9451 | 10.3215 | 8.7463 | 1.2557 | -5.3821 | -9.2911 | -8.7064 | 395148 | 398108 | HARTSHEAD-HEYROD | STALYBRIDGE
| Tardy Gate | 10.5141 | 9.9778 | 9.8022 | 9.3734 | 9.2312 | 8.7703 | 8.3933 | 8.0426 | 7.5649 | 7.0053 | 5.2175 | 4.3007 | 3.9945 | 4.1051 | 14.6511 | 14.1148 | 13.9392 | 13.5104 | 13.3682 | 12.9073 | 12.5303 | 12.1796 | 11.7019 | 11.1423 | 9.3545 | 8.4377 | 8.1315 | 8.2421 | 10.708 | 10.3445 | 10.1429 | 9.7271 | 9.6167 | 9.2053 | 8.8746 | 8.5689 | 8.1399 | 7.6954 | 6.4605 | 5.5071 | 4.8033 | 4.4403 | 14.845 | 14.4815 | 14.2799 | 13.8641 | 13.7537 | 13.3423 | 13.0116 | 12.7059 | 12.2769 | 11.8324 | 10.5975 | 9.6441 | 8.9403 | 8.5773 | 10.5206 | 9.9983 | 9.8344 | 9.4178 | 9.289 | 8.8452 | 8.4833 | 8.1466 | 7.6922 | 7.1834 | 5.6456 | 4.9407 | 4.6498 | 4.8284 | 14.6576 | 14.1353 | 13.9714 | 13.5548 | 13.426 | 12.9822 | 12.6203 | 12.2836 | 11.8292 | 11.3204 | 9.7826 | 9.0777 | 8.7868 | 8.9654 | 10.5258 | 10.0063 | 9.8543 | 9.4515 | 9.3586 | 8.95 | 8.6066 | 8.2958 | 7.9134 | 7.5175 | 5.359 | 0.99109 | -2.5296 | -4.7355 | 14.6628 | 14.1433 | 13.9913 | 13.5885 | 13.4956 | 13.087 | 12.7436 | 12.4328 | 12.0504 | 11.6545 | 9.496 | 5.1281 | 1.6074 | -0.59848 | 10.5034 | 9.9473 | 9.8095 | 9.4437 | 9.3728 | 9.0052 | 8.7097 | 8.4549 | 7.9917 | 6.8849 | 2.0171 | -1.9086 | -4.2744 | -3.6079 | 14.6404 | 14.0843 | 14.0843 | 13.5807 | 13.5098 | 13.1422 | 12.8467 | 12.5919 | 12.1287 | 11.0219 | 6.1541 | 2.2284 | -0.13735 | 0.5291 | 353958 | 426066 | RIBBLE | PENWORTHAM
| Tarleton | 5.2837 | 4.8402 | 4.4492 | 3.9532 | 3.425 | 2.8241 | 2.1376 | 1.434 | 0.74353 | -0.13714 | -3.4 | -5.1329 | -5.6005 | -5.2683 | 9.9207 | 9.4772 | 9.0862 | 8.5902 | 8.062 | 7.4611 | 6.7746 | 6.071 | 5.3805 | 4.4999 | 1.237 | -0.49589 | -0.96352 | -0.63125 | 5.5229 | 5.3065 | 4.87 | 4.4522 | 4.0567 | 3.5829 | 3.0069 | 2.4232 | 1.7926 | 1.1302 | -0.55123 | -2.0423 | -2.9973 | -3.525 | 10.1599 | 9.9435 | 9.507 | 9.0892 | 8.6937 | 8.2199 | 7.6439 | 7.0602 | 6.4296 | 5.7672 | 4.0858 | 2.5947 | 1.6397 | 1.112 | 5.2869 | 4.8605 | 4.4889 | 4.0133 | 3.5074 | 2.9297 | 2.266 | 1.5839 | 0.92636 | 0.13293 | -2.7718 | -4.1624 | -4.4818 | -4.0736 | 9.9239 | 9.4975 | 9.1259 | 8.6503 | 8.1444 | 7.5667 | 6.903 | 6.2209 | 5.5634 | 4.7699 | 1.8652 | 0.47457 | 0.1552 | 0.56336 | 5.3113 | 4.8729 | 4.492 | 4.0209 | 3.5081 | 2.8976 | 2.1506 | 1.3862 | 0.71868 | 0.021598 | -3.2667 | -7.0058 | -8.8974 | -10.1432 | 9.9483 | 9.5099 | 9.129 | 8.6579 | 8.1451 | 7.5346 | 6.7876 | 6.0232 | 5.3557 | 4.6586 | 1.3703 | -2.3688 | -4.2604 | -5.5062 | 5.2124 | 4.6439 | 4.2391 | 3.7736 | 3.2419 | 2.6604 | 1.9762 | 1.3121 | 0.7333 | -0.26953 | -4.9623 | -7.8483 | -8.7679 | -8.2257 | 9.8494 | 9.2809 | 9.2809 | 8.4106 | 7.8789 | 7.2974 | 6.6132 | 5.9491 | 5.3703 | 4.3675 | -0.32526 | -3.2113 | -4.1309 | -3.5887 | 344741 | 422417 | WRIGHTINGTON | PENWORTHAM
| The Height | 5.0537 | 4.8135 | 4.6152 | 4.2239 | 3.9458 | 3.4002 | 2.9732 | 2.5286 | 1.979 | 1.3854 | -0.7046 | -2.1698 | -2.9449 | -3.3689 | 15.7537 | 15.5135 | 15.3152 | 14.9239 | 14.6458 | 14.1002 | 13.6732 | 13.2286 | 12.679 | 12.0854 | 9.9954 | 8.5302 | 7.7551 | 7.3311 | 5.0665 | 4.8493 | 4.6575 | 4.2928 | 4.0633 | 3.5691 | 3.1903 | 2.794 | 2.373 | 1.882 | 0.26164 | -1.069 | -2.0729 | -2.81 | 15.7665 | 15.5493 | 15.3575 | 14.9928 | 14.7633 | 14.2691 | 13.8903 | 13.494 | 13.073 | 12.582 | 10.9616 | 9.631 | 8.6271 | 7.89 | 5.0624 | 4.8255 | 4.6378 | 4.2551 | 3.9873 | 3.4552 | 3.0397 | 2.606 | 2.0745 | 1.5252 | -0.35994 | -1.5415 | -2.1932 | -2.4467 | 15.7624 | 15.5255 | 15.3378 | 14.9551 | 14.6873 | 14.1552 | 13.7397 | 13.306 | 12.7745 | 12.2252 | 10.3401 | 9.1585 | 8.5068 | 8.2533 | 5.0601 | 4.8287 | 4.6462 | 4.2557 | 4.0108 | 3.4898 | 3.0639 | 2.6207 | 2.131 | 1.646 | -1.1137 | -5.8474 | -9.384 | -11.6432 | 15.7601 | 15.5287 | 15.3462 | 14.9557 | 14.7108 | 14.1898 | 13.7639 | 13.3207 | 12.831 | 12.346 | 9.5863 | 4.8526 | 1.316 | -0.9432 | 5.0669 | 4.79 | 4.5892 | 4.2084 | 3.976 | 3.393 | 2.9995 | 2.5925 | 2.1055 | 0.95052 | -4.351 | -8.5961 | -10.9757 | -10.5404 | 15.7669 | 15.49 | 15.49 | 14.9084 | 14.676 | 14.093 | 13.6995 | 13.2925 | 12.8055 | 11.6505 | 6.349 | 2.1039 | -0.27573 | 0.15955 | 379792 | 400497 | AGECROFT | KEARSLEY
| Thornton | 9.9223 | 9.5522 | 9.2352 | 8.8913 | 8.6401 | 8.1981 | 7.7593 | 7.2965 | 6.7811 | 6.1908 | -0.056466 | -3.2706 | -3.5248 | -3.4111 | 14.5593 | 14.1892 | 13.8722 | 13.5283 | 13.2771 | 12.8351 | 12.3963 | 11.9335 | 11.4181 | 10.8278 | 4.5805 | 1.3664 | 1.1122 | 1.2259 | 10.0659 | 9.8255 | 9.5026 | 9.1695 | 8.9647 | 8.5808 | 8.1853 | 7.7643 | 7.2957 | 6.7394 | 5.4424 | 4.3043 | 3.6319 | 3.1245 | 14.7029 | 14.4625 | 14.1396 | 13.8065 | 13.6017 | 13.2178 | 12.8223 | 12.4013 | 11.9327 | 11.3764 | 10.0794 | 8.9413 | 8.2689 | 7.7615 | 9.9277 | 9.5692 | 9.2642 | 8.9303 | 8.7036 | 8.2988 | 7.8867 | 7.426 | 6.9548 | 6.4221 | 0.37081 | -2.7109 | -2.8688 | -2.7287 | 14.5647 | 14.2062 | 13.9012 | 13.5673 | 13.3406 | 12.9358 | 12.5237 | 12.063 | 11.5918 | 11.0591 | 5.0078 | 1.9261 | 1.7682 | 1.9083 | 9.9323 | 9.5762 | 9.2806 | 8.9563 | 8.7656 | 8.381 | 7.9722 | 7.5406 | 5.262 | 4.8718 | -3.5944 | -8.4935 | -12.1004 | -14.6414 | 14.5693 | 14.2132 | 13.9176 | 13.5933 | 13.4026 | 13.018 | 12.6092 | 12.1776 | 9.899 | 9.5088 | 1.0426 | -3.8565 | -7.4634 | -10.0044 | 9.9569 | 9.5846 | 9.3011 | 9.0095 | 8.7975 | 8.4615 | 7.8525 | 7.5083 | 7.0449 | 4.8617 | -5.5442 | -9.8011 | -12.1936 | -11.5913 | 14.5939 | 14.2216 | 14.2216 | 13.6465 | 13.4345 | 13.0985 | 12.4895 | 12.1453 | 11.6819 | 9.4987 | -0.90724 | -5.1641 | -7.5566 | -6.9543 | 334207 | 442111 | BISPHAM | PENWORTHAM
| Townley St | 6.986 | 6.7729 | 6.7027 | 6.4663 | 6.2014 | 5.8862 | 5.5734 | 5.203 | 4.8571 | 4.5123 | 3.3652 | 2.93 | 2.9604 | 3.1808 | 23.244 | 23.0309 | 22.9607 | 22.7243 | 22.4594 | 22.1442 | 21.8314 | 21.461 | 21.1151 | 20.7703 | 19.6232 | 19.188 | 19.2184 | 19.4388 | 7.1376 | 7.0504 | 6.8341 | 6.5794 | 6.3246 | 6.0266 | 5.7271 | 5.364 | 5.0126 | 4.6791 | 3.7711 | 3.2209 | 2.9505 | 2.8399 | 23.3956 | 23.3084 | 23.0921 | 22.8374 | 22.5826 | 22.2846 | 21.9851 | 21.622 | 21.2706 | 20.9371 | 20.0291 | 19.4789 | 19.2085 | 19.0979 | 6.9902 | 6.7801 | 6.7073 | 6.4975 | 6.2409 | 5.9353 | 5.6317 | 5.2709 | 4.9392 | 4.6259 | 3.5622 | 3.1734 | 3.2053 | 3.4216 | 23.2482 | 23.0381 | 22.9653 | 22.7555 | 22.4989 | 22.1933 | 21.8897 | 21.5289 | 21.1972 | 20.8839 | 19.8202 | 19.4314 | 19.4633 | 19.6796 | 7.0006 | 6.8028 | 6.7468 | 6.5685 | 6.3594 | 6.1154 | 5.8851 | 5.6123 | 5.3923 | 5.2025 | 4.1428 | 1.9346 | 0.23257 | -0.83534 | 23.2586 | 23.0608 | 23.0048 | 22.8265 | 22.6174 | 22.3734 | 22.1431 | 21.8703 | 21.6503 | 21.4605 | 20.4008 | 18.1926 | 16.4906 | 15.4227 | 6.9959 | 6.784 | 6.7127 | 6.5396 | 6.3633 | 6.1685 | 5.9821 | 5.7667 | 5.5582 | 5.1229 | 2.5207 | 0.48588 | -0.58414 | -0.075466 | 23.2539 | 23.042 | 23.042 | 22.7976 | 22.6213 | 22.4265 | 22.2401 | 22.0247 | 21.8162 | 21.3809 | 18.7787 | 16.7439 | 15.6739 | 16.1825 | 387242 | 405960 | CHADDERTON | WHITEGATE
| Trafford | 2.0792 | 0.6862 | 0.68452 | 0.61438 | 0.43121 | 0.14306 | -0.19522 | -0.28323 | -0.40582 | -0.59613 | -1.599 | -3.049 | -4.1831 | -5.4559 | 9.0792 | 7.6862 | 7.6845 | 7.6144 | 7.4312 | 7.1431 | 6.8048 | 6.7168 | 6.5942 | 6.4039 | 5.401 | 3.951 | 2.8169 | 1.5441 | 2.9476 | 2.3464 | 2.257 | 2.0734 | 1.8007 | 1.4895 | 1.1187 | 0.96279 | 0.75812 | 0.51828 | -0.34454 | -1.3487 | -2.3293 | -3.101 | 9.9476 | 9.3464 | 9.257 | 9.0734 | 8.8007 | 8.4895 | 8.1187 | 7.9628 | 7.7581 | 7.5183 | 6.6555 | 5.6513 | 4.6707 | 3.899 | 2.0834 | 0.69991 | 0.69435 | 0.6239 | 0.45684 | 0.16867 | -0.16516 | -0.25381 | -0.37439 | -0.5491 | -1.3826 | -2.2349 | -3.0735 | -3.7704 | 9.0834 | 7.6999 | 7.6944 | 7.6239 | 7.4568 | 7.1687 | 6.8348 | 6.7462 | 6.6256 | 6.4509 | 5.6174 | 4.7651 | 3.9265 | 3.2296 | 2.1131 | 0.75884 | 0.80003 | 0.75568 | 0.61304 | 0.34418 | 0.042604 | -0.063568 | -0.28435 | -0.47577 | -2.4886 | -5.5214 | -7.6379 | -8.6532 | 9.1131 | 7.7588 | 7.8 | 7.7557 | 7.613 | 7.3442 | 7.0426 | 6.9364 | 6.7157 | 6.5242 | 4.5114 | 1.4786 | -0.63787 | -1.6532 | 2.0945 | 0.71423 | 0.7338 | 0.67384 | 0.52848 | 0.21147 | -0.1399 | -0.3782 | -0.72061 | -1.259 | -4.423 | -7.2865 | -8.691 | -8.5141 | 9.0945 | 7.7142 | 7.7142 | 7.6738 | 7.5285 | 7.2115 | 6.8601 | 6.6218 | 6.2794 | 5.741 | 2.577 | -0.28647 | -1.691 | -1.5141 | 380714 | 396551 | STRETFORD | SOUTH MANCHESTER
| Trafford Park North | 2.281 | 2.0685 | 1.9424 | 1.9992 | 2.0668 | 2.0929 | 1.9113 | 1.8531 | 1.7387 | 1.6592 | -8.0206 | -8.5428 | -8.3103 | -8.0881 | 7.531 | 7.3185 | 7.1924 | 7.2492 | 7.3168 | 7.3429 | 7.1613 | 7.1031 | 6.9887 | 6.9092 | -2.7706 | -3.2928 | -3.0603 | -2.8381 | 2.6681 | 2.7589 | 2.5324 | 2.5059 | 2.5211 | 2.542 | 2.3536 | 2.2355 | 2.1061 | 2.0032 | 1.5887 | 1.1368 | 0.41814 | 0.27778 | 7.9181 | 8.0089 | 7.7824 | 7.7559 | 7.7711 | 7.792 | 7.6036 | 7.4855 | 7.3561 | 7.2532 | 6.8387 | 6.3868 | 5.6681 | 5.5278 | 2.2821 | 2.0695 | 1.9422 | 1.9932 | 2.062 | 2.0858 | 1.9042 | 1.8472 | 1.7305 | 1.6528 | -7.9344 | -8.0547 | -7.7697 | -7.2655 | 7.5321 | 7.3195 | 7.1922 | 7.2432 | 7.312 | 7.3358 | 7.1542 | 7.0972 | 6.9805 | 6.9028 | -2.6844 | -2.8047 | -2.5197 | -2.0155 | 2.3117 | 2.1304 | 2.0353 | 2.1065 | 2.2179 | 2.2474 | 2.0727 | 1.997 | 1.8715 | 1.7671 | -7.4952 | -8.6433 | -8.8841 | -8.4141 | 7.5617 | 7.3804 | 7.2853 | 7.3565 | 7.4679 | 7.4974 | 7.3227 | 7.247 | 7.1215 | 7.0171 | -2.2452 | -3.3933 | -3.6341 | -3.1641 | 2.3015 | 2.1066 | 1.9973 | 2.0573 | 2.1505 | -1.6866 | -9.186 | -8.5332 | -8.1262 | -7.7761 | -8.2907 | -9.5035 | -9.5572 | -8.5597 | 7.5515 | 7.3566 | 7.3566 | 7.3073 | 7.4005 | 3.5634 | -3.936 | -3.2832 | -2.8762 | -2.5261 | -3.0407 | -4.2535 | -4.3072 | -3.3097 | 378738 | 397694 | BARTON | CARRINGTON
| Trimpell | 20.0163 | 19.9554 | 19.9292 | 19.8855 | 19.8077 | 19.7614 | 19.6921 | 19.598 | 19.5435 | 19.4529 | 18.9513 | 18.1264 | 17.4726 | 16.9079 | -3.7987 | -3.8596 | -3.8858 | -3.9295 | -4.0073 | -4.0536 | -4.1229 | -4.217 | -4.2715 | -4.3621 | -4.8637 | -5.6886 | -6.3424 | -6.9071 | 20.0991 | 20.105 | 20.0587 | 20.0001 | 19.9147 | 19.8664 | 19.7932 | 19.6942 | 19.6336 | 19.5509 | 19.1831 | 18.733 | 18.1848 | 17.8379 | -3.7159 | -3.71 | -3.7563 | -3.8149 | -3.9003 | -3.9486 | -4.0218 | -4.1208 | -4.1814 | -4.2641 | -4.6319 | -5.082 | -5.6302 | -5.9771 | 20.0178 | 19.9595 | 19.9362 | 19.8938 | 19.8179 | 19.7733 | 19.7059 | 19.6139 | 19.5624 | 19.479 | 19.0614 | 18.5782 | 18.0752 | 17.8163 | -3.7972 | -3.8555 | -3.8788 | -3.9212 | -3.9971 | -4.0417 | -4.1091 | -4.2011 | -4.2526 | -4.336 | -4.7536 | -5.2368 | -5.7398 | -5.9987 | 20.0191 | 19.961 | 19.9382 | 19.8967 | 19.8222 | 19.7695 | 19.6795 | 19.5575 | 19.4759 | 19.3687 | 18.308 | 16.4177 | 14.7252 | 14.2113 | -3.7959 | -3.854 | -3.8768 | -3.9183 | -3.9928 | -4.0455 | -4.1355 | -4.2575 | -4.3391 | -4.4463 | -5.507 | -7.3973 | -9.0898 | -9.6037 | 20.0187 | 19.9564 | 19.9301 | 19.8846 | 19.7996 | 19.7298 | 19.6173 | 19.4639 | 19.3255 | 19.0137 | 17.2242 | 15.3335 | 14.009 | 14.3296 | -3.7963 | -3.8586 | -3.8586 | -3.9304 | -4.0154 | -4.0852 | -4.1977 | -4.3511 | -4.4895 | -4.8013 | -6.5908 | -8.4815 | -9.806 | -9.4854 | 341861 | 458979 | - | HEYSHAM
| Trinity | 25.974 | 23.5231 | 22.7899 | 22.6763 | 22.5781 | 22.5211 | 22.3083 | 22.1541 | 22.0561 | 21.8326 | 21.4671 | 21.2493 | 21.0747 | 21.0453 | 11.474 | 9.0231 | 8.2899 | 8.1763 | 8.0781 | 8.0211 | 7.8083 | 7.6541 | 7.5561 | 7.3326 | 6.9671 | 6.7493 | 6.5747 | 6.5453 | 27.4752 | 26.3504 | 25.8331 | 25.6093 | 25.4126 | 25.2742 | 24.985 | 24.7314 | 24.5132 | 24.1566 | 23.7479 | 23.4543 | 23.1999 | 23.1574 | 12.9752 | 11.8504 | 11.3331 | 11.1093 | 10.9126 | 10.7742 | 10.485 | 10.2314 | 10.0132 | 9.6566 | 9.2479 | 8.9543 | 8.6999 | 8.6574 | 26.04 | 23.5342 | 22.927 | 22.8328 | 22.7445 | 22.6882 | 22.4889 | 22.3417 | 22.2584 | 22.059 | 21.7125 | 21.5414 | 21.3229 | 21.1644 | 11.54 | 9.0342 | 8.427 | 8.3328 | 8.2445 | 8.1882 | 7.9889 | 7.8417 | 7.7584 | 7.559 | 7.2125 | 7.0414 | 6.8229 | 6.6644 | 26.0021 | 23.5854 | 22.8893 | 22.8064 | 22.7389 | 22.7112 | 22.5287 | 22.404 | 22.3354 | 22.1481 | 21.9028 | 20.5088 | 19.2565 | 18.3764 | 11.5021 | 9.0854 | 8.3893 | 8.3064 | 8.2389 | 8.2112 | 8.0287 | 7.904 | 7.8354 | 7.6481 | 7.4028 | 6.0088 | 4.7565 | 3.8764 | 26.0121 | 23.6032 | 22.9201 | 22.8581 | 22.8123 | 22.8075 | 22.6468 | 22.5377 | 22.4913 | 22.2971 | 20.8675 | 19.4293 | 18.5255 | 18.6798 | 11.5121 | 9.1032 | 9.1032 | 8.3581 | 8.3123 | 8.3075 | 8.1468 | 8.0377 | 7.9913 | 7.7971 | 6.3675 | 4.9293 | 4.0255 | 4.1798 | 382649 | 398230 | FREDERICK RD | KEARSLEY
| Tulketh | 6.5456 | 5.4823 | 4.7859 | 4.2971 | 4.1333 | 3.6065 | 3.0371 | 2.5459 | 2.0837 | 1.3862 | -0.71671 | -1.6419 | -1.9088 | -1.5643 | 10.6826 | 9.6193 | 8.9229 | 8.4341 | 8.2703 | 7.7435 | 7.1741 | 6.6829 | 6.2207 | 5.5232 | 3.4203 | 2.4951 | 2.2282 | 2.5727 | 7.1236 | 6.5899 | 6.003 | 5.5241 | 5.3705 | 4.8792 | 4.3366 | 3.8594 | 3.3954 | 2.7691 | 1.1878 | 0.24609 | -0.33603 | -0.50128 | 11.2606 | 10.7269 | 10.14 | 9.6611 | 9.5075 | 9.0162 | 8.4736 | 7.9964 | 7.5324 | 6.9061 | 5.3248 | 4.3831 | 3.801 | 3.6357 | 6.5564 | 5.5112 | 4.852 | 4.3717 | 4.2358 | 3.7314 | 3.1842 | 2.7135 | 2.2796 | 1.6459 | -0.25421 | -1.048 | -1.2634 | -0.93675 | 10.6934 | 9.6482 | 8.989 | 8.5087 | 8.3728 | 7.8684 | 7.3212 | 6.8505 | 6.4166 | 5.7829 | 3.8828 | 3.089 | 2.8736 | 3.2003 | 6.5615 | 5.511 | 4.8291 | 4.3483 | 4.219 | 3.7259 | 3.1769 | 2.7041 | 2.3294 | 1.7871 | -1.3199 | -8.1536 | -13.8352 | -17.4399 | 10.6985 | 9.648 | 8.9661 | 8.4853 | 8.356 | 7.8629 | 7.3139 | 6.8411 | 6.4664 | 5.9241 | 2.8171 | -4.0166 | -9.6982 | -13.3029 | 6.5662 | 5.4829 | 4.7984 | 4.3501 | 4.2664 | 3.8434 | 3.3631 | 2.9747 | 2.4623 | 0.68125 | -7.2019 | -13.3478 | -17.1651 | -15.9232 | 10.7032 | 9.6199 | 9.6199 | 8.4871 | 8.4034 | 7.9804 | 7.5001 | 7.1117 | 6.5993 | 4.8183 | -3.0649 | -9.2108 | -13.0281 | -11.7862 | 352393 | 431036 | RIBBLE | PENWORTHAM
| Ulverston | 4.5878 | 3.7558 | 3.2723 | 3.0424 | 2.8012 | 2.4791 | 2.1274 | 1.8161 | 1.4877 | 1.0593 | -0.39729 | -1.166 | -1.381 | -1.2122 | 7.5878 | 6.7558 | 6.2723 | 6.0424 | 5.8012 | 5.4791 | 5.1274 | 4.8161 | 4.4877 | 4.0593 | 2.6027 | 1.834 | 1.619 | 1.7878 | 5.0031 | 4.5647 | 4.1668 | 3.9297 | 3.6906 | 3.3786 | 3.0318 | 2.7158 | 2.3769 | 2.0046 | 1.0442 | 0.28048 | -0.17916 | -0.43333 | 8.0031 | 7.5647 | 7.1668 | 6.9297 | 6.6906 | 6.3786 | 6.0318 | 5.7158 | 5.3769 | 5.0046 | 4.0442 | 3.2805 | 2.8208 | 2.5667 | 4.596 | 3.776 | 3.3055 | 3.0889 | 2.8618 | 2.5553 | 2.2191 | 1.9221 | 1.6136 | 1.2275 | -0.091905 | -0.76231 | -0.94051 | -0.77619 | 7.596 | 6.776 | 6.3055 | 6.0889 | 5.8618 | 5.5553 | 5.2191 | 4.9221 | 4.6136 | 4.2275 | 2.9081 | 2.2377 | 2.0595 | 2.2238 | 4.596 | 3.7637 | 3.2786 | 3.0454 | 2.8053 | 2.4773 | 2.0999 | 1.7629 | 1.4579 | 1.1222 | -0.82792 | -4.7784 | -7.7654 | -9.7492 | 7.596 | 6.7637 | 6.2786 | 6.0454 | 5.8053 | 5.4773 | 5.0999 | 4.7629 | 4.4579 | 4.1222 | 2.1721 | -1.7784 | -4.7654 | -6.7492 | 4.6068 | 3.7642 | 3.2811 | 3.0638 | 2.8339 | 2.537 | 2.2046 | 1.9247 | 1.5662 | 0.56999 | -3.9703 | -7.4861 | -9.424 | -8.7478 | 7.6068 | 6.7642 | 6.7642 | 6.0638 | 5.8339 | 5.537 | 5.2046 | 4.9247 | 4.5662 | 3.57 | -0.97032 | -4.4861 | -6.424 | -5.7478 | 327495 | 477808 | ULVERSTON | HARKER
| Union Rd | 6.9779 | 6.3965 | 6.5561 | 6.0564 | 6.0826 | 5.5652 | 5.1876 | 4.9722 | 4.4066 | 3.3101 | 1.5699 | -0.16508 | -0.80791 | -0.83067 | 11.6149 | 11.0335 | 11.1931 | 10.6934 | 10.7196 | 10.2022 | 9.8246 | 9.6092 | 9.0436 | 7.9471 | 6.2069 | 4.4719 | 3.8291 | 3.8063 | 7.1167 | 6.6401 | 6.6795 | 6.1409 | 6.1522 | 5.6339 | 5.2453 | 4.9363 | 4.4168 | 3.8688 | 2.5734 | 1.6569 | 0.89128 | 0.51869 | 11.7537 | 11.2771 | 11.3165 | 10.7779 | 10.7892 | 10.2709 | 9.8823 | 9.5733 | 9.0538 | 8.5058 | 7.2104 | 6.2939 | 5.5283 | 5.1557 | 6.9512 | 6.4406 | 6.6185 | 6.1415 | 6.1818 | 5.6881 | 5.3308 | 5.1319 | 4.5974 | 3.5558 | 1.9913 | 0.4752 | 0.079067 | 0.20528 | 11.5882 | 11.0776 | 11.2555 | 10.7785 | 10.8188 | 10.3251 | 9.9678 | 9.7689 | 9.2344 | 8.1928 | 6.6283 | 5.1122 | 4.7161 | 4.8423 | 6.9839 | 6.4069 | 6.5706 | 6.0687 | 6.0928 | 5.5584 | 5.1319 | 4.3192 | 3.7762 | 3.2896 | -0.029662 | -5.4963 | -9.8502 | -12.5625 | 11.6209 | 11.0439 | 11.2076 | 10.7057 | 10.7298 | 10.1954 | 9.7689 | 8.9562 | 8.4132 | 7.9266 | 4.6073 | -0.8593 | -5.2132 | -7.9255 | 7.0151 | 6.4523 | 6.6383 | 6.1878 | 6.2485 | 4.4699 | 3.6078 | 3.4972 | 2.9988 | 1.6504 | -4.2982 | -9.0882 | -11.9723 | -10.9436 | 11.6521 | 11.0893 | 11.0893 | 10.8248 | 10.8855 | 9.1069 | 8.2448 | 8.1342 | 7.6358 | 6.2874 | 0.33877 | -4.4512 | -7.3353 | -6.3066 | 372174 | 410598 | BOLTON | KEARSLEY
| Upholland | 3.5455 | 3.0929 | 2.7661 | 2.3334 | 1.7851 | 1.1926 | 0.54517 | -0.12648 | -0.78087 | -1.5937 | -4.4397 | -5.7218 | -5.7761 | -5.1665 | 7.0455 | 6.5929 | 6.2661 | 5.8334 | 5.2851 | 4.6926 | 4.0452 | 3.3735 | 2.7191 | 1.9063 | -0.93971 | -2.2218 | -2.2761 | -1.6665 | 3.7536 | 3.5037 | 3.1113 | 2.7651 | 2.3454 | 1.8935 | 1.392 | 0.86792 | 0.33538 | -0.2017 | -1.9469 | -3.1799 | -3.8506 | -4.1877 | 7.2536 | 7.0037 | 6.6113 | 6.2651 | 5.8454 | 5.3935 | 4.892 | 4.3679 | 3.8354 | 3.2983 | 1.5531 | 0.32011 | -0.3506 | -0.68768 | 3.5618 | 3.1472 | 2.8122 | 2.3987 | 1.8761 | 1.31 | 0.68865 | 0.042074 | -0.57823 | -1.3076 | -3.9483 | -5.0583 | -5.0734 | -4.5693 | 7.0618 | 6.6472 | 6.3122 | 5.8987 | 5.3761 | 4.81 | 4.1887 | 3.5421 | 2.9218 | 2.1924 | -0.44833 | -1.5583 | -1.5734 | -1.0693 | 3.5722 | 3.1544 | 2.8168 | 2.4283 | 1.9469 | 1.4142 | 0.79427 | 0.15311 | -0.38507 | -0.93199 | -3.9172 | -9.4198 | -13.3091 | -16.0132 | 7.0722 | 6.6544 | 6.3168 | 5.9283 | 5.4469 | 4.9142 | 4.2943 | 3.6531 | 3.1149 | 2.568 | -0.41716 | -5.9198 | -9.8091 | -12.5132 | 3.5206 | 3.0075 | 2.675 | 2.2989 | 1.8267 | 1.3517 | 0.82183 | 0.3085 | -0.25224 | -1.618 | -7.9061 | -12.5304 | -14.9283 | -13.9215 | 7.0206 | 6.5075 | 6.5075 | 5.7989 | 5.3267 | 4.8517 | 4.3218 | 3.8085 | 3.2478 | 1.882 | -4.4061 | -9.0304 | -11.4283 | -10.4215 | 352531 | 404369 | ORRELL | KIRKBY
| Urmston | 11.4837 | 11.1408 | 11.0147 | 10.8199 | 10.5093 | 10.1294 | 9.6789 | 9.3815 | 8.9775 | 8.5447 | 7.0274 | 6.2699 | 6.1047 | 6.2136 | 16.1207 | 15.7778 | 15.6517 | 15.4569 | 15.1463 | 14.7664 | 14.3159 | 14.0185 | 13.6145 | 13.1817 | 11.6644 | 10.9069 | 10.7417 | 10.8506 | 11.6269 | 11.4039 | 11.2039 | 11.0035 | 10.7165 | 10.3713 | 9.9535 | 9.684 | 9.302 | 8.9333 | 7.8239 | 7.0835 | 6.7039 | 6.4905 | 16.2639 | 16.0409 | 15.8409 | 15.6405 | 15.3535 | 15.0083 | 14.5905 | 14.321 | 13.939 | 13.5703 | 12.4609 | 11.7205 | 11.3409 | 11.1275 | 11.4941 | 11.1675 | 11.0563 | 10.8727 | 10.5778 | 10.2143 | 9.7805 | 9.4966 | 9.1136 | 8.722 | 7.3453 | 6.677 | 6.538 | 6.6476 | 16.1311 | 15.8045 | 15.6933 | 15.5097 | 15.2148 | 14.8513 | 14.4175 | 14.1336 | 13.7506 | 13.359 | 11.9823 | 11.314 | 11.175 | 11.2846 | 11.4969 | 11.1684 | 11.0578 | 10.8757 | 10.5915 | 10.24 | 9.8112 | 9.5334 | 9.1949 | 8.8675 | 6.6854 | 1.9056 | -1.9612 | -4.6613 | 16.1339 | 15.8054 | 15.6948 | 15.5127 | 15.2285 | 14.877 | 14.4482 | 14.1704 | 13.8319 | 13.5045 | 11.3224 | 6.5426 | 2.6758 | -0.024257 | 11.4949 | 11.1385 | 11.0296 | 10.8782 | 10.6312 | 10.3348 | 9.9573 | 9.7422 | 9.3147 | 8.1611 | 2.8089 | -1.5178 | -4.0862 | -3.4417 | 16.1319 | 15.7755 | 15.7755 | 15.5152 | 15.2682 | 14.9718 | 14.5943 | 14.3792 | 13.9517 | 12.7981 | 7.4459 | 3.1192 | 0.55078 | 1.1953 | 377117 | 395709 | STRETFORD | SOUTH MANCHESTER
| Victoria Park | 4.0739 | 3.7178 | 1.5263 | -0.56936 | -2.6743 | -4.9038 | -7.1681 | -0.24208 | -1.3856 | -2.4818 | -2.5836 | -2.7656 | -2.7009 | -2.394 | 10.5739 | 10.2178 | 8.0263 | 5.9306 | 3.8257 | 1.5962 | -0.66806 | -1.7421 | -2.8856 | -3.9818 | -4.0836 | -4.2656 | -4.2009 | -3.894 | 4.6793 | 4.8307 | 2.4675 | 0.22236 | -1.9877 | -4.2579 | -6.5851 | -7.7396 | -8.9778 | -10.18 | -10.3983 | -10.7782 | -10.8774 | -10.631 | 11.1793 | 11.3307 | 8.9675 | 6.7224 | 4.5123 | 2.2421 | -0.085114 | -1.2396 | -2.4778 | -3.68 | -3.8983 | -4.2782 | -4.3774 | -4.131 | 4.0742 | 3.7215 | 1.5345 | -0.54965 | -2.6491 | -4.8725 | -7.1301 | -8.198 | -9.334 | -10.4341 | -10.5095 | -10.6971 | -10.6155 | -10.3126 | 10.5742 | 10.2215 | 8.0345 | 5.9504 | 3.8509 | 1.6275 | -0.63014 | -1.698 | -2.834 | -3.9341 | -4.0095 | -4.1971 | -4.1155 | -3.8126 | 4.1198 | 3.8113 | 1.668 | -0.37864 | -2.4339 | -4.6122 | -6.8231 | -7.8447 | -8.9335 | -9.975 | -9.7913 | -9.774 | -9.4864 | -8.9405 | 10.6198 | 10.3113 | 8.168 | 6.1214 | 4.0661 | 1.8878 | -0.32314 | -1.3447 | -2.4335 | -3.475 | -3.2913 | -3.274 | -2.9864 | -2.4405 | 4.1155 | 3.8022 | 1.6633 | -0.37346 | -2.4184 | -4.5833 | -6.781 | -7.7864 | -8.8565 | -9.9078 | -9.7808 | -9.7308 | -9.3874 | -8.7273 | 10.6155 | 10.3022 | 10.3022 | 6.1265 | 4.0816 | 1.9167 | -0.28105 | -1.2864 | -2.3565 | -3.4078 | -3.2808 | -3.2308 | -2.8874 | -2.2273 | 385373 | 395948 | LONGSIGHT | BREDBURY
| Warbreck | 7.3972 | 7.2429 | 7.1421 | 6.9099 | 6.7642 | 6.4993 | 6.2432 | 5.9542 | 5.6805 | 5.3358 | 4.2784 | 3.701 | 3.5821 | 3.6173 | 10.8972 | 10.7429 | 10.6421 | 10.4099 | 10.2642 | 9.9993 | 9.7432 | 9.4542 | 9.1805 | 8.8358 | 7.7784 | 7.201 | 7.0821 | 7.1173 | 7.4994 | 7.4287 | 7.2854 | 7.0665 | 6.9557 | 6.7312 | 6.5123 | 6.2606 | 6.0152 | 5.7354 | 5.0016 | 4.5038 | 4.2497 | 4.1039 | 10.9994 | 10.9287 | 10.7854 | 10.5665 | 10.4557 | 10.2312 | 10.0123 | 9.7606 | 9.5152 | 9.2354 | 8.5016 | 8.0038 | 7.7497 | 7.6039 | 7.4029 | 7.2564 | 7.1637 | 6.938 | 6.7988 | 6.5417 | 6.2927 | 6.0105 | 5.7483 | 5.4352 | 4.5066 | 4.1071 | 4.0502 | 4.1831 | 10.9029 | 10.7564 | 10.6637 | 10.438 | 10.2988 | 10.0417 | 9.7927 | 9.5105 | 9.2483 | 8.9352 | 8.0066 | 7.6071 | 7.5502 | 7.6831 | 7.4084 | 7.267 | 7.1854 | 6.9765 | 6.8609 | 6.6244 | 6.3886 | 6.1196 | 5.9046 | 5.6537 | 4.0591 | 0.68022 | -1.8976 | -3.673 | 10.9084 | 10.767 | 10.6854 | 10.4765 | 10.3609 | 10.1244 | 9.8886 | 9.6196 | 9.4046 | 9.1537 | 7.5591 | 4.1802 | 1.6024 | -0.17301 | 7.4078 | 7.2375 | 7.1481 | 6.96 | 6.8689 | 6.668 | 6.4591 | 6.2237 | 5.9524 | 5.1328 | 1.3537 | -1.7149 | -3.3587 | -2.7645 | 10.9078 | 10.7375 | 10.7375 | 10.46 | 10.3689 | 10.168 | 9.9591 | 9.7237 | 9.4524 | 8.6328 | 4.8537 | 1.7851 | 0.14129 | 0.73548 | 331775 | 438420 | BISPHAM | PENWORTHAM
| Wardleworth | 9.4002 | 9.2351 | 9.0096 | 8.9641 | 8.8097 | 8.3974 | 8.0131 | 7.7115 | 7.5999 | 7.1405 | 5.597 | 4.8051 | 4.5845 | 4.4147 | 14.0372 | 13.8721 | 13.6466 | 13.6011 | 13.4467 | 13.0344 | 12.6501 | 12.3485 | 12.2369 | 11.7775 | 10.234 | 9.4421 | 9.2215 | 9.0517 | 9.6459 | 9.6793 | 9.3492 | 9.2499 | 9.0721 | 8.6678 | 8.2812 | 7.9707 | 7.6708 | 7.2496 | 6.0472 | 5.193 | 4.6588 | 4.3439 | 14.2829 | 14.3163 | 13.9862 | 13.8869 | 13.7091 | 13.3048 | 12.9182 | 12.6077 | 12.3078 | 11.8866 | 10.6842 | 9.83 | 9.2958 | 8.9809 | 9.407 | 9.2488 | 9.0324 | 8.9937 | 8.8481 | 8.4469 | 8.0733 | 7.7817 | 7.6857 | 7.3243 | 5.8936 | 5.1784 | 4.973 | 4.8738 | 14.044 | 13.8858 | 13.6694 | 13.6307 | 13.4851 | 13.0839 | 12.7103 | 12.4187 | 12.3227 | 11.9613 | 10.5306 | 9.8154 | 9.61 | 9.5108 | 9.4156 | 9.2629 | 9.0453 | 8.9993 | 8.8439 | 8.4189 | 7.9965 | 7.6478 | 7.5139 | 7.131 | 5.4272 | 1.4512 | -1.6772 | -3.8129 | 14.0526 | 13.8999 | 13.6823 | 13.6363 | 13.4809 | 13.0559 | 12.6335 | 12.2848 | 12.1509 | 11.768 | 10.0642 | 6.0882 | 2.9598 | 0.82407 | 9.436 | 9.2874 | 9.0781 | 9.0529 | 8.9122 | 8.5155 | 8.1276 | 7.8189 | 7.6477 | 6.7404 | 2.4316 | -1.1887 | -3.2748 | -2.8148 | 14.073 | 13.9244 | 13.9244 | 13.6899 | 13.5492 | 13.1525 | 12.7646 | 12.4559 | 12.2847 | 11.3774 | 7.0686 | 3.4483 | 1.3622 | 1.8222 | 390339 | 414050 | BELFIELD | ROCHDALE
| Warton | 8.906 | 8.4808 | 8.3735 | 8.204 | 7.9597 | 7.6959 | 7.4017 | 7.0134 | 6.7577 | 6.5581 | 5.5454 | 5.0854 | 5.0526 | 5.3114 | 13.543 | 13.1178 | 13.0105 | 12.841 | 12.5967 | 12.3329 | 12.0387 | 11.6504 | 11.3947 | 11.1951 | 10.1824 | 9.7224 | 9.6896 | 9.9484 | 9.2943 | 9.2099 | 8.9936 | 8.7786 | 8.5226 | 8.2897 | 8.0159 | 7.708 | 7.4346 | 7.2674 | 6.5453 | 6.0638 | 5.8363 | 5.8176 | 13.9313 | 13.8469 | 13.6306 | 13.4156 | 13.1596 | 12.9267 | 12.6529 | 12.345 | 12.0716 | 11.9044 | 11.1823 | 10.7008 | 10.4733 | 10.4546 | 8.9084 | 8.4859 | 8.3814 | 8.215 | 7.9745 | 7.715 | 7.4252 | 7.0415 | 6.7924 | 6.6057 | 5.6264 | 5.1854 | 5.1565 | 5.4096 | 13.5454 | 13.1229 | 13.0184 | 12.852 | 12.6115 | 12.352 | 12.0622 | 11.6785 | 11.4294 | 11.2427 | 10.2634 | 9.8224 | 9.7935 | 10.0466 | 8.9371 | 8.5351 | 8.4514 | 8.3205 | 8.1129 | 7.8076 | 7.5338 | 7.226 | 6.9956 | 6.8763 | 4.9808 | 4.1328 | 3.5363 | 2.8923 | 13.5741 | 13.1721 | 13.0884 | 12.9575 | 12.7499 | 12.4446 | 12.1708 | 11.863 | 11.6326 | 11.5133 | 9.6178 | 8.7698 | 8.1733 | 7.5293 | 8.9415 | 8.5313 | 8.4431 | 8.3086 | 8.03 | 7.8137 | 7.5651 | 5.8453 | 5.7337 | 5.6164 | 4.5608 | 3.9179 | 3.6001 | 3.8127 | 13.5785 | 13.1683 | 13.1683 | 12.9456 | 12.667 | 12.4507 | 12.2021 | 10.4823 | 10.3707 | 10.2534 | 9.1978 | 8.5549 | 8.2371 | 8.4497 | 341290 | 428540 | PEEL | PENWORTHAM
| Waterhead | 14.5583 | 14.3988 | 14.2598 | 14.1285 | 13.8565 | 13.5944 | 13.3471 | 13.056 | 12.7405 | 12.3927 | 11.1959 | 10.5456 | 10.3458 | 10.39 | 19.1953 | 19.0358 | 18.8968 | 18.7655 | 18.4935 | 18.2314 | 17.9841 | 17.693 | 17.3775 | 17.0297 | 15.8329 | 15.1826 | 14.9828 | 15.027 | 14.6014 | 14.4739 | 14.2882 | 14.1636 | 13.9152 | 13.6786 | 13.4538 | 13.1856 | 12.8895 | 12.6071 | 11.7592 | 11.1248 | 10.7307 | 10.4607 | 19.2384 | 19.1109 | 18.9252 | 18.8006 | 18.5522 | 18.3156 | 18.0908 | 17.8226 | 17.5265 | 17.2441 | 16.3962 | 15.7618 | 15.3677 | 15.0977 | 14.5653 | 14.4132 | 14.2816 | 14.1572 | 13.8948 | 13.6421 | 13.4034 | 13.1212 | 12.8194 | 12.5036 | 11.4164 | 10.8466 | 10.6673 | 10.7046 | 19.2023 | 19.0502 | 18.9186 | 18.7942 | 18.5318 | 18.2791 | 18.0404 | 17.7582 | 17.4564 | 17.1406 | 16.0534 | 15.4836 | 15.3043 | 15.3416 | 14.5615 | 14.4025 | 14.2655 | 14.1374 | 13.8786 | 13.6255 | 13.3703 | 13.0702 | 12.7894 | 12.5218 | 10.7596 | 6.8241 | 3.71 | 1.5981 | 19.1985 | 19.0395 | 18.9025 | 18.7744 | 18.5156 | 18.2625 | 18.0073 | 17.7072 | 17.4264 | 17.1588 | 15.3966 | 11.4611 | 8.347 | 6.2351 | 14.5931 | 14.4407 | 14.3092 | 14.2075 | 13.9727 | 13.7602 | 13.5513 | 13.3057 | 12.9549 | 12.005 | 7.6118 | 4.0786 | 2.0328 | 2.5997 | 19.2301 | 19.0777 | 19.0777 | 18.8445 | 18.6097 | 18.3972 | 18.1883 | 17.9427 | 17.5919 | 16.642 | 12.2488 | 8.7156 | 6.6698 | 7.2367 | 394942 | 405940 | GREENHILL | WHITEGATE
| Waterswallows | 12.3712 | 11.9716 | 11.9272 | 11.829 | 11.7615 | 11.5135 | 11.225 | 10.9759 | 10.7013 | 10.3993 | 9.0731 | 7.9866 | 7.1217 | 6.2091 | 17.0082 | 16.6086 | 16.5642 | 16.466 | 16.3985 | 16.1505 | 15.862 | 15.6129 | 15.3383 | 15.0363 | 13.7101 | 12.6236 | 11.7587 | 10.8461 | 12.7211 | 12.6247 | 12.4939 | 12.3485 | 12.2294 | 11.9885 | 11.8 | 11.6403 | 11.4021 | 11.1608 | 10.2293 | 9.4366 | 8.7693 | 8.3288 | 17.3581 | 17.2617 | 17.1309 | 16.9855 | 16.8664 | 16.6255 | 16.437 | 16.2773 | 16.0391 | 15.7978 | 14.8663 | 14.0736 | 13.4063 | 12.9658 | 12.3716 | 11.974 | 11.9315 | 11.8359 | 11.7716 | 11.5555 | 11.2679 | 11.0221 | 10.7556 | 10.4782 | 9.3368 | 8.6441 | 7.9315 | 7.3581 | 17.0086 | 16.611 | 16.5685 | 16.4729 | 16.4086 | 16.1925 | 15.9049 | 15.6591 | 15.3926 | 15.1152 | 13.9738 | 13.2811 | 12.5685 | 11.9951 | 12.3905 | 12.0056 | 11.9709 | 11.8795 | 11.8056 | 11.5571 | 11.2652 | 10.9305 | 10.5713 | 10.1815 | 7.9768 | 5.5738 | 4.2092 | 3.5873 | 17.0275 | 16.6426 | 16.6079 | 16.5165 | 16.4426 | 16.1941 | 15.9022 | 15.5675 | 15.2083 | 14.8185 | 12.6138 | 10.2108 | 8.8462 | 8.2243 | 12.3791 | 11.9748 | 11.9256 | 11.8205 | 11.6856 | 11.4098 | 10.9871 | 10.6099 | 10.1868 | 9.6561 | 7.1313 | 5.1848 | 4.4802 | 4.6008 | 17.0161 | 16.6118 | 16.6118 | 16.4575 | 16.3226 | 16.0468 | 15.6241 | 15.2469 | 14.8238 | 14.2931 | 11.7683 | 9.8218 | 9.1172 | 9.2378 | 407734 | 375459 | BUXTON | STALYBRIDGE
| Weaste | 4.9827 | 4.4304 | 4.2628 | 4.1384 | 3.9794 | 3.5408 | 3.3074 | 3.1194 | 2.724 | 2.4188 | 1.3676 | 0.1797 | -0.53086 | -1.3219 | 11.9827 | 11.4304 | 11.2628 | 11.1384 | 10.9794 | 10.5408 | 10.3074 | 10.1194 | 9.724 | 9.4188 | 8.3676 | 7.1797 | 6.4691 | 5.6781 | 5.3972 | 5.1941 | 4.9203 | 4.6729 | 4.4575 | 4.0458 | 3.7925 | 3.5759 | 3.1466 | 2.7281 | 1.8862 | 0.99217 | 0.2647 | -0.27716 | 12.3972 | 12.1941 | 11.9203 | 11.6729 | 11.4575 | 11.0458 | 10.7925 | 10.5759 | 10.1466 | 9.7281 | 8.8862 | 7.9922 | 7.2647 | 6.7228 | 4.9864 | 4.4435 | 4.2747 | 4.1595 | 3.9985 | 3.566 | 3.3375 | 3.154 | 2.7674 | 2.4798 | 1.5532 | 0.69407 | 0.12466 | -0.29494 | 11.9864 | 11.4435 | 11.2747 | 11.1595 | 10.9985 | 10.566 | 10.3375 | 10.154 | 9.7674 | 9.4798 | 8.5532 | 7.6941 | 7.1247 | 6.7051 | 5.0146 | 4.4833 | 4.3656 | 4.2388 | 4.1049 | 3.735 | 3.5131 | 3.3237 | 2.9259 | 2.6131 | 0.85279 | -2.2714 | -4.5755 | -5.9485 | 12.0146 | 11.4833 | 11.3656 | 11.2388 | 11.1049 | 10.735 | 10.5131 | 10.3237 | 9.9259 | 9.6131 | 7.8528 | 4.7286 | 2.4245 | 1.0515 | 5.0055 | 4.4671 | 4.3192 | 4.2166 | 4.0831 | 3.6919 | 3.4486 | 3.2352 | 2.7984 | 2.2756 | -1.1324 | -3.975 | -5.544 | -5.3547 | 12.0055 | 11.4671 | 11.4671 | 11.2166 | 11.0831 | 10.6919 | 10.4486 | 10.2352 | 9.7984 | 9.2756 | 5.8676 | 3.025 | 1.456 | 1.6453 | 378751 | 398897 | FREDERICK RD | KEARSLEY
| Werneth | 13.6157 | 13.4303 | 13.2727 | 13.0166 | 12.836 | 12.5413 | 12.2785 | 11.956 | 11.6036 | 11.2422 | 9.8491 | 8.9794 | 8.6376 | 8.5645 | 18.2527 | 18.0673 | 17.9097 | 17.6536 | 17.473 | 17.1783 | 16.9155 | 16.593 | 16.2406 | 15.8792 | 14.4861 | 13.6164 | 13.2746 | 13.2015 | 13.6558 | 13.4982 | 13.2929 | 13.0428 | 12.8856 | 12.6148 | 12.3716 | 12.067 | 11.7241 | 11.3909 | 10.367 | 9.6626 | 9.2547 | 9.0146 | 18.2928 | 18.1352 | 17.9299 | 17.6798 | 17.5226 | 17.2518 | 17.0086 | 16.704 | 16.3611 | 16.0279 | 15.004 | 14.2996 | 13.8917 | 13.6516 | 13.6239 | 13.4472 | 13.2982 | 13.0511 | 12.8795 | 12.5959 | 12.3432 | 12.0315 | 11.6958 | 11.3707 | 10.1082 | 9.3847 | 9.1318 | 9.1245 | 18.2609 | 18.0842 | 17.9352 | 17.6881 | 17.5165 | 17.2329 | 16.9802 | 16.6685 | 16.3328 | 16.0077 | 14.7452 | 14.0217 | 13.7688 | 13.7615 | 13.6197 | 13.4394 | 13.291 | 13.0453 | 12.8862 | 12.613 | 12.3628 | 12.0514 | 11.7514 | 11.4786 | 9.6846 | 5.9117 | 2.9807 | 1.0551 | 18.2567 | 18.0764 | 17.928 | 17.6823 | 17.5232 | 17.25 | 16.9998 | 16.6884 | 16.3884 | 16.1156 | 14.3216 | 10.5487 | 7.6177 | 5.6921 | 13.5978 | 13.4146 | 13.2931 | 13.0977 | 12.9868 | 12.7735 | 12.5741 | 12.3208 | 11.9699 | 11.0745 | 6.8812 | 3.5188 | 1.5989 | 2.1526 | 18.2348 | 18.0516 | 18.0516 | 17.7347 | 17.6238 | 17.4105 | 17.2111 | 16.9578 | 16.6069 | 15.7115 | 11.5182 | 8.1558 | 6.2359 | 6.7896 | 391273 | 403453 | GREENHILL | WHITEGATE
| Wesley Place Bacup | 12.6539 | 12.4577 | 12.3221 | 12.1236 | 11.8978 | 11.628 | 11.3098 | 10.9585 | 10.6177 | 10.2137 | 8.7063 | 7.847 | 7.5839 | 7.5439 | 17.2909 | 17.0947 | 16.9591 | 16.7606 | 16.5348 | 16.265 | 15.9468 | 15.5955 | 15.2547 | 14.8507 | 13.3433 | 12.484 | 12.2209 | 12.1809 | 12.7264 | 12.5854 | 12.3804 | 12.165 | 11.9336 | 11.6432 | 11.3147 | 10.9612 | 10.6073 | 10.2333 | 9.1884 | 8.4277 | 7.9706 | 7.6269 | 17.3634 | 17.2224 | 17.0174 | 16.802 | 16.5706 | 16.2802 | 15.9517 | 15.5982 | 15.2443 | 14.8703 | 13.8254 | 13.0647 | 12.6076 | 12.2639 | 12.6639 | 12.4809 | 12.3587 | 12.1728 | 11.9621 | 11.7078 | 11.417 | 11.0828 | 10.7637 | 10.3948 | 8.9875 | 8.2615 | 8.0459 | 8.0584 | 17.3009 | 17.1179 | 16.9957 | 16.8098 | 16.5991 | 16.3448 | 16.054 | 15.7198 | 15.4007 | 15.0318 | 13.6245 | 12.8985 | 12.6829 | 12.6954 | 12.6572 | 12.459 | 12.3195 | 12.1125 | 11.8849 | 11.6066 | 11.2909 | 10.9555 | 10.6553 | 10.3433 | 8.2599 | 3.5933 | -0.054897 | -2.4857 | 17.2942 | 17.096 | 16.9565 | 16.7495 | 16.5219 | 16.2436 | 15.9279 | 15.5925 | 15.2923 | 14.9803 | 12.8969 | 8.2303 | 4.5821 | 2.1513 | 12.682 | 12.4929 | 12.372 | 12.2007 | 12.0123 | 11.7824 | 11.5122 | 11.2274 | 10.8328 | 9.7146 | 4.5645 | 0.34625 | -2.0505 | -1.3878 | 17.319 | 17.1299 | 17.1299 | 16.8377 | 16.6493 | 16.4194 | 16.1492 | 15.8644 | 15.4698 | 14.3516 | 9.2015 | 4.9832 | 2.5865 | 3.2492 | 386475 | 422130 | ROSSENDALE | PADIHAM
| West Didsbury | 7.015 | 6.4718 | 6.0702 | 5.718 | 5.2614 | 4.7678 | 4.1868 | 3.6447 | 3.1192 | 2.4852 | 0.29636 | -0.68409 | -0.80833 | -0.54049 | 14.015 | 13.4718 | 13.0702 | 12.718 | 12.2614 | 11.7678 | 11.1868 | 10.6447 | 10.1192 | 9.4852 | 7.2964 | 6.3159 | 6.1917 | 6.4595 | 7.2285 | 6.887 | 6.4895 | 6.2006 | 5.8276 | 5.4111 | 4.9057 | 4.4355 | 3.9705 | 3.4607 | 1.7961 | 0.72098 | 0.16309 | -0.16654 | 14.2285 | 13.887 | 13.4895 | 13.2006 | 12.8276 | 12.4111 | 11.9057 | 11.4355 | 10.9705 | 10.4607 | 8.7961 | 7.721 | 7.1631 | 6.8335 | 7.0312 | 6.5081 | 6.1272 | 5.792 | 5.3565 | 4.8832 | 4.3223 | 3.7982 | 3.2989 | 2.7245 | 0.74672 | -0.10279 | -0.1886 | 0.048101 | 14.0312 | 13.5081 | 13.1272 | 12.792 | 12.3565 | 11.8832 | 11.3223 | 10.7982 | 10.2989 | 9.7245 | 7.7467 | 6.8972 | 6.8114 | 7.0481 | 7.0222 | 6.4795 | 6.0826 | 5.7301 | 5.2796 | 4.7801 | 4.171 | 3.602 | 3.125 | 2.6026 | 0.097704 | -3.922 | -6.6315 | -8.5876 | 14.0222 | 13.4795 | 13.0826 | 12.7301 | 12.2796 | 11.7801 | 11.171 | 10.602 | 10.125 | 9.6026 | 7.0977 | 3.078 | 0.36852 | -1.5876 | 6.9866 | 6.3768 | 5.9847 | 5.6782 | 5.2756 | 4.8504 | 4.3168 | 3.8414 | 3.4328 | 2.3377 | -2.7054 | -6.2237 | -7.9739 | -7.1801 | 13.9866 | 13.3768 | 13.3768 | 12.6782 | 12.2756 | 11.8504 | 11.3168 | 10.8414 | 10.4328 | 9.3377 | 4.2946 | 0.77634 | -0.97392 | -0.18007 | 383306 | 392514 | WEST DIDSBURY | SOUTH MANCHESTER
| Westgate | 6.8644 | 6.7863 | 6.4757 | 6.021 | 5.3779 | 4.9042 | 4.2472 | 3.3497 | 2.8495 | 2.0444 | -0.97312 | -3.0783 | -4.3188 | -3.7499 | 5.0014 | 4.9233 | 4.6127 | 4.158 | 3.5149 | 3.0412 | 2.3842 | 1.4867 | 0.98645 | 0.18135 | -2.8361 | -4.9413 | -6.1818 | -5.6129 | 6.9473 | 6.937 | 6.5348 | 6.1086 | 5.5218 | 5.0958 | 4.4856 | 3.6314 | 3.1631 | 2.4887 | 0.32323 | -1.4318 | -3.2762 | -2.9441 | 5.0843 | 5.074 | 4.6718 | 4.2456 | 3.6588 | 3.2328 | 2.6226 | 1.7684 | 1.3001 | 0.62573 | -1.5398 | -3.2948 | -5.1392 | -4.8071 | 6.8957 | 6.826 | 6.5585 | 6.128 | 5.5169 | 5.0707 | 4.4439 | 3.5817 | 3.1191 | 2.3976 | -0.36848 | -2.1226 | -3.0432 | -2.2031 | 5.0327 | 4.963 | 4.6955 | 4.265 | 3.6539 | 3.2077 | 2.5809 | 1.7187 | 1.2561 | 0.53456 | -2.2315 | -3.9856 | -4.9062 | -4.0661 | 6.8666 | 6.789 | 6.484 | 6.0361 | 5.4188 | 4.9561 | 4.2696 | 3.3465 | 2.9003 | 2.2561 | -1.7667 | -9.392 | -15.9772 | -18.4519 | 5.0036 | 4.926 | 4.621 | 4.1731 | 3.5558 | 3.0931 | 2.4066 | 1.4835 | 1.0373 | 0.39311 | -3.6297 | -11.255 | -17.8402 | -20.3149 | 6.8442 | 6.7368 | 6.4243 | 6.0083 | 5.3979 | 4.9747 | 4.3478 | 3.5007 | 2.9709 | 1.2055 | -7.1816 | -14.1087 | -18.9739 | -16.7574 | 4.9812 | 4.8738 | 4.8738 | 4.1453 | 3.5349 | 3.1117 | 2.4848 | 1.6377 | 1.1079 | -0.65752 | -9.0446 | -15.9717 | -20.8369 | -18.6204 | 343077 | 463204 | LANCASTER | HEYSHAM
| Westhoughton | 4.6459 | 3.9799 | 3.5879 | 2.9252 | 2.8329 | 1.9978 | 1.4452 | 0.74098 | 0.14502 | -0.76509 | -3.4827 | -4.9213 | -5.5547 | -5.4935 | 9.2829 | 8.6169 | 8.2249 | 7.5622 | 7.4699 | 6.6348 | 6.0822 | 5.378 | 4.782 | 3.8719 | 1.1543 | -0.28426 | -0.91771 | -0.85646 | 4.8468 | 4.3755 | 4.0016 | 3.3986 | 3.3964 | 2.6656 | 2.2122 | 1.615 | 1.1071 | 0.41004 | -1.3733 | -2.5976 | -3.6087 | -4.1623 | 9.4838 | 9.0125 | 8.6386 | 8.0356 | 8.0334 | 7.3026 | 6.8492 | 6.252 | 5.7441 | 5.047 | 3.2637 | 2.0394 | 1.0283 | 0.47468 | 4.6566 | 4.0071 | 3.6314 | 2.987 | 2.9246 | 2.1135 | 1.5799 | 0.89542 | 0.32802 | -0.50213 | -2.9181 | -3.9763 | -4.4203 | -4.1806 | 9.2936 | 8.6441 | 8.2684 | 7.624 | 7.5616 | 6.7505 | 6.2169 | 5.5324 | 4.965 | 4.1349 | 1.7189 | 0.6607 | 0.21665 | 0.45636 | 4.6499 | 3.9858 | 3.6064 | 2.9645 | 2.9288 | 2.137 | 1.5974 | 0.90981 | 0.42723 | -0.24846 | -3.8746 | -11.3994 | -17.4812 | -21.4426 | 9.2869 | 8.6228 | 8.2434 | 7.6015 | 7.5658 | 6.774 | 6.2344 | 5.5468 | 5.0642 | 4.3885 | 0.76236 | -6.7624 | -12.8442 | -16.8056 | 4.6667 | 3.9827 | 3.6224 | 3.0454 | 3.0311 | 2.3277 | 1.8788 | 1.3025 | 0.71666 | -1.2029 | -9.6739 | -16.3187 | -20.3596 | -19.1778 | 9.3037 | 8.6197 | 8.6197 | 7.6824 | 7.6681 | 6.9647 | 6.5158 | 5.9395 | 5.3537 | 3.4341 | -5.0369 | -11.6817 | -15.7226 | -14.5408 | 365831 | 407025 | WESTHOUGHTON | KEARSLEY
| Westlinton | 10.438 | 10.1131 | 9.9163 | 9.6867 | 9.7713 | 9.5561 | 9.3102 | 9.2287 | 8.9443 | 8.5788 | 7.0549 | 5.7756 | 4.8477 | 4.2086 | 12.938 | 12.6131 | 12.4163 | 12.1867 | 12.2713 | 12.0561 | 11.8102 | 11.7287 | 11.4443 | 11.0788 | 9.5549 | 8.2756 | 7.3477 | 6.7086 | 10.7004 | 10.5555 | 10.3335 | 10.103 | 10.1642 | 9.9829 | 9.7394 | 9.5854 | 9.3782 | 9.1477 | 8.3464 | 7.1289 | 5.9234 | 5.0261 | 13.2004 | 13.0555 | 12.8335 | 12.603 | 12.6642 | 12.4829 | 12.2394 | 12.0854 | 11.8782 | 11.6477 | 10.8464 | 9.6289 | 8.4234 | 7.5261 | 10.4419 | 10.1318 | 9.9461 | 9.7338 | 9.8223 | 9.6123 | 9.3744 | 9.2973 | 9.0293 | 8.7075 | 7.4294 | 6.5566 | 5.8717 | 5.6343 | 12.9419 | 12.6318 | 12.4461 | 12.2338 | 12.3223 | 12.1123 | 11.8744 | 11.7973 | 11.5293 | 11.2075 | 9.9294 | 9.0566 | 8.3717 | 8.1343 | 10.4493 | 10.1176 | 9.907 | 9.6616 | 9.7045 | 9.4381 | 9.0828 | 8.8685 | 8.544 | 8.2298 | 6.1618 | 3.8997 | 2.5175 | 2.0679 | 12.9493 | 12.6176 | 12.407 | 12.1616 | 12.2045 | 11.9381 | 11.5828 | 11.3685 | 11.044 | 10.7298 | 8.6618 | 6.3997 | 5.0175 | 4.5679 | 10.4337 | 10.061 | 9.864 | 9.608 | 9.5969 | 9.2592 | 8.8806 | 8.6649 | 8.2702 | 7.7606 | 5.0868 | 3.1064 | 2.2686 | 2.468 | 12.9337 | 12.561 | 12.561 | 12.108 | 12.0969 | 11.7592 | 11.3806 | 11.1649 | 10.7702 | 10.2606 | 7.5868 | 5.6064 | 4.7686 | 4.968 | 339551 | 564489 | CARLISLE | HARKER
| Whalley | 8.9285 | 8.324 | 7.883 | 7.4617 | 6.9867 | 6.4861 | 5.9343 | 5.3699 | 4.8149 | 4.1077 | 1.4321 | -0.052042 | -0.51029 | -0.32787 | 13.5655 | 12.961 | 12.52 | 12.0987 | 11.6237 | 11.1231 | 10.5713 | 10.0069 | 9.4519 | 8.7447 | 6.0691 | 4.585 | 4.1267 | 4.3091 | 9.1561 | 8.7678 | 8.318 | 7.9671 | 7.5675 | 7.1434 | 6.6638 | 6.168 | 5.6505 | 5.1337 | 3.4899 | 2.0827 | 1.1365 | 0.4764 | 13.7931 | 13.4048 | 12.955 | 12.6041 | 12.2045 | 11.7804 | 11.3008 | 10.805 | 10.2875 | 9.7707 | 8.1269 | 6.7197 | 5.7735 | 5.1134 | 8.9356 | 8.3475 | 7.9254 | 7.5279 | 7.0782 | 6.603 | 6.0769 | 5.5377 | 5.0118 | 4.3748 | 2.012 | 0.72939 | 0.30184 | 0.44839 | 13.5726 | 12.9845 | 12.5624 | 12.1649 | 11.7152 | 11.24 | 10.7139 | 10.1747 | 9.6488 | 9.0118 | 6.649 | 5.3664 | 4.9388 | 5.0854 | 8.9427 | 8.3218 | 7.8629 | 7.4307 | 6.9326 | 6.3836 | 5.7436 | 5.0821 | 4.5069 | 3.9256 | 1.319 | -2.3228 | -4.4487 | -6.1696 | 13.5797 | 12.9588 | 12.4999 | 12.0677 | 11.5696 | 11.0206 | 10.3806 | 9.7191 | 9.1439 | 8.5626 | 5.956 | 2.3142 | 0.18833 | -1.5326 | 8.928 | 8.2668 | 7.8227 | 7.4254 | 6.9619 | 6.481 | 5.9331 | 5.3917 | 4.9242 | 3.9769 | -0.45312 | -3.4219 | -4.7569 | -4.2977 | 13.565 | 12.9038 | 12.9038 | 12.0624 | 11.5989 | 11.118 | 10.5701 | 10.0287 | 9.5612 | 8.6139 | 4.1839 | 1.2151 | -0.11986 | 0.33934 | 373376 | 436176 | PADIHAM | PADIHAM
| Whalley Range | 2.1101 | 1.5833 | 1.1423 | 0.71991 | 0.17189 | -0.45357 | -1.2067 | -0.83755 | -1.4519 | -2.2241 | -5.0588 | -6.5027 | -6.8818 | -6.6897 | 11.2471 | 10.7203 | 10.2793 | 9.8569 | 9.3089 | 8.6834 | 7.9303 | 7.3024 | 6.6881 | 5.9159 | 3.0812 | 1.6373 | 1.2582 | 1.4503 | 2.4087 | 2.1336 | 1.5825 | 1.1623 | 0.65346 | 0.071953 | -0.65444 | -1.2715 | -1.8917 | -2.5898 | -4.6143 | -5.9512 | -6.6402 | -7.0095 | 11.5457 | 11.2706 | 10.7195 | 10.2993 | 9.7905 | 9.209 | 8.4826 | 7.8655 | 7.2453 | 6.5472 | 4.5227 | 3.1858 | 2.4968 | 2.1275 | 2.1214 | 1.6086 | 1.1835 | 0.7753 | 0.24435 | -0.36225 | -1.0955 | -1.7061 | -2.2932 | -2.9986 | -5.6343 | -6.9584 | -7.3073 | -7.1508 | 11.2584 | 10.7456 | 10.3205 | 9.9123 | 9.3814 | 8.7748 | 8.0415 | 7.4309 | 6.8438 | 6.1384 | 3.5027 | 2.1786 | 1.8297 | 1.9862 | 2.1404 | 1.6358 | 1.2182 | 0.80875 | 0.28462 | -0.33291 | -1.1107 | -1.7654 | -2.3292 | -2.9711 | -6.5024 | -12.3741 | -16.9677 | -19.9652 | 11.2774 | 10.7728 | 10.3552 | 9.9457 | 9.4216 | 8.8041 | 8.0263 | 7.3716 | 6.8078 | 6.1659 | 2.6346 | -3.2371 | -7.8307 | -10.8282 | 2.1259 | 1.5504 | 1.12 | 0.74742 | 0.26547 | -0.26979 | -0.95434 | -1.4911 | -2.0515 | -3.5631 | -10.9012 | -16.5953 | -19.498 | -18.1304 | 11.2629 | 10.6874 | 10.6874 | 9.8844 | 9.4025 | 8.8672 | 8.1827 | 7.6459 | 7.0855 | 5.5739 | -1.7642 | -7.4583 | -10.361 | -8.9934 | 382923 | 394645 | WEST DIDSBURY | SOUTH MANCHESTER
| Whasset | 2.7371 | 2.4631 | 2.2345 | 1.9604 | 1.8419 | 1.5008 | -1.5212 | -1.626 | -3.891 | -4.0997 | -5.3536 | -6.1328 | -6.0743 | -5.754 | 6.7371 | 6.4631 | 6.2345 | 5.9604 | 5.8419 | 5.5008 | 2.4788 | 2.374 | 0.10904 | -0.099736 | -1.3536 | -2.1328 | -2.0743 | -1.754 | 2.9413 | 2.833 | 2.5239 | 2.2404 | 2.1187 | 1.7893 | 1.4159 | 1.1459 | 0.87161 | 0.49182 | -0.3862 | -1.2585 | -1.9583 | -2.2789 | 6.9413 | 6.833 | 6.5239 | 6.2404 | 6.1187 | 5.7893 | 5.4159 | 5.1459 | 4.8716 | 4.4918 | 3.6138 | 2.7415 | 2.0417 | 1.7211 | 2.7435 | 2.4805 | 2.2661 | 2.0087 | 1.9042 | 1.5799 | -1.4249 | -1.5144 | -3.7609 | -3.9234 | -5.0048 | -5.6031 | -5.4599 | -5.0823 | 6.7435 | 6.4805 | 6.2661 | 6.0087 | 5.9042 | 5.5799 | 2.5751 | 2.4856 | 0.23907 | 0.076649 | -1.0048 | -1.6031 | -1.4599 | -1.0823 | 2.7559 | 2.4873 | 2.2672 | 2.0026 | 1.8761 | 1.5134 | -1.4075 | -1.5565 | -3.6684 | -3.768 | -6.743 | -8.7769 | -9.4774 | -10.2887 | 6.7559 | 6.4873 | 6.2672 | 6.0026 | 5.8761 | 5.5134 | 2.5925 | 2.4435 | 0.33156 | 0.23196 | -2.743 | -4.7769 | -5.4774 | -6.2887 | 2.7532 | 2.4727 | 2.2631 | 2.0182 | 1.8996 | -0.89386 | -3.6185 | -3.5546 | -3.4684 | -3.8104 | -6.5595 | -8.1279 | -8.5148 | -7.9629 | 6.7532 | 6.4727 | 6.4727 | 6.0182 | 5.8996 | 3.1061 | 0.38152 | 0.44542 | 0.53165 | 0.18962 | -2.5595 | -4.1279 | -4.5148 | -3.9629 | 350648 | 481468 | KENDAL (PARKSIDE RD) | HUTTON
| Whinfell | 0.87986 | 0.85872 | 0.86352 | 0.88453 | 0.85903 | 0.86912 | 0.85901 | 0.8742 | 0.85344 | 0.84968 | 0.88598 | 0.87584 | 0.88474 | 0.87352 | 0.87986 | 0.85872 | 0.86352 | 0.88453 | 0.85903 | 0.86912 | 0.85901 | 0.8742 | 0.85344 | 0.84968 | 0.88598 | 0.87584 | 0.88474 | 0.87352 | 0.87996 | 0.85904 | 0.86409 | 0.88532 | 0.86001 | 0.87047 | 0.86075 | 0.87631 | 0.85596 | 0.85234 | 0.88891 | 0.87891 | 0.88794 | 0.87683 | 0.87996 | 0.85904 | 0.86409 | 0.88532 | 0.86001 | 0.87047 | 0.86075 | 0.87631 | 0.85596 | 0.85234 | 0.88891 | 0.87891 | 0.88794 | 0.87683 | 0.87986 | 0.85872 | 0.86352 | 0.88453 | 0.85903 | 0.86912 | 0.85901 | 0.8742 | 0.85344 | 0.84968 | 0.88598 | 0.87584 | 0.88474 | 0.87352 | 0.87986 | 0.85872 | 0.86352 | 0.88453 | 0.85903 | 0.86912 | 0.85901 | 0.8742 | 0.85344 | 0.84968 | 0.88598 | 0.87584 | 0.88474 | 0.87352 | 0.87972 | 0.85831 | 0.86278 | 0.88345 | 0.8576 | 0.86701 | 0.8562 | 0.87071 | 0.84921 | 0.84496 | 0.88158 | 0.87177 | 0.881 | 0.87004 | 0.87972 | 0.85831 | 0.86278 | 0.88345 | 0.8576 | 0.86701 | 0.8562 | 0.87071 | 0.84921 | 0.84496 | 0.88158 | 0.87177 | 0.881 | 0.87004 | 0.87972 | 0.85831 | 0.86278 | 0.88345 | 0.8576 | 0.86701 | 0.8562 | 0.87071 | 0.84921 | 0.84496 | 0.88158 | 0.87177 | 0.881 | 0.87004 | 0.87972 | 0.85831 | 0.85831 | 0.88345 | 0.8576 | 0.86701 | 0.8562 | 0.87071 | 0.84921 | 0.84496 | 0.88158 | 0.87177 | 0.881 | 0.87004 | 357906 | 527506 | PENRITH & SHAP | HUTTON
| Whittle Le Woods | 6.4404 | 6.1411 | 5.8367 | 5.4604 | 5.1085 | 4.6065 | 4.1305 | 3.5894 | 3.0971 | 2.4814 | 0.28348 | -0.94289 | -1.2626 | -1.2523 | 9.9404 | 9.6411 | 9.3367 | 8.9604 | 8.6085 | 8.1065 | 7.6305 | 7.0894 | 6.5971 | 5.9814 | 3.7835 | 2.5571 | 2.2374 | 2.2477 | 6.5148 | 6.282 | 5.9372 | 5.584 | 5.2851 | 4.8338 | 4.4072 | 3.9166 | 3.4649 | 2.9524 | 1.3238 | 0.10799 | -0.59437 | -1.1433 | 10.0148 | 9.782 | 9.4372 | 9.084 | 8.7851 | 8.3338 | 7.9072 | 7.4166 | 6.9649 | 6.4524 | 4.8238 | 3.608 | 2.9056 | 2.3567 | 6.4474 | 6.1607 | 5.8692 | 5.5046 | 5.1795 | 4.6956 | 4.2367 | 3.7131 | 3.2445 | 2.6821 | 0.69867 | -0.37306 | -0.67929 | -0.70017 | 9.9474 | 9.6607 | 9.3692 | 9.0046 | 8.6795 | 8.1956 | 7.7367 | 7.2131 | 6.7445 | 6.1821 | 4.1987 | 3.1269 | 2.8207 | 2.7998 | 6.4487 | 6.155 | 5.8544 | 5.4696 | 5.1548 | 4.685 | 4.2296 | 3.7142 | 3.3057 | 2.8382 | 0.46255 | -3.6484 | -6.7141 | -9.0166 | 9.9487 | 9.655 | 9.3544 | 8.9696 | 8.6548 | 8.185 | 7.7296 | 7.2142 | 6.8057 | 6.3382 | 3.9625 | -0.14841 | -3.2141 | -5.5166 | 6.4412 | 6.1182 | 5.8222 | 5.4518 | 5.1674 | 4.7571 | 4.3635 | 3.9249 | 3.4993 | 2.4504 | -2.2807 | -5.9419 | -8.0125 | -7.7195 | 9.9412 | 9.6182 | 9.6182 | 8.9518 | 8.6674 | 8.2571 | 7.8635 | 7.4249 | 6.9993 | 5.9504 | 1.2193 | -2.4419 | -4.5125 | -4.2195 | 357874 | 421203 | LEYLAND | PENWORTHAM
| Whitworth | 4.1055 | 4.0446 | 3.8866 | 3.8886 | 3.7662 | 3.6343 | 3.4206 | 3.2199 | 3.0279 | 2.7832 | 1.9779 | 1.6273 | 1.586 | 1.7154 | 5.6055 | 5.5446 | 5.3866 | 5.3886 | 5.2662 | 5.1343 | 4.9206 | 4.7199 | 4.5279 | 4.2832 | 3.4779 | 3.1273 | 3.086 | 3.2154 | 4.189 | 4.1944 | 4.0197 | 4.0172 | 3.9027 | 3.8384 | 3.6689 | 3.5114 | 3.358 | 3.1866 | 2.6737 | 2.329 | 2.1495 | 2.0527 | 5.689 | 5.6944 | 5.5197 | 5.5172 | 5.4027 | 5.3384 | 5.1689 | 5.0114 | 4.858 | 4.6866 | 4.1737 | 3.829 | 3.6495 | 3.5527 | 4.1075 | 4.0501 | 3.8973 | 3.9034 | 3.7869 | 3.6491 | 3.4397 | 3.2427 | 3.057 | 2.8321 | 2.0954 | 1.7825 | 1.7486 | 1.8646 | 5.6075 | 5.5501 | 5.3973 | 5.4034 | 5.2869 | 5.1491 | 4.9397 | 4.7427 | 4.557 | 4.3321 | 3.5954 | 3.2825 | 3.2486 | 3.3646 | 4.1119 | 4.0536 | 3.8969 | 3.8998 | 3.7762 | 3.701 | 3.5047 | 3.326 | 3.1781 | 3.0132 | 2.2135 | 1.1459 | 0.5179 | 0.12829 | 5.6119 | 5.5536 | 5.3969 | 5.3998 | 5.2762 | 5.201 | 5.0047 | 4.826 | 4.6781 | 4.5132 | 3.7135 | 2.6459 | 2.0179 | 1.6283 | 4.1102 | 4.043 | 3.8826 | 3.8869 | 3.7634 | 3.6643 | 3.4888 | 3.3421 | 3.2041 | 2.9026 | 1.5985 | 0.7686 | 0.45391 | 0.72574 | 5.6102 | 5.543 | 5.543 | 5.3869 | 5.2634 | 5.1643 | 4.9888 | 4.8421 | 4.7041 | 4.4026 | 3.0985 | 2.2686 | 1.9539 | 2.2257 | 388779 | 419157 | ROCHDALE CENTRAL | ROCHDALE
| Wigton | -1.2467 | -2.0176 | -1.9017 | -2.2711 | -2.59 | -3.1089 | -3.6279 | -3.8778 | -4.4736 | -7.4522 | -9.7922 | -12.3004 | -13.1171 | -12.5614 | 2.8903 | 2.1194 | 2.2353 | 1.8659 | 1.547 | 1.0281 | 0.50906 | 0.25918 | -0.33664 | -3.3152 | -5.6552 | -8.1634 | -8.9801 | -8.4244 | -0.88249 | -1.341 | -1.3803 | -1.7516 | -2.0726 | -2.576 | -3.097 | -3.368 | -3.9675 | -4.6317 | -5.8546 | -7.6365 | -9.1674 | -9.9643 | 3.2545 | 2.796 | 2.7567 | 2.3854 | 2.0644 | 1.561 | 1.04 | 0.76895 | 0.1695 | -0.49466 | -1.7176 | -3.4995 | -5.0304 | -5.8273 | -1.2389 | -1.9791 | -1.8345 | -2.1732 | -2.4668 | -2.9602 | -3.4546 | -3.6851 | -4.2399 | -7.1235 | -9.1184 | -11.3322 | -11.9313 | -11.3368 | 2.8981 | 2.1579 | 2.3025 | 1.9638 | 1.6702 | 1.1768 | 0.68242 | 0.45193 | -0.10293 | -2.9865 | -4.9814 | -7.1952 | -7.7943 | -7.1998 | -1.219 | -2.0036 | -1.9039 | -2.2882 | -2.6715 | -3.2913 | -3.9752 | -4.3839 | -5.0438 | -7.7512 | -9.7997 | -13.5334 | -14.9796 | -15.7418 | 2.918 | 2.1334 | 2.2331 | 1.8488 | 1.4655 | 0.84575 | 0.16177 | -0.24694 | -0.90683 | -3.6142 | -5.6627 | -9.3964 | -10.8426 | -11.6048 | -1.1948 | -1.9838 | -1.8781 | -2.25 | -2.6674 | -3.2796 | -3.8933 | -6.3734 | -6.8535 | -8.8313 | -12.16 | -14.3761 | -15.2091 | -14.3594 | 2.9422 | 2.1532 | 2.1532 | 1.887 | 1.4696 | 0.85737 | 0.24374 | -2.2364 | -2.7165 | -4.6943 | -8.023 | -10.2391 | -11.0721 | -10.2224 | 325814 | 549933 | CARLISLE | HARKER
| Willow Hey | 11.9267 | 11.6367 | 11.5444 | 11.4032 | 11.2033 | 10.9791 | 10.7295 | 10.3818 | 10.0348 | 9.628 | 8.1405 | 7.2428 | 6.8751 | 6.5252 | 16.5637 | 16.2737 | 16.1814 | 16.0402 | 15.8403 | 15.6161 | 15.3665 | 15.0188 | 14.6718 | 14.265 | 12.7775 | 11.8798 | 11.5121 | 11.1622 | 12.1661 | 12.0679 | 11.8972 | 11.6939 | 11.4562 | 11.2108 | 10.8786 | 10.5255 | 10.1501 | 9.7522 | 8.932 | 8.1596 | 7.6232 | 7.2641 | 16.8031 | 16.7049 | 16.5342 | 16.3309 | 16.0932 | 15.8478 | 15.5156 | 15.1625 | 14.7871 | 14.3892 | 13.569 | 12.7966 | 12.2602 | 11.9011 | 11.9349 | 11.653 | 11.5692 | 11.4367 | 11.2471 | 11.0338 | 10.7684 | 10.4414 | 10.1133 | 9.747 | 8.4399 | 7.7929 | 7.4085 | 7.251 | 16.5719 | 16.29 | 16.2062 | 16.0737 | 15.8841 | 15.6708 | 15.4054 | 15.0784 | 14.7503 | 14.384 | 13.0769 | 12.4299 | 12.0455 | 11.888 | 11.9407 | 11.6662 | 11.5889 | 11.4568 | 11.2426 | 10.9606 | 10.6318 | 10.2841 | 9.9447 | 9.6 | 7.5159 | 3.7951 | 1.0482 | -0.87278 | 16.5777 | 16.3032 | 16.2259 | 16.0938 | 15.8796 | 15.5976 | 15.2688 | 14.9211 | 14.5817 | 14.237 | 12.1529 | 8.4321 | 5.6852 | 3.7642 | 11.9381 | 11.642 | 11.5601 | 11.4281 | 11.2044 | 10.9321 | 10.5946 | 10.2452 | 9.8717 | 9.0884 | 5.0474 | 1.6477 | -0.32738 | 0.019196 | 16.5751 | 16.279 | 16.279 | 16.0651 | 15.8414 | 15.5691 | 15.2316 | 14.8822 | 14.5087 | 13.7254 | 9.6844 | 6.2847 | 4.3096 | 4.6562 | 347779 | 406066 | SKELMERSDALE | WASHWAY FARM
| Willowbank | 3.0218 | 2.5684 | 2.4796 | 2.2984 | 2.1013 | 1.8722 | 1.6243 | 1.3541 | 1.0471 | 0.70205 | -0.8738 | -2.1999 | -3.043 | -3.655 | 6.5218 | 6.0684 | 5.9796 | 5.7984 | 5.6013 | 5.3722 | 5.1243 | 4.8541 | 4.5471 | 4.2021 | 2.6262 | 1.3001 | 0.45704 | -0.155 | 3.3678 | 3.2106 | 3.0042 | 2.7307 | 2.5088 | 2.261 | 1.9782 | 1.6649 | 1.2965 | 0.9462 | -0.13171 | -1.0951 | -1.8265 | -2.3332 | 6.8678 | 6.7106 | 6.5042 | 6.2307 | 6.0088 | 5.761 | 5.4782 | 5.1649 | 4.7965 | 4.4462 | 3.3683 | 2.4049 | 1.6735 | 1.1668 | 3.0143 | 2.5704 | 2.4885 | 2.2854 | 2.1305 | 1.8883 | 1.645 | 1.3662 | 1.0681 | 0.75792 | -0.62392 | -1.6119 | -2.2848 | -2.6595 | 6.5143 | 6.0704 | 5.9885 | 5.7854 | 5.6305 | 5.3883 | 5.145 | 4.8662 | 4.5681 | 4.2579 | 2.8761 | 1.8881 | 1.2152 | 0.84053 | 3.0389 | 2.6004 | 2.5232 | 2.3463 | 2.157 | 1.9141 | 1.6115 | 1.2533 | 0.86912 | 0.47774 | -2.076 | -6.5927 | -10.2673 | -12.7711 | 6.5389 | 6.1004 | 6.0232 | 5.8463 | 5.657 | 5.4141 | 5.1115 | 4.7533 | 4.3691 | 3.9777 | 1.424 | -3.0927 | -6.7673 | -9.2711 | 3.0531 | 2.6079 | 2.5308 | 2.343 | 2.1755 | 1.9053 | 1.5977 | 1.2327 | 0.75045 | -0.29201 | -5.2482 | -9.5698 | -12.1898 | -11.7882 | 6.5531 | 6.1079 | 6.1079 | 5.843 | 5.6755 | 5.4053 | 5.0977 | 4.7327 | 4.2504 | 3.208 | -1.7482 | -6.0698 | -8.6898 | -8.2882 | 391885 | 406064 | GREENHILL | WHITEGATE
| Willowholme | 11.8753 | 11.4441 | 11.2078 | 10.9243 | 10.7899 | 10.3966 | 9.9664 | 9.5745 | 9.1914 | 8.6817 | 6.9986 | 6.1651 | 5.996 | 6.2445 | 16.0123 | 15.5811 | 15.3448 | 15.0613 | 14.9269 | 14.5336 | 14.1034 | 13.7115 | 13.3284 | 12.8187 | 11.1356 | 10.3021 | 10.133 | 10.3815 | 12.2484 | 12.1325 | 11.8573 | 11.5488 | 11.4183 | 11.0606 | 10.6652 | 10.3051 | 9.9518 | 9.5325 | 8.2922 | 7.4471 | 7.0026 | 6.8584 | 16.3854 | 16.2695 | 15.9943 | 15.6858 | 15.5553 | 15.1976 | 14.8022 | 14.4421 | 14.0888 | 13.6695 | 12.4292 | 11.5841 | 11.1396 | 10.9954 | 11.8793 | 11.4582 | 11.2326 | 10.9575 | 10.8327 | 10.4522 | 10.0349 | 9.6556 | 9.2922 | 8.8285 | 7.3169 | 6.6615 | 6.59 | 6.893 | 16.0163 | 15.5952 | 15.3696 | 15.0945 | 14.9697 | 14.5892 | 14.1719 | 13.7926 | 13.4292 | 12.9655 | 11.4539 | 10.7985 | 10.727 | 11.03 | 11.8957 | 11.4896 | 11.2824 | 11.0253 | 10.9397 | 10.604 | 10.2231 | 9.8884 | 9.606 | 9.2572 | 7.2693 | 3.6142 | 0.80354 | -0.93787 | 16.0327 | 15.6266 | 15.4194 | 15.1623 | 15.0767 | 14.741 | 14.3601 | 14.0254 | 13.743 | 13.3942 | 11.4063 | 7.7512 | 4.9405 | 3.1991 | 11.8895 | 11.4489 | 11.2287 | 10.9794 | 10.8999 | 10.5893 | 10.2382 | 9.9446 | 9.5952 | 8.6407 | 4.4101 | 1.1672 | -0.63686 | 0.045817 | 16.0265 | 15.5859 | 15.5859 | 15.1164 | 15.0369 | 14.7263 | 14.3752 | 14.0816 | 13.7322 | 12.7777 | 8.5471 | 5.3042 | 3.5001 | 4.1828 | 338653 | 556688 | CARLISLE | HARKER
| Wilmslow | 4.673 | 4.2547 | 4.202 | 4.0471 | 3.8081 | 3.471 | 3.1073 | 2.8504 | 2.6012 | 2.2709 | 1.1798 | 0.5535 | 0.34686 | 0.32231 | 8.173 | 7.7547 | 7.702 | 7.5471 | 7.3081 | 6.971 | 6.6073 | 6.3504 | 6.1012 | 5.7709 | 4.6798 | 4.0535 | 3.8469 | 3.8223 | 4.822 | 4.5641 | 4.3829 | 4.1905 | 3.9112 | 3.5538 | 3.1434 | 2.8175 | 2.5102 | 2.1369 | 1.2116 | 0.50762 | 0.093965 | -0.20389 | 8.322 | 8.0641 | 7.8829 | 7.6905 | 7.4112 | 7.0538 | 6.6434 | 6.3175 | 6.0102 | 5.6369 | 4.7116 | 4.0076 | 3.594 | 3.2961 | 4.6823 | 4.2906 | 4.2537 | 4.1177 | 3.8981 | 3.5816 | 3.239 | 2.9977 | 2.7747 | 2.482 | 1.4989 | 0.94656 | 0.75804 | 0.73933 | 8.1823 | 7.7906 | 7.7537 | 7.6177 | 7.3981 | 7.0816 | 6.739 | 6.4977 | 6.2747 | 5.982 | 4.9989 | 4.4466 | 4.258 | 4.2393 | 4.6904 | 4.2907 | 4.2682 | 4.1122 | 3.8935 | 3.5736 | 3.2213 | 2.9784 | 2.7603 | 2.4985 | 1.1016 | -1.7783 | -3.9768 | -5.508 | 8.1904 | 7.7907 | 7.7682 | 7.6122 | 7.3935 | 7.0736 | 6.7213 | 6.4784 | 6.2603 | 5.9985 | 4.6016 | 1.7217 | -0.47683 | -2.008 | 4.6768 | 4.2743 | 4.279 | 4.1752 | 4.0076 | 3.748 | 3.4539 | 3.2738 | 3.0338 | 2.3009 | -0.99828 | -3.6222 | -5.0804 | -4.6416 | 8.1768 | 7.7743 | 7.7743 | 7.6752 | 7.5076 | 7.248 | 6.9539 | 6.7738 | 6.5338 | 5.8009 | 2.5017 | -0.12216 | -1.5804 | -1.1416 | 384710 | 381286 | MOSS NOOK | SOUTH MANCHESTER
| Windermere | 9.4644 | 9.1251 | 8.818 | 8.398 | 8.0936 | 7.6134 | 7.0667 | 6.574 | 6.0738 | 5.3929 | 3.0466 | 1.8811 | 1.6195 | 1.9977 | 13.4644 | 13.1251 | 12.818 | 12.398 | 12.0936 | 11.6134 | 11.0667 | 10.574 | 10.0738 | 9.3929 | 7.0466 | 5.8811 | 5.6195 | 5.9977 | 9.5474 | 9.298 | 8.9266 | 8.5488 | 8.2873 | 7.8467 | 7.3379 | 6.87 | 6.3553 | 5.2471 | 4.425 | 3.4125 | 2.7743 | 2.3939 | 13.5474 | 13.298 | 12.9266 | 12.5488 | 12.2873 | 11.8467 | 11.3379 | 10.87 | 10.3553 | 9.2471 | 8.425 | 7.4125 | 6.7743 | 6.3939 | 9.4683 | 9.1455 | 8.8579 | 8.4627 | 8.1815 | 7.7287 | 7.2101 | 6.744 | 6.2753 | 5.6641 | 3.5288 | 2.5002 | 2.2888 | 2.638 | 13.4683 | 13.1455 | 12.8579 | 12.4627 | 12.1815 | 11.7287 | 11.2101 | 10.744 | 10.2753 | 9.6641 | 7.5288 | 6.5002 | 6.2888 | 6.638 | 9.468 | 9.1144 | 8.7999 | 8.3831 | 8.064 | 7.5572 | 6.9581 | 6.4083 | 5.9189 | 5.3945 | 2.9515 | -1.2859 | -4.175 | -6.4042 | 13.468 | 13.1144 | 12.7999 | 12.3831 | 12.064 | 11.5572 | 10.9581 | 10.4083 | 9.9189 | 9.3945 | 6.9515 | 2.7141 | -0.17496 | -2.4042 | 9.4109 | 9.0115 | 8.7236 | 8.3452 | 8.0613 | 7.6222 | 7.1124 | 6.6844 | 6.2892 | 5.2031 | 0.24705 | -3.3193 | -5.2401 | -4.6335 | 13.4109 | 13.0115 | 13.0115 | 12.3452 | 12.0613 | 11.6222 | 11.1124 | 10.6844 | 10.2892 | 9.2031 | 4.247 | 0.68074 | -1.2401 | -0.63353 | 341657 | 498418 | KENDAL (PARKSIDE RD) | HUTTON
| Winifred Rd | 5.3237 | 4.6619 | 4.7858 | 4.2969 | 4.3406 | 3.9901 | 3.56 | 3.1558 | 2.749 | 2.1997 | 0.53546 | -0.20428 | -0.32351 | -0.020546 | 8.8237 | 8.1619 | 8.2858 | 7.7969 | 7.8406 | 7.4901 | 7.06 | 6.6558 | 6.249 | 5.6997 | 4.0355 | 3.2957 | 3.1765 | 3.4795 | 5.5248 | 5.0355 | 5.0754 | 4.5535 | 4.5809 | 4.2257 | 3.8157 | 3.4097 | 2.9434 | 2.5521 | 1.3779 | 0.61393 | 0.19136 | 0.058054 | 9.0248 | 8.5355 | 8.5754 | 8.0535 | 8.0809 | 7.7257 | 7.3157 | 6.9097 | 6.4434 | 6.0521 | 4.8779 | 4.1139 | 3.6914 | 3.5581 | 5.3331 | 4.6848 | 4.8141 | 4.3394 | 4.3904 | 4.0542 | 3.6294 | 3.2399 | 2.855 | 2.3571 | 0.84438 | 0.20961 | 0.12923 | 0.42441 | 8.8331 | 8.1848 | 8.3141 | 7.8394 | 7.8904 | 7.5542 | 7.1294 | 6.7399 | 6.355 | 5.8571 | 4.3444 | 3.7096 | 3.6292 | 3.9244 | 5.3382 | 4.6957 | 4.8463 | 4.3902 | 4.4737 | 4.1748 | 3.7696 | 3.4172 | 3.1185 | 2.7293 | 0.49734 | -4.3573 | -8.3017 | -10.6593 | 8.8382 | 8.1957 | 8.3463 | 7.8902 | 7.9737 | 7.6748 | 7.2696 | 6.9172 | 6.6185 | 6.2293 | 3.9973 | -0.85731 | -4.8017 | -7.1593 | 5.3486 | 4.6878 | 4.8529 | 4.4491 | 4.5915 | 4.3693 | 3.9851 | 3.7131 | 3.3553 | 2.1114 | -3.4314 | -7.7839 | -10.3859 | -9.2496 | 8.8486 | 8.1878 | 8.1878 | 7.9491 | 8.0915 | 7.8693 | 7.4851 | 7.2131 | 6.8553 | 5.6114 | 0.068592 | -4.2839 | -6.8859 | -5.7496 | 389971 | 388470 | ADSWOOD | BREDBURY
| Withington | 2.5461 | 2.1652 | 1.8645 | 1.5241 | 1.0625 | 0.55877 | -0.0077325 | -0.55001 | -1.038 | -1.6508 | -3.8393 | -4.9842 | -5.3421 | -5.3002 | 6.0461 | 5.6652 | 5.3645 | 5.0241 | 4.5625 | 4.0588 | 3.4923 | 2.95 | 2.462 | 1.8492 | -0.33932 | -1.4842 | -1.8421 | -1.8002 | 2.6961 | 2.4417 | 2.0593 | 1.7252 | 1.2922 | 0.81247 | 0.25565 | -0.29332 | -0.80496 | -1.3801 | -3.0536 | -4.2172 | -4.8513 | -5.2563 | 6.1961 | 5.9417 | 5.5593 | 5.2252 | 4.7922 | 4.3125 | 3.7557 | 3.2067 | 2.695 | 2.1199 | 0.44639 | -0.71716 | -1.3513 | -1.7563 | 2.5808 | 2.2237 | 1.905 | 1.5836 | 1.145 | 0.65858 | 0.099879 | -0.40382 | -0.87737 | -1.4358 | -3.4752 | -4.5688 | -4.9038 | -4.8867 | 6.0808 | 5.7237 | 5.405 | 5.0836 | 4.645 | 4.1586 | 3.5999 | 3.0962 | 2.6226 | 2.0642 | 0.024824 | -1.0688 | -1.4038 | -1.3867 | 2.5595 | 2.182 | 1.8813 | 1.5285 | 1.0634 | 0.53815 | -0.083296 | -0.68971 | -1.1709 | -1.7147 | -4.6303 | -9.9995 | -13.9151 | -16.6935 | 6.0595 | 5.682 | 5.3813 | 5.0285 | 4.5634 | 4.0382 | 3.4167 | 2.8103 | 2.3291 | 1.7853 | -1.1303 | -6.4995 | -10.4151 | -13.1935 | 2.5594 | 2.1442 | 1.8484 | 1.5401 | 1.1243 | 0.67812 | 0.14074 | -0.36002 | -0.82403 | -2.1876 | -8.6423 | -13.4613 | -16.0428 | -15.1592 | 6.0594 | 5.6442 | 5.6442 | 5.0401 | 4.6243 | 4.1781 | 3.6407 | 3.14 | 2.676 | 1.3124 | -5.1423 | -9.9613 | -12.5428 | -11.6592 | 384841 | 392774 | WEST DIDSBURY | SOUTH MANCHESTER
| Withyfold Drive | 16.354 | 15.8743 | 15.3588 | 14.9907 | 14.3771 | 13.773 | 13.0363 | 12.3411 | 11.5184 | 10.8838 | 8.0867 | 6.0507 | 5.7761 | 5.7926 | 23.354 | 22.8743 | 22.3588 | 21.9907 | 21.3771 | 20.773 | 20.0363 | 19.3411 | 18.5184 | 17.8838 | 15.0867 | 13.0507 | 12.7761 | 12.7926 | 16.4964 | 16.1652 | 15.6444 | 15.2998 | 14.7478 | 14.1669 | 13.5219 | 12.8481 | 12.081 | 11.3014 | 9.516 | 7.7553 | 7.0643 | 6.4071 | 23.4964 | 23.1652 | 22.6444 | 22.2998 | 21.7478 | 21.1669 | 20.5219 | 19.8481 | 19.081 | 18.3014 | 16.516 | 14.7553 | 14.0643 | 13.4071 | 16.3583 | 15.9012 | 15.413 | 15.0617 | 14.4748 | 13.898 | 13.1897 | 12.5214 | 11.7395 | 11.1823 | 8.6726 | 6.8999 | 6.7256 | 6.8173 | 23.3583 | 22.9012 | 22.413 | 22.0617 | 21.4748 | 20.898 | 20.1897 | 19.5214 | 18.7395 | 18.1823 | 15.6726 | 13.8999 | 13.7256 | 13.8173 | 16.369 | 15.9233 | 15.4481 | 15.1097 | 14.5625 | 14.0261 | 13.3428 | 12.7097 | 12.0214 | 11.6011 | 7.2828 | 1.1837 | -2.4215 | -5.4355 | 23.369 | 22.9233 | 22.4481 | 22.1097 | 21.5625 | 21.0261 | 20.3428 | 19.7097 | 19.0214 | 18.6011 | 14.2828 | 8.1837 | 4.5785 | 1.5645 | 16.29 | 15.7415 | 15.2806 | 15.0044 | 14.5151 | 14.0686 | 13.4747 | 12.9524 | 12.0591 | 10.9618 | 3.9213 | -1.991 | -4.0078 | -3.4993 | 23.29 | 22.7415 | 22.7415 | 22.0044 | 21.5151 | 21.0686 | 20.4747 | 19.9524 | 19.0591 | 17.9618 | 10.9213 | 5.009 | 2.9922 | 3.5007 | 392132 | 374352 | MACCLESFIELD | MACCLESFIELD
| Woodbine St | 6.0775 | 5.7218 | 5.5053 | 5.3936 | 5.1958 | 4.7607 | 4.3379 | 4.1684 | 3.7842 | 3.3037 | 2.0693 | 1.2363 | 0.89567 | 0.68982 | 9.5775 | 9.2218 | 9.0053 | 8.8936 | 8.6958 | 8.2607 | 7.8379 | 7.6684 | 7.2842 | 6.8037 | 5.5693 | 4.7363 | 4.3957 | 4.1898 | 6.2381 | 6.0442 | 5.7539 | 5.6144 | 5.4142 | 4.9964 | 4.584 | 4.3982 | 4.0287 | 3.5773 | 2.6494 | 1.8591 | 1.346 | 0.92862 | 9.7381 | 9.5442 | 9.2539 | 9.1144 | 8.9142 | 8.4964 | 8.084 | 7.8982 | 7.5287 | 7.0773 | 6.1494 | 5.3591 | 4.846 | 4.4286 | 6.0773 | 5.7484 | 5.5447 | 5.4422 | 5.2568 | 4.8376 | 4.4302 | 4.2363 | 3.9062 | 3.4624 | 2.3267 | 1.6682 | 1.3785 | 1.2677 | 9.5773 | 9.2484 | 9.0447 | 8.9422 | 8.7568 | 8.3376 | 7.9302 | 7.7363 | 7.4062 | 6.9624 | 5.8267 | 5.1682 | 4.8785 | 4.7677 | 6.0845 | 5.7363 | 5.5251 | 5.415 | 5.2285 | 4.7996 | 4.371 | 4.1789 | 3.8277 | 3.4048 | 1.6292 | -2.0601 | -4.9553 | -7.0546 | 9.5845 | 9.2363 | 9.0251 | 8.915 | 8.7285 | 8.2996 | 7.871 | 7.6789 | 7.3277 | 6.9048 | 5.1292 | 1.4399 | -1.4553 | -3.5546 | 6.1022 | 5.744 | 5.5354 | 5.4494 | 5.2936 | 4.9068 | 4.5138 | 4.3746 | 3.9615 | 2.9368 | -1.1729 | -4.5331 | -6.4688 | -6.1097 | 9.6022 | 9.244 | 9.244 | 8.9494 | 8.7936 | 8.4068 | 8.0138 | 7.8746 | 7.4615 | 6.4368 | 2.3271 | -1.0331 | -2.9688 | -2.6097 | 390519 | 412388 | CASTLETON | ROCHDALE
| Woodfield Rd | 5.9409 | 4.9675 | 4.3972 | 4.0333 | 3.7175 | 3.252 | 2.6288 | 2.0021 | 1.3678 | 0.63297 | -2.1022 | -3.9355 | -4.7918 | -5.2598 | 10.5779 | 9.6045 | 9.0342 | 8.6703 | 8.3545 | 7.889 | 7.2658 | 6.6391 | 6.0048 | 5.27 | 2.5348 | 0.70151 | -0.15476 | -0.62281 | 6.4608 | 5.9741 | 5.4266 | 4.9969 | 4.5434 | 4.0074 | 3.3834 | 2.7505 | 2.0987 | 1.4152 | -0.74187 | -2.4779 | -3.6254 | -4.5411 | 11.0978 | 10.6111 | 10.0636 | 9.6339 | 9.1804 | 8.6444 | 8.0204 | 7.3875 | 6.7357 | 6.0522 | 3.8951 | 2.1591 | 1.0116 | 0.095925 | 5.96 | 5.0108 | 4.4652 | 4.1221 | 3.8345 | 3.4289 | 2.8427 | 2.253 | 1.6651 | 1.0089 | -1.4059 | -2.9094 | -3.6091 | -3.9185 | 10.597 | 9.6478 | 9.1022 | 8.7591 | 8.4715 | 8.0659 | 7.4797 | 6.89 | 6.3021 | 5.6459 | 3.2311 | 1.7276 | 1.0279 | 0.71852 | 5.9587 | 5.0005 | 4.4348 | 4.0533 | 3.7423 | 3.3572 | 2.784 | 2.1895 | 1.6474 | 1.0804 | -2.4904 | -8.8027 | -13.6794 | -16.9961 | 10.5957 | 9.6375 | 9.0718 | 8.6903 | 8.3793 | 7.9942 | 7.421 | 6.8265 | 6.2844 | 5.7174 | 2.1466 | -4.1657 | -9.0424 | -12.3591 | 5.9716 | 5.0075 | 4.4539 | 4.0994 | 3.8185 | 3.4735 | 3.0027 | 2.4988 | 1.8627 | 0.32961 | -6.6926 | -12.4515 | -15.7429 | -15.2823 | 10.6086 | 9.6445 | 9.6445 | 8.7364 | 8.4555 | 8.1105 | 7.6397 | 7.1358 | 6.4997 | 4.9666 | -2.0556 | -7.8145 | -11.1059 | -10.6453 | 358258 | 418014 | WRIGHTINGTON | PENWORTHAM
| Woodhill Lane | 0.18272 | 0.093213 | 0.032403 | -0.089681 | -0.30516 | -0.46017 | -0.6487 | 2.0781 | 1.9548 | 1.7269 | 0.97557 | 0.50887 | 0.33393 | 0.51453 | 1.1827 | 1.0932 | 1.0324 | 0.91032 | 0.69484 | 0.53983 | 0.3513 | 0.078074 | -0.045167 | -0.27312 | -1.0244 | -1.4911 | -1.6661 | -1.4855 | 0.2967 | 0.29298 | 0.13898 | -0.033786 | -0.29513 | -0.49198 | -0.73687 | 1.92 | 1.7169 | 1.4203 | 0.85407 | 0.38766 | 0.10054 | 0.16058 | 1.2967 | 1.293 | 1.139 | 0.96621 | 0.70487 | 0.50802 | 0.26313 | -0.080006 | -0.28309 | -0.57967 | -1.1459 | -1.6123 | -1.8995 | -1.8394 | 0.19408 | 0.11777 | 0.072598 | -0.034794 | -0.23354 | -0.37463 | -0.54857 | 2.1955 | 2.0879 | 1.8866 | 1.1898 | 0.76645 | 0.60935 | 0.79569 | 1.1941 | 1.1178 | 1.0726 | 0.96521 | 0.76646 | 0.62537 | 0.45143 | 0.19548 | 0.08787 | -0.11337 | -0.81017 | -1.2336 | -1.3907 | -1.2043 | 0.18862 | 0.097647 | 0.033344 | -0.097423 | -0.3304 | -0.51272 | -0.74396 | 1.9349 | 1.7844 | 1.5528 | 0.40399 | -1.9893 | -3.7897 | -4.7417 | 1.1886 | 1.0976 | 1.0333 | 0.90258 | 0.6696 | 0.48728 | 0.25604 | -0.065094 | -0.2156 | -0.44721 | -1.596 | -3.9893 | -5.7897 | -6.7417 | 0.21467 | 0.14032 | 0.093522 | -0.011396 | -0.22041 | -0.36984 | -0.56089 | 2.1653 | 2.0264 | 1.4045 | -1.405 | -3.6004 | -4.8268 | -4.135 | 1.2147 | 1.1403 | 1.1403 | 0.9886 | 0.77959 | 0.63016 | 0.43911 | 0.16532 | 0.026358 | -0.59551 | -3.405 | -5.6004 | -6.8268 | -6.135 | 343294 | 463785 | LANCASTER | HEYSHAM
| Woodhouse Park | 5.5304 | 5.056 | 4.9558 | 4.8221 | 4.6064 | 4.3011 | 3.9709 | 3.7175 | 3.4852 | 3.1596 | 1.9074 | 1.1324 | 0.82534 | 0.71699 | 9.0304 | 8.556 | 8.4558 | 8.3221 | 8.1064 | 7.8011 | 7.4709 | 7.2175 | 6.9852 | 6.6596 | 5.4074 | 4.6324 | 4.3253 | 4.217 | 5.7587 | 5.4924 | 5.3465 | 5.1971 | 4.9804 | 4.6886 | 4.3648 | 4.1133 | 3.8752 | 3.5845 | 2.6134 | 1.8961 | 1.5052 | 1.2068 | 9.2587 | 8.9924 | 8.8465 | 8.6971 | 8.4804 | 8.1886 | 7.8648 | 7.6133 | 7.3752 | 7.0845 | 6.1134 | 5.3961 | 5.0052 | 4.7068 | 5.5574 | 5.0987 | 5.012 | 4.8903 | 4.6907 | 4.4017 | 4.088 | 3.8494 | 3.6347 | 3.3385 | 2.1944 | 1.4951 | 1.2168 | 1.1175 | 9.0574 | 8.5987 | 8.512 | 8.3903 | 8.1907 | 7.9017 | 7.588 | 7.3494 | 7.1347 | 6.8385 | 5.6944 | 4.9951 | 4.7168 | 4.6175 | 5.5305 | 5.0481 | 4.9245 | 4.75 | 4.4963 | 4.1317 | 3.7102 | 3.3441 | 3.0457 | 2.683 | 0.89037 | -2.8014 | -5.7133 | -8.1004 | 9.0305 | 8.5481 | 8.4245 | 8.25 | 7.9963 | 7.6317 | 7.2102 | 6.8441 | 6.5457 | 6.183 | 4.3904 | 0.69861 | -2.2133 | -4.6004 | 5.5665 | 5.1077 | 5.0029 | 4.8603 | 4.6506 | 4.3387 | 3.9657 | 3.652 | 3.3658 | 2.4436 | -1.8148 | -5.1893 | -7.2612 | -7.0544 | 9.0665 | 8.6077 | 8.6077 | 8.3603 | 8.1506 | 7.8387 | 7.4657 | 7.152 | 6.8658 | 5.9436 | 1.6852 | -1.6893 | -3.7612 | -3.5544 | 382132 | 386340 | MOSS NOOK | SOUTH MANCHESTER
| Woodley | 9.5271 | 9.0254 | 8.8945 | 8.8324 | 8.5551 | 8.3324 | 8.065 | 7.8809 | 7.5845 | 7.3101 | 6.1224 | 4.6402 | 3.7157 | 2.6447 | 14.1641 | 13.6624 | 13.5315 | 13.4694 | 13.1921 | 12.9694 | 12.702 | 12.5179 | 12.2215 | 11.9471 | 10.7594 | 9.2772 | 8.3527 | 7.2817 | 9.8328 | 9.5927 | 9.4023 | 9.2753 | 8.9647 | 8.7252 | 8.4337 | 8.215 | 7.8736 | 7.4427 | 6.7206 | 5.8043 | 5.0308 | 4.3031 | 14.4698 | 14.2297 | 14.0393 | 13.9123 | 13.6017 | 13.3622 | 13.0707 | 12.852 | 12.5106 | 12.0797 | 11.3576 | 10.4413 | 9.6678 | 8.9401 | 9.5333 | 9.039 | 8.9144 | 8.8577 | 8.5889 | 8.3744 | 8.1159 | 7.9394 | 7.6559 | 7.4056 | 6.3963 | 5.4148 | 4.7267 | 4.1109 | 14.1703 | 13.676 | 13.5514 | 13.4947 | 13.2259 | 13.0114 | 12.7529 | 12.5764 | 12.2929 | 12.0426 | 11.0333 | 10.0518 | 9.3637 | 8.7479 | 9.5401 | 9.0525 | 8.9351 | 8.8831 | 8.6132 | 8.3781 | 8.0766 | 7.8401 | 7.4835 | 7.0703 | 4.6806 | -0.24797 | -4.0535 | -6.55 | 14.1771 | 13.6895 | 13.5721 | 13.5201 | 13.2502 | 13.0151 | 12.7136 | 12.4771 | 12.1205 | 11.7073 | 9.3176 | 4.389 | 0.58352 | -1.913 | 9.5385 | 9.0297 | 8.9024 | 8.8564 | 8.5933 | 8.2484 | 7.9198 | 7.6458 | 7.2264 | 6.5867 | 1.5028 | -3.0464 | -5.8746 | -5.6466 | 14.1755 | 13.6667 | 13.6667 | 13.4934 | 13.2303 | 12.8854 | 12.5568 | 12.2828 | 11.8634 | 11.2237 | 6.1398 | 1.5906 | -1.2376 | -1.0096 | 393116 | 392019 | VERNON PARK | BREDBURY
| Woolfold | 10.5191 | 9.9999 | 9.727 | 9.252 | 8.8848 | 8.3212 | 7.7248 | 7.145 | 6.5477 | 5.9397 | 3.6902 | 2.7248 | 2.5961 | 3.0369 | 14.5191 | 13.9999 | 13.727 | 13.252 | 12.8848 | 12.3212 | 11.7248 | 11.145 | 10.5477 | 9.9397 | 7.6902 | 6.7248 | 6.5961 | 7.0369 | 10.786 | 10.4912 | 10.153 | 9.7134 | 9.4262 | 8.9634 | 8.4642 | 7.9763 | 7.4631 | 6.991 | 5.4434 | 4.539 | 4.0566 | 4.0129 | 14.786 | 14.4912 | 14.153 | 13.7134 | 13.4262 | 12.9634 | 12.4642 | 11.9763 | 11.4631 | 10.991 | 9.4434 | 8.539 | 8.0566 | 8.0129 | 10.5267 | 10.0216 | 9.7616 | 9.2989 | 8.9475 | 8.4021 | 7.8229 | 7.2587 | 6.6873 | 6.1018 | 4.0205 | 3.1742 | 3.0739 | 3.4796 | 14.5267 | 14.0216 | 13.7616 | 13.2989 | 12.9475 | 12.4021 | 11.8229 | 11.2587 | 10.6873 | 10.1018 | 8.0205 | 7.1742 | 7.0739 | 7.4796 | 10.5462 | 10.0631 | 9.8432 | 9.4353 | 9.1652 | 8.7214 | 8.2559 | 7.8253 | 7.4419 | 7.0694 | 4.2021 | -0.76533 | -4.6528 | -6.946 | 14.5462 | 14.0631 | 13.8432 | 13.4353 | 13.1652 | 12.7214 | 12.2559 | 11.8253 | 11.4419 | 11.0694 | 8.2021 | 3.2347 | -0.65282 | -2.946 | 10.4628 | 9.8619 | 9.6171 | 9.2292 | 8.9924 | 8.6102 | 8.2005 | 7.8491 | 7.3519 | 6.0707 | 0.081163 | -4.4194 | -6.9969 | -5.6713 | 14.4628 | 13.8619 | 13.8619 | 13.2292 | 12.9924 | 12.6102 | 12.2005 | 11.8491 | 11.3519 | 10.0707 | 4.0812 | -0.41935 | -2.9969 | -1.6713 | 378874 | 411666 | BURY | KEARSLEY
| Wordsworth St | 8.828 | 8.5415 | 8.4098 | 8.1868 | 7.7743 | 7.1945 | 6.9388 | 6.5845 | 6.092 | 5.408 | 3.5615 | 2.7573 | 2.6224 | 2.9453 | 13.465 | 13.1785 | 13.0468 | 12.8238 | 12.4113 | 11.8315 | 11.5758 | 11.2215 | 10.729 | 10.045 | 8.1985 | 7.3943 | 7.2594 | 7.5823 | 9.051 | 8.8643 | 8.5956 | 8.3193 | 7.8901 | 7.3059 | 7.0324 | 6.6905 | 6.1493 | 5.6621 | 4.7012 | 3.8927 | 3.4037 | 3.2049 | 13.688 | 13.5013 | 13.2326 | 12.9563 | 12.5271 | 11.9429 | 11.6694 | 11.3275 | 10.7863 | 10.2991 | 9.3382 | 8.5297 | 8.0407 | 7.8419 | 8.8371 | 8.5607 | 8.4711 | 8.2596 | 7.8629 | 7.303 | 7.0037 | 6.6184 | 6.1471 | 5.519 | 3.8502 | 3.1512 | 3.0149 | 3.3024 | 13.4741 | 13.1977 | 13.1081 | 12.8966 | 12.4999 | 11.94 | 11.6407 | 11.2554 | 10.7841 | 10.156 | 8.4872 | 7.7882 | 7.6519 | 7.9394 | 8.8484 | 8.5837 | 8.4953 | 8.3196 | 7.9751 | 7.4831 | 7.1491 | 6.7899 | 6.4097 | 5.9145 | 3.2078 | -3.1652 | -8.333 | -11.7205 | 13.4854 | 13.2207 | 13.1323 | 12.9566 | 12.6121 | 12.1201 | 11.7861 | 11.4269 | 11.0467 | 10.5515 | 7.8448 | 1.4718 | -3.696 | -7.0835 | 8.8667 | 8.5949 | 8.4868 | 8.3471 | 8.0473 | 7.6261 | 7.3413 | 7.0687 | 6.5602 | 4.8816 | -2.2912 | -7.9519 | -11.3798 | -10.1233 | 13.5037 | 13.2319 | 13.2319 | 12.9841 | 12.6843 | 12.2631 | 11.9783 | 11.7057 | 11.1972 | 9.5186 | 2.3458 | -3.3149 | -6.7428 | -5.4863 | 370709 | 410873 | BOLTON | KEARSLEY
| Worsley Mesnes | 12.9496 | 12.7126 | 12.5303 | 11.4953 | 10.3886 | 8.0104 | 5.6056 | 4.0015 | 2.3939 | 1.1272 | -0.45327 | -1.2396 | -1.4234 | -1.2905 | 17.5866 | 17.3496 | 17.1673 | 16.1323 | 15.0256 | 12.6474 | 10.2426 | 8.6385 | 7.0309 | 5.7642 | 4.1837 | 3.3974 | 3.2136 | 3.3465 | 13.0467 | 12.8898 | 12.6811 | 12.279 | 11.8292 | 11.0313 | 10.209 | 9.5763 | 8.9378 | 8.3932 | 7.2833 | 6.5193 | 6.0927 | 5.8337 | 17.6837 | 17.5268 | 17.3181 | 16.916 | 16.4662 | 15.6683 | 14.846 | 14.2133 | 13.5748 | 13.0302 | 11.9203 | 11.1563 | 10.7297 | 10.4707 | 12.9567 | 12.726 | 12.5448 | 11.5156 | 10.4174 | 8.0472 | 5.6502 | 4.0542 | 2.4611 | 1.2333 | -0.20007 | -0.87844 | -1.0265 | -0.89323 | 17.5937 | 17.363 | 17.1818 | 16.1526 | 15.0544 | 12.6842 | 10.2872 | 8.6912 | 7.0981 | 5.8703 | 4.4369 | 3.7586 | 3.6105 | 3.7438 | 12.9556 | 12.7256 | 12.556 | 11.532 | 10.4564 | 8.1112 | 5.7285 | 4.1501 | 2.6206 | 1.4889 | -0.58982 | -4.936 | -8.4221 | -10.8418 | 17.5926 | 17.3626 | 17.193 | 16.169 | 15.0934 | 12.7482 | 10.3655 | 8.7871 | 7.2576 | 6.1259 | 4.0472 | -0.29896 | -3.7851 | -6.2048 | 12.971 | 12.7268 | 12.5468 | 11.5454 | 10.4898 | 8.1847 | 5.8464 | 4.324 | 2.7092 | 0.84945 | -4.0148 | -7.9105 | -10.2039 | -9.6551 | 17.608 | 17.3638 | 17.3638 | 16.1824 | 15.1268 | 12.8217 | 10.4834 | 8.961 | 7.3462 | 5.4865 | 0.62215 | -3.2735 | -5.5669 | -5.0181 | 357435 | 403977 | WIGAN | KIRKBY
| Wrightington | 10.9978 | 10.588 | 10.1344 | 9.5416 | 9.0345 | 8.3427 | 7.6493 | 6.8719 | 6.1765 | 5.2034 | 1.8031 | 0.084106 | -0.19903 | 0.20347 | 15.6348 | 15.225 | 14.7714 | 14.1786 | 13.6715 | 12.9797 | 12.2863 | 11.5089 | 10.8135 | 9.8404 | 6.4401 | 4.7211 | 4.438 | 4.8405 | 11.1025 | 10.7961 | 10.3355 | 9.8777 | 9.5163 | 8.9722 | 8.431 | 7.8099 | 7.2331 | 6.5835 | 4.5633 | 2.9191 | 1.8711 | 1.1217 | 15.7395 | 15.4331 | 14.9725 | 14.5147 | 14.1533 | 13.6092 | 13.068 | 12.4469 | 11.8701 | 11.2205 | 9.2003 | 7.5561 | 6.5081 | 5.7587 | 11.0033 | 10.6093 | 10.175 | 9.6214 | 9.1421 | 8.4814 | 7.8179 | 7.0709 | 6.41 | 5.5301 | 2.4163 | 0.89806 | 0.67913 | 1.1247 | 15.6403 | 15.2463 | 14.812 | 14.2584 | 13.7791 | 13.1184 | 12.4549 | 11.7079 | 11.047 | 10.1671 | 7.0533 | 5.5351 | 5.3161 | 5.7617 | 11.0079 | 10.5784 | 10.1074 | 9.5228 | 9.0252 | 8.323 | 7.5862 | 6.7667 | 6.1221 | 5.3995 | 2.4853 | -1.2284 | -3.2263 | -4.8841 | 15.6449 | 15.2154 | 14.7444 | 14.1598 | 13.6622 | 12.96 | 12.2232 | 11.4037 | 10.7591 | 10.0365 | 7.1223 | 3.4086 | 1.4107 | -0.24713 | 10.9843 | 10.4844 | 9.9951 | 9.4089 | 8.9297 | 8.2962 | 7.6632 | 6.9923 | 6.4784 | 5.4202 | 0.8121 | -2.0601 | -3.2253 | -2.6876 | 15.6213 | 15.1214 | 15.1214 | 14.0459 | 13.5667 | 12.9332 | 12.3002 | 11.6293 | 11.1154 | 10.0572 | 5.4491 | 2.5769 | 1.4117 | 1.9494 | 353466 | 413290 | WRIGHTINGTON | PENWORTHAM
| Yealand | 0.5747 | 0.47084 | 0.44264 | 0.29819 | 0.12957 | -0.023816 | -0.22828 | -0.32951 | -0.51699 | -0.63884 | -1.2785 | -1.5674 | -1.6489 | -1.4839 | 8.5747 | 8.4708 | 8.4426 | 8.2982 | 8.1296 | 7.9762 | 7.7717 | 7.6705 | 7.483 | 7.3612 | 6.7215 | 6.4326 | 6.3511 | 6.5161 | 0.66176 | 0.59386 | 0.53748 | 0.4154 | 0.27695 | 0.15469 | -0.014478 | -0.087249 | -0.24529 | -0.3226 | -0.68197 | -0.99333 | -1.2352 | -1.3187 | 8.6618 | 8.5939 | 8.5375 | 8.4154 | 8.2769 | 8.1547 | 7.9855 | 7.9128 | 7.7547 | 7.6774 | 7.318 | 7.0067 | 6.7648 | 6.6813 | 0.57601 | 0.47269 | 0.45371 | 0.33314 | 0.15452 | 0.020506 | -0.17926 | -0.29696 | -0.47936 | -0.58811 | -1.1349 | -1.3751 | -1.4343 | -1.2693 | 8.576 | 8.4727 | 8.4537 | 8.3331 | 8.1545 | 8.0205 | 7.8207 | 7.703 | 7.5206 | 7.4119 | 6.8651 | 6.6249 | 6.5657 | 6.7307 | 0.5793 | 0.4764 | 0.43647 | 0.30602 | 0.1929 | -0.01086 | -0.21586 | -0.24466 | -0.46059 | -0.53695 | -1.2385 | -2.1014 | -2.6184 | -2.9811 | 8.5793 | 8.4764 | 8.4365 | 8.306 | 8.1929 | 7.9891 | 7.7841 | 7.7553 | 7.5394 | 7.4631 | 6.7615 | 5.8986 | 5.3816 | 5.0189 | 0.57571 | 0.4564 | 0.40256 | 0.26554 | 0.14563 | -0.038367 | -0.22641 | -0.22926 | -0.41821 | -0.61915 | -1.6857 | -2.3775 | -2.6789 | -2.5357 | 8.5757 | 8.4564 | 8.4564 | 8.2655 | 8.1456 | 7.9616 | 7.7736 | 7.7707 | 7.5818 | 7.3809 | 6.3143 | 5.6225 | 5.3211 | 5.4643 | 351537 | 475934 | KENDAL (PARKSIDE RD) | HUTTON

## BSP Headroom
Click the scenario name to move directly to the associated results | Best View
Steady Progression
System Transformation
Consumer Transformation
Leading the Way
| BSP | Best View Firm Headroom MVA | [13 empty] | Best View Non Firm Headroom MVA | [13 empty] | Steady Progression Firm Headroom MVA | [13 empty] | Steady Progression Non Firm Headroom MVA | [13 empty] | System Transformation Firm Headroom MVA | [13 empty] | System Transformation Non Firm Headroom MVA | [13 empty] | Consumer Transformation Firm Headroom MVA | [13 empty] | Consumer Transformation Non Firm Headroom MVA | [13 empty] | Leading the Way Firm Headroom MVA | [13 empty] | Leading the Way Non Firm Headroom MVA
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2036 | 2041 | 2046 | 2051 | Easting | Northing | GSP
| Adswood | 54.6641 | 45.5345 | 44.8965 | 44.0559 | 42.8721 | 41.5098 | 39.8999 | 38.3439 | 36.7654 | 34.9981 | 28.6677 | 25.4915 | 24.8542 | 25.5513 | 72.6641 | 63.5345 | 62.8965 | 62.0559 | 60.8721 | 59.5098 | 57.8999 | 56.3439 | 54.7654 | 52.9981 | 46.6677 | 43.4915 | 42.8542 | 43.5513 | 59.4247 | 54.8911 | 53.9733 | 53.0448 | 51.9491 | 50.686 | 49.1692 | 47.6804 | 46.1227 | 44.5389 | 39.8896 | 36.7517 | 35.0036 | 33.9783 | 77.4247 | 72.8911 | 71.9733 | 71.0448 | 69.9491 | 68.686 | 67.1692 | 65.6804 | 64.1227 | 62.5389 | 57.8896 | 54.7517 | 53.0036 | 51.9783 | 54.7176 | 45.6662 | 45.084 | 44.2124 | 43.0836 | 41.7851 | 40.2399 | 38.7464 | 37.2585 | 35.6802 | 29.8935 | 27.3114 | 26.9819 | 27.8367 | 72.7176 | 63.6662 | 63.084 | 62.2124 | 61.0836 | 59.7851 | 58.2399 | 56.7464 | 55.2585 | 53.6802 | 47.8935 | 45.3114 | 44.9819 | 45.8367 | 54.7183 | 45.6608 | 45.129 | 44.4041 | 43.4121 | 42.2554 | 40.8369 | 39.4934 | 38.3155 | 37.1311 | 28.8948 | 11.4004 | -2.0657 | -10.7857 | 72.7183 | 63.6608 | 63.129 | 62.4041 | 61.4121 | 60.2554 | 58.8369 | 57.4934 | 56.3155 | 55.1311 | 46.8948 | 29.4004 | 15.9343 | 7.2143 | 54.7368 | 45.5852 | 45.0855 | 44.4816 | 43.6516 | 42.7417 | 41.5453 | 40.4652 | 39.0215 | 34.8503 | 15.2455 | -0.37915 | -9.0785 | -5.9478 | 72.7368 | 63.5852 | 63.0855 | 62.4816 | 61.6516 | 60.7417 | 59.5453 | 58.4652 | 57.0215 | 52.8503 | 33.2455 | 17.6208 | 8.9215 | 12.0522 | 389188 | 388310 | BREDBURY
| Agecroft | 18.7305 | 17.9301 | 17.1479 | 15.9861 | 14.3636 | 12.6759 | 10.7172 | 23.7664 | 21.7005 | 19.4524 | 10.9827 | 5.9709 | 3.9431 | 3.4897 | 30.7305 | 29.9301 | 29.1479 | 27.9861 | 26.3636 | 24.6759 | 22.7172 | 20.7664 | 18.7005 | 16.4524 | 7.9827 | 2.9709 | 0.94311 | 0.48973 | 18.876 | 18.2027 | 17.2264 | 16.049 | 14.5641 | 12.9752 | 11.2073 | 24.369 | 22.4417 | 20.3492 | 14.0165 | 9.0801 | 5.817 | 3.4925 | 30.876 | 30.2027 | 29.2264 | 28.049 | 26.5641 | 24.9752 | 23.2073 | 21.369 | 19.4417 | 17.3492 | 11.0165 | 6.0801 | 2.817 | 0.49254 | 18.7603 | 17.9805 | 17.343 | 16.1653 | 14.6767 | 13.0326 | 11.1954 | 24.3296 | 22.3804 | 20.3609 | 12.7805 | 8.626 | 6.9783 | 6.6127 | 30.7603 | 29.9805 | 29.343 | 28.1653 | 26.6767 | 25.0326 | 23.1954 | 21.3296 | 19.3804 | 17.3609 | 9.7805 | 5.626 | 3.9783 | 3.6127 | 18.7691 | 18.0193 | 17.3028 | 16.1631 | 14.6609 | 13.0622 | 11.215 | 24.3003 | 22.5092 | 20.7861 | 10.1435 | -9.0705 | -23.5064 | -33.3428 | 30.7691 | 30.0193 | 29.3028 | 28.1631 | 26.6609 | 25.0622 | 23.215 | 21.3003 | 19.5092 | 17.7861 | 7.1435 | -12.0705 | -26.5064 | -36.3428 | 18.8631 | 18.0133 | 17.3088 | 16.3079 | 14.9194 | 13.4272 | 11.734 | 25.1007 | 23.2329 | 18.668 | -3.3256 | -20.6959 | -30.3098 | -27.9981 | 30.8631 | 30.0133 | 29.3088 | 28.3079 | 26.9194 | 25.4272 | 23.734 | 22.1007 | 20.2329 | 15.668 | -6.3256 | -23.6959 | -33.3098 | -30.9981 | 380345 | 401831 | KEARSLEY
| Altrincham | 60.0792 | 58.7094 | 57.5046 | 56.1038 | 54.4189 | 52.5458 | 50.5648 | 48.5226 | 46.4656 | 44.1865 | 36.6853 | 33.2332 | 32.7605 | 33.7863 | 78.0792 | 76.7094 | 75.5046 | 74.1038 | 72.4189 | 70.5458 | 68.5648 | 66.5226 | 64.4656 | 62.1865 | 54.6853 | 51.2332 | 50.7605 | 51.7863 | 60.5794 | 59.6176 | 58.23 | 56.9587 | 55.4751 | 53.7981 | 51.9807 | 50.0801 | 47.9129 | 45.662 | 40.36 | 36.6466 | 34.4929 | 33.3102 | 78.5794 | 77.6176 | 76.23 | 74.9587 | 73.4751 | 71.7981 | 69.9807 | 68.0801 | 65.9129 | 63.662 | 58.36 | 54.6466 | 52.4929 | 51.3102 | 60.1246 | 58.8133 | 57.6451 | 56.3021 | 54.6923 | 52.8966 | 50.9894 | 49.0175 | 47.0661 | 45.0202 | 38.2912 | 35.4026 | 35.106 | 36.1908 | 78.1246 | 76.8133 | 75.6451 | 74.3021 | 72.6923 | 70.8966 | 68.9894 | 67.0175 | 65.0661 | 63.0202 | 56.2912 | 53.4026 | 53.106 | 54.1908 | 60.1418 | 58.8613 | 57.8264 | 56.6 | 55.1637 | 53.5708 | 51.8594 | 50.1332 | 48.6249 | 47.137 | 37.9514 | 19.7008 | 5.7421 | -3.5425 | 78.1418 | 76.8613 | 75.8264 | 74.6 | 73.1637 | 71.5708 | 69.8594 | 68.1332 | 66.6249 | 65.137 | 55.9514 | 37.7008 | 23.7421 | 14.4575 | 59.9221 | 58.2628 | 57.2538 | 56.286 | 55.1022 | 53.8426 | 52.434 | 51.0714 | 49.4081 | 44.9162 | 23.9371 | 7.4771 | -1.6447 | 1.8828 | 77.9221 | 76.2628 | 75.2538 | 74.286 | 73.1022 | 71.8426 | 70.434 | 69.0714 | 67.4081 | 62.9162 | 41.9371 | 25.4771 | 16.3553 | 19.8828 | 376380 | 389012 | CARRINGTON
| Atherton | 28.0128 | 26.4247 | 19.0664 | 10.7937 | 7.5488 | 3.1956 | -1.4612 | -5.7157 | -10.1292 | -14.8219 | -29.2364 | -37.0284 | -38.4988 | -37.3221 | 46.0128 | 44.4247 | 37.0664 | 28.7937 | 25.5488 | 21.1956 | 16.5388 | 12.2843 | 7.8708 | 3.1781 | -11.2364 | -19.0284 | -20.4988 | -19.3221 | 28.4753 | 27.2705 | 25.2593 | 23.1971 | 20.7717 | 17.875 | 14.6963 | 11.514 | 8.2237 | 4.6817 | -5.1365 | -12.0932 | -16.0887 | -18.5047 | 46.4753 | 45.2705 | 43.2593 | 41.1971 | 38.7717 | 35.875 | 32.6963 | 29.514 | 26.2237 | 22.6817 | 12.8635 | 5.9068 | 1.9113 | -0.50468 | 28.0905 | 26.6011 | 19.3448 | 11.1587 | 8.0333 | 3.8039 | -0.73056 | -4.9907 | -9.2984 | -13.6023 | -26.5184 | -32.9761 | -33.9446 | -32.4104 | 46.0905 | 44.6011 | 37.3448 | 29.1587 | 26.0333 | 21.8039 | 17.2694 | 13.0093 | 8.7016 | 4.3977 | -8.5184 | -14.9761 | -15.9446 | -14.4104 | 28.0379 | 26.4815 | 19.2098 | 11.064 | 8.1046 | 4.0585 | -0.36938 | -4.3546 | -7.9587 | -11.2995 | -28.7535 | -63.733 | -89.9279 | -107.2869 | 46.0379 | 44.4815 | 37.2098 | 29.064 | 26.1046 | 22.0585 | 17.6306 | 13.6454 | 10.0413 | 6.7005 | -10.7535 | -45.733 | -71.9279 | -89.2869 | 28.1264 | 26.3827 | 19.0692 | 11.1287 | 8.379 | 4.7167 | 0.69235 | -2.7842 | -6.8692 | -15.7698 | -55.2714 | -85.8401 | -102.768 | -97.5335 | 46.1264 | 44.3827 | 37.0692 | 29.1287 | 26.379 | 22.7167 | 18.6924 | 15.2158 | 11.1308 | 2.2302 | -37.2714 | -67.8401 | -84.768 | -79.5335 | 366150 | 402088 | KEARSLEY
| Barrow & Sandgate | 55.5475 | 50.358 | 46.1075 | 42.9383 | 42.0379 | 41.1959 | 40.2255 | 39.1703 | 38.2172 | 37.2512 | 34.3118 | 22.6699 | 24.7525 | 27.1472 | 93.5475 | 88.358 | 84.1075 | 80.9383 | 80.0379 | 79.1959 | 78.2255 | 77.1703 | 76.2172 | 75.2512 | 72.3118 | 60.6699 | 62.7525 | 65.1472 | 57.9951 | 55.6738 | 52.8146 | 50.4828 | 49.3862 | 48.1587 | 46.714 | 45.1181 | 42.8509 | 40.3838 | 38.5047 | 37.5519 | 37.4136 | 38.04 | 95.9951 | 93.6738 | 90.8146 | 88.4828 | 87.3862 | 86.1587 | 84.714 | 83.1181 | 80.8509 | 78.3838 | 76.5047 | 75.5519 | 75.4136 | 76.04 | 55.6584 | 50.5582 | 46.3988 | 43.3148 | 42.4962 | 41.743 | 40.867 | 39.9093 | 39.0706 | 38.2667 | 34.7752 | 23.2846 | 25.6315 | 28.2612 | 93.6584 | 88.5582 | 84.3988 | 81.3148 | 80.4962 | 79.743 | 78.867 | 77.9093 | 77.0706 | 76.2667 | 72.7752 | 61.2846 | 63.6315 | 66.2612 | 55.6322 | 50.5309 | 46.3733 | 43.3054 | 42.5197 | 41.6819 | 40.824 | 39.9822 | 39.1695 | 38.3846 | 13.8885 | 1.7412 | -8.3632 | -14.3113 | 93.6322 | 88.5309 | 84.3733 | 81.3054 | 80.5197 | 79.6819 | 78.824 | 77.9822 | 77.1695 | 76.3846 | 51.8885 | 39.7412 | 29.6368 | 23.6887 | 55.7246 | 50.6368 | 46.5543 | 43.6434 | 42.4687 | 41.984 | 32.859 | 32.7889 | 32.536 | 31.942 | 5.8158 | -6.7134 | -12.383 | -6.387 | 93.7246 | 88.6368 | 84.5543 | 81.6434 | 80.4687 | 79.984 | 70.859 | 70.7889 | 70.536 | 69.942 | 43.8158 | 31.2866 | 25.617 | 31.613 | 319709 | 470489 | HARKER
| Barton | 68.8561 | 65.6783 | 64.3893 | 63.0898 | 61.3878 | 59.4347 | 57.3914 | 55.3373 | 53.2793 | 50.8785 | 27.1034 | 5.1761 | 2.7663 | 2.5387 | 98.8561 | 95.6783 | 94.3893 | 93.0898 | 91.3878 | 89.4347 | 87.3914 | 85.3373 | 83.2793 | 80.8785 | 57.1034 | 35.1761 | 32.7663 | 32.5387 | 70.8351 | 69.4313 | 67.7293 | 66.1511 | 64.3472 | 62.3984 | 60.299 | 58.1543 | 55.9177 | 53.5905 | 46.105 | 39.9053 | 35.5362 | 32.5004 | 100.8351 | 99.4313 | 97.7293 | 96.1511 | 94.3472 | 92.3984 | 90.299 | 88.1543 | 85.9177 | 83.5905 | 76.105 | 69.9053 | 65.5362 | 62.5004 | 68.8911 | 65.7785 | 64.5616 | 63.3227 | 61.7025 | 59.8329 | 57.8722 | 55.8998 | 53.9534 | 51.849 | 29.1114 | 8.668 | 6.9482 | 7.7036 | 98.8911 | 95.7785 | 94.5616 | 93.3227 | 91.7025 | 89.8329 | 87.8722 | 85.8998 | 83.9534 | 81.849 | 59.1114 | 38.668 | 36.9482 | 37.7036 | 68.9591 | 65.9051 | 64.755 | 63.5747 | 62.0669 | 60.2913 | 58.1835 | 56.0462 | 54.0243 | 52.0208 | 9.964 | -14.6628 | -33.1874 | -43.9747 | 98.9591 | 95.9051 | 94.755 | 93.5747 | 92.0669 | 90.2913 | 88.1835 | 86.0462 | 84.0243 | 82.0208 | 39.964 | 15.3372 | -3.1874 | -13.9747 | 68.894 | 65.7362 | 64.6185 | 63.5451 | 62.1212 | 56.6334 | 47.4373 | 45.8535 | 43.0903 | 33.431 | 7.5881 | -15.4424 | -27.6588 | -25.2695 | 98.894 | 95.7362 | 94.6185 | 93.5451 | 92.1212 | 86.6334 | 77.4373 | 75.8535 | 73.0903 | 63.431 | 37.5881 | 14.5576 | 2.3412 | 4.7305 | 376758 | 397174 | CARRINGTON
| Belfield | 56.0059 | 54.6442 | 54.1141 | 53.4266 | 52.4569 | 51.3192 | 50.1361 | 48.9331 | 47.7481 | 46.5058 | 42.6654 | 40.0417 | 38.9506 | 38.7964 | 74.0059 | 72.6442 | 72.1141 | 71.4266 | 70.4569 | 69.3192 | 68.1361 | 66.9331 | 65.7481 | 64.5058 | 60.6654 | 58.0417 | 56.9506 | 56.7964 | 57.0403 | 56.5324 | 55.5903 | 54.6191 | 53.4966 | 52.2901 | 50.9946 | 49.6416 | 48.2415 | 46.818 | 43.4706 | 41.2152 | 39.9422 | 38.9581 | 75.0403 | 74.5324 | 73.5903 | 72.6191 | 71.4966 | 70.2901 | 68.9946 | 67.6416 | 66.2415 | 64.818 | 61.4706 | 59.2152 | 57.9422 | 56.9581 | 56.0354 | 54.7045 | 54.2062 | 53.5502 | 52.6186 | 51.5237 | 50.3841 | 49.2247 | 48.1001 | 46.9745 | 43.4515 | 41.3883 | 40.4983 | 40.5561 | 74.0354 | 72.7045 | 72.2062 | 71.5502 | 70.6186 | 69.5237 | 68.3841 | 67.2247 | 66.1001 | 64.9745 | 61.4515 | 59.3883 | 58.4983 | 58.5561 | 56.1088 | 54.8806 | 54.5225 | 54.0402 | 53.3324 | 52.5217 | 51.7046 | 50.915 | 50.2228 | 49.4814 | 42.8916 | 29.421 | 19.1209 | 12.5171 | 74.1088 | 72.8806 | 72.5225 | 72.0402 | 71.3324 | 70.5217 | 69.7046 | 68.915 | 68.2228 | 67.4814 | 60.8916 | 47.421 | 37.1209 | 30.5171 | 56.1273 | 54.8248 | 54.4598 | 54.07 | 53.4736 | 52.8185 | 52.133 | 51.5056 | 50.9046 | 47.6847 | 32.5002 | 20.3684 | 13.6619 | 15.862 | 74.1273 | 72.8248 | 72.4598 | 72.07 | 71.4736 | 70.8185 | 70.133 | 69.5056 | 68.9046 | 65.6847 | 50.5002 | 38.3684 | 31.6619 | 33.862 | 391033 | 413945 | ROCHDALE
| Bispham | 43.4398 | 41.9469 | 40.6736 | 39.1255 | 37.1588 | 34.9625 | 32.5761 | 30.1144 | 27.6003 | 24.6394 | 10.117 | 3.1721 | 2.5651 | 4.1483 | 61.4398 | 59.9469 | 58.6736 | 57.1255 | 55.1588 | 52.9625 | 50.5761 | 48.1144 | 45.6003 | 42.6394 | 28.117 | 21.1721 | 20.5651 | 22.1483 | 44.0918 | 43.1336 | 41.6561 | 40.2269 | 38.5134 | 36.539 | 34.3471 | 32.0585 | 29.6825 | 27.2666 | 20.3214 | 15.3274 | 12.5196 | 11.0329 | 62.0918 | 61.1336 | 59.6561 | 58.2269 | 56.5134 | 54.539 | 52.3471 | 50.0585 | 47.6825 | 45.2666 | 38.3214 | 33.3274 | 30.5196 | 29.0329 | 43.5042 | 42.0866 | 40.9247 | 39.4605 | 37.5991 | 35.5082 | 33.2237 | 30.8604 | 28.4089 | 25.689 | 12.2867 | 6.2637 | 6.0081 | 7.7775 | 61.5042 | 60.0866 | 58.9247 | 57.4605 | 55.5991 | 53.5082 | 51.2237 | 48.8604 | 46.4089 | 43.689 | 30.2867 | 24.2637 | 24.0081 | 25.7775 | 43.5087 | 42.0904 | 40.9619 | 39.5614 | 37.8409 | 35.8812 | 33.6341 | 31.358 | 27.4623 | 25.477 | 6.489 | -19.9 | -40.0574 | -53.506 | 61.5087 | 60.0904 | 58.9619 | 57.5614 | 55.8409 | 53.8812 | 51.6341 | 49.358 | 45.4623 | 43.477 | 24.489 | -1.9 | -22.0574 | -35.506 | 43.5516 | 41.9 | 40.7081 | 39.4379 | 37.7984 | 36.0685 | 33.853 | 31.9649 | 29.5764 | 22.1482 | -12.9732 | -36.5858 | -49.7585 | -45.1617 | 61.5516 | 59.9 | 58.7081 | 57.4379 | 55.7984 | 54.0685 | 51.853 | 49.9649 | 47.5764 | 40.1482 | 5.0268 | -18.5858 | -31.7585 | -27.1617 | 332328 | 439711 | PENWORTHAM
| Blackburn | 66.6112 | 61.9942 | 42.1379 | 39.3818 | 38.4829 | 37.4332 | 36.239 | 35.1308 | 34.0202 | 32.5513 | 27.4066 | 24.8047 | 24.2436 | 24.227 | 84.6112 | 79.9942 | 60.1379 | 57.3818 | 56.4829 | 55.4332 | 54.239 | 53.1308 | 52.0202 | 50.5513 | 45.4066 | 42.8047 | 42.2436 | 42.227 | 68.8627 | 66.8241 | 48.2047 | 46.3193 | 45.3336 | 44.293 | 43.0755 | 41.8248 | 40.4 | 38.9365 | 35.3305 | 32.8655 | 31.5378 | 30.9573 | 86.8627 | 84.8241 | 66.2047 | 64.3193 | 63.3336 | 62.293 | 61.0755 | 59.8248 | 58.4 | 56.9365 | 53.3305 | 50.8655 | 49.5378 | 48.9573 | 66.6532 | 62.0815 | 42.2678 | 39.558 | 38.7161 | 37.7252 | 36.5911 | 35.5419 | 34.507 | 33.2601 | 28.6541 | 26.5522 | 26.1938 | 26.5315 | 84.6532 | 80.0815 | 60.2678 | 57.558 | 56.7161 | 55.7252 | 54.5911 | 53.5419 | 52.507 | 51.2601 | 46.6541 | 44.5522 | 44.1938 | 44.5315 | 66.6651 | 62.0895 | 42.2594 | 39.5213 | 38.6274 | 37.553 | 36.2785 | 35.0543 | 33.8912 | 32.7082 | 25.8006 | 9.945 | -2.4106 | -10.4237 | 84.6651 | 80.0895 | 60.2594 | 57.5213 | 56.6274 | 55.553 | 54.2785 | 53.0543 | 51.8912 | 50.7082 | 43.8006 | 27.945 | 15.5894 | 7.5763 | 66.6681 | 62.0292 | 42.2072 | 39.5455 | 38.7504 | 37.82 | 36.6718 | 35.6119 | 34.3054 | 30.9591 | 12.8697 | -1.4562 | -9.4537 | -6.2119 | 84.6681 | 80.0292 | 60.2072 | 57.5455 | 56.7504 | 55.82 | 54.6718 | 53.6119 | 52.3054 | 48.9591 | 30.8697 | 16.5438 | 8.5463 | 11.7881 | 370584 | 429294 | PENWORTHAM
| Blackpool | 38.0499 | 36.6122 | 35.5537 | 34.2952 | 32.6411 | 30.817 | 28.883 | 26.8106 | 24.6957 | 22.2537 | 13.968 | 9.7967 | 8.9746 | 10.2883 | 56.0499 | 54.6122 | 53.5537 | 52.2952 | 50.6411 | 48.817 | 46.883 | 44.8106 | 42.6957 | 40.2537 | 31.968 | 27.7967 | 26.9746 | 28.2883 | 38.7308 | 37.8368 | 36.3441 | 34.9688 | 33.3021 | 31.44 | 29.0243 | 25.0424 | 20.6178 | 15.7262 | 13.035 | 11.4196 | 10.9397 | 10.3284 | 56.7308 | 55.8368 | 54.3441 | 52.9688 | 51.3021 | 49.44 | 47.0243 | 43.0424 | 38.6178 | 33.7262 | 31.035 | 29.4196 | 28.9397 | 28.3284 | 38.0993 | 36.7294 | 35.7475 | 34.5657 | 33.0018 | 31.2759 | 29.4412 | 27.4705 | 25.4961 | 23.3308 | 15.8128 | 12.37 | 11.9325 | 13.4198 | 56.0993 | 54.7294 | 53.7475 | 52.5657 | 51.0018 | 49.2759 | 47.4412 | 45.4705 | 43.4961 | 41.3308 | 33.8128 | 30.37 | 29.9325 | 31.4198 | 38.1054 | 36.7301 | 35.7829 | 34.6503 | 33.1212 | 31.3933 | 29.4372 | 27.3557 | 25.4908 | 23.6057 | 11.6687 | -12.9363 | -33.0222 | -46.997 | 56.1054 | 54.7301 | 53.7829 | 52.6503 | 51.1212 | 49.3933 | 47.4372 | 45.3557 | 43.4908 | 41.6057 | 29.6687 | 5.0637 | -15.0222 | -28.997 | 38.0608 | 36.5071 | 35.659 | 34.8072 | 33.4807 | 32.073 | 30.4719 | 28.8123 | 26.7712 | 20.8471 | -6.9061 | -31.5232 | -45.5753 | -40.3548 | 56.0608 | 54.5071 | 53.659 | 52.8072 | 51.4807 | 50.073 | 48.4719 | 46.8123 | 44.7712 | 38.8471 | 11.0939 | -13.5232 | -27.5753 | -22.3548 | 330835 | 435308 | PENWORTHAM
| Bloom St | 11.6185 | 8.2727 | 18.8252 | 24.264 | 23.6947 | 22.8811 | 22.119 | 21.4111 | 20.7489 | 20.0521 | 17.6206 | 16.3227 | 15.9716 | 16.4161 | 53.4185 | 50.0727 | 60.6252 | 66.064 | 65.4947 | 64.6811 | 63.919 | 63.2111 | 62.5489 | 61.8521 | 59.4206 | 58.1227 | 57.7716 | 58.2161 | 14.5019 | 13.6577 | 22.7323 | 27.823 | 26.9188 | 25.9454 | 24.935 | 23.9185 | 22.8604 | 21.7767 | 19.5162 | 17.9338 | 17.2362 | 17.3421 | 56.3019 | 55.4577 | 64.5323 | 69.623 | 68.7188 | 67.7454 | 66.735 | 65.7185 | 64.6604 | 63.5767 | 61.3162 | 59.7338 | 59.0362 | 59.1421 | 11.6463 | 8.3494 | 19.1035 | 24.1984 | 23.6662 | 22.8883 | 22.1615 | 21.4893 | 20.869 | 20.235 | 17.9289 | 16.7221 | 16.4146 | 16.8638 | 53.4463 | 50.1494 | 60.9035 | 65.9984 | 65.4662 | 64.6883 | 63.9615 | 63.2893 | 62.669 | 62.035 | 59.7289 | 58.5221 | 58.2146 | 58.6638 | 11.7723 | 8.5762 | 19.2571 | 24.7021 | 24.1965 | 23.428 | 22.6799 | 21.9734 | 21.3452 | 20.7544 | 18.2301 | 13.3292 | 9.8851 | 7.8804 | 53.5723 | 50.3762 | 61.0571 | 66.5021 | 65.9965 | 65.228 | 64.4799 | 63.7734 | 63.1452 | 62.5544 | 60.0301 | 55.1292 | 51.6851 | 49.6804 | 11.809 | 8.6428 | 19.3848 | 24.8395 | 24.3938 | 23.7072 | 23.0496 | 22.4491 | 21.9227 | 20.5191 | 14.36 | 9.8511 | 7.6441 | 9.5503 | 53.609 | 50.4428 | 61.1848 | 66.6395 | 66.1938 | 65.5072 | 64.8496 | 64.2491 | 63.7227 | 62.3191 | 56.16 | 51.6511 | 49.4441 | 51.3503 | 384221 | 397717 | SOUTH MANCHESTER
| Bolton | 35.1863 | 32.9796 | 31.2371 | 28.911 | 25.9995 | 22.7152 | 19.1731 | 15.5363 | 11.843 | 7.0782 | -7.1768 | -14.9873 | -16.2801 | -14.4237 | 47.1863 | 44.9796 | 43.2371 | 40.911 | 37.9995 | 34.7152 | 31.1731 | 27.5363 | 23.843 | 19.0782 | 4.8232 | -2.9873 | -4.2801 | -2.4237 | 36.4276 | 35.2027 | 32.8345 | 30.4947 | 27.813 | 24.8014 | 21.4824 | 18.0218 | 14.4321 | 10.3236 | 0.33876 | -6.3228 | -10.3357 | -12.3393 | 48.4276 | 47.2027 | 44.8345 | 42.4947 | 39.813 | 36.8014 | 33.4824 | 30.0218 | 26.4321 | 22.3236 | 12.3388 | 5.6772 | 1.6643 | -0.33931 | 35.3016 | 33.2432 | 31.6558 | 29.4499 | 26.6848 | 23.5513 | 20.157 | 16.6648 | 13.1823 | 8.8687 | -3.8401 | -10.3338 | -10.9791 | -8.5742 | 47.3016 | 45.2432 | 43.6558 | 41.4499 | 38.6848 | 35.5513 | 32.157 | 28.6648 | 25.1823 | 20.8687 | 8.1599 | 1.6662 | 1.0209 | 3.4258 | 35.2636 | 33.1442 | 31.5481 | 29.4031 | 26.7649 | 23.7576 | 20.3507 | 16.3244 | 13.2933 | 10.2404 | -10.2652 | -51.5939 | -82.9501 | -103.0737 | 47.2636 | 45.1442 | 43.5481 | 41.4031 | 38.7649 | 35.7576 | 32.3507 | 28.3244 | 25.2933 | 22.2404 | 1.7348 | -39.5939 | -70.9501 | -91.0737 | 35.16 | 32.6934 | 31.0574 | 29.1248 | 26.6649 | 22.7344 | 19.2323 | 16.377 | 12.8467 | 2.7778 | -44.126 | -81.0474 | -101.2121 | -93.2031 | 47.16 | 44.6934 | 43.0574 | 41.1248 | 38.6649 | 34.7344 | 31.2323 | 28.377 | 24.8467 | 14.7778 | -32.126 | -69.0474 | -89.2121 | -81.2031 | 372255 | 410566 | KEARSLEY
| Burnley | 68.5096 | 66.9078 | 65.9425 | 65.0678 | 63.9325 | 62.6217 | 61.2147 | 59.7514 | 58.2737 | 56.5814 | 50.7907 | 47.7716 | 47.1657 | 47.8496 | 86.5096 | 84.9078 | 83.9425 | 83.0678 | 81.9325 | 80.6217 | 79.2147 | 77.7514 | 76.2737 | 74.5814 | 68.7907 | 65.7716 | 65.1657 | 65.8496 | 69.2858 | 68.3825 | 67.2581 | 66.2972 | 65.1696 | 63.8974 | 62.5063 | 61.0421 | 59.5223 | 57.9604 | 53.8301 | 50.9406 | 49.4113 | 48.6212 | 87.2858 | 86.3825 | 85.2581 | 84.2972 | 83.1696 | 81.8974 | 80.5063 | 79.0421 | 77.5223 | 75.9604 | 71.8301 | 68.9406 | 67.4113 | 66.6212 | 68.5405 | 66.9991 | 66.057 | 65.2255 | 64.1429 | 62.8894 | 61.5407 | 60.1358 | 58.7402 | 57.2182 | 51.899 | 49.3429 | 48.9659 | 49.7019 | 86.5405 | 84.9991 | 84.057 | 83.2255 | 82.1429 | 80.8894 | 79.5407 | 78.1358 | 76.7402 | 75.2182 | 69.899 | 67.3429 | 66.9659 | 67.7019 | 68.5377 | 66.9706 | 66.0521 | 65.2377 | 64.2202 | 63.0458 | 61.744 | 60.3997 | 59.2137 | 58.0082 | 50.1631 | 33.2109 | 20.317 | 12.5121 | 86.5377 | 84.9706 | 84.0521 | 83.2377 | 82.2202 | 81.0458 | 79.744 | 78.3997 | 77.2137 | 76.0082 | 68.1631 | 51.2109 | 38.317 | 30.5121 | 68.6305 | 67.043 | 66.1599 | 65.4866 | 64.6137 | 63.654 | 62.5701 | 61.4835 | 60.0018 | 55.8212 | 36.7123 | 21.5945 | 13.4135 | 16.8993 | 86.6305 | 85.043 | 84.1599 | 83.4866 | 82.6137 | 81.654 | 80.5701 | 79.4835 | 78.0018 | 73.8212 | 54.7123 | 39.5945 | 31.4135 | 34.8993 | 385569 | 434469 | ROCHDALE
| Bury | 51.4142 | 49.4506 | 48.6253 | 47.4001 | 45.808 | 43.8774 | 41.8675 | 39.8353 | 37.8192 | 35.7743 | 28.4545 | 24.1732 | 22.6884 | 22.2234 | 69.4142 | 67.4506 | 66.6253 | 65.4001 | 63.808 | 61.8774 | 59.8675 | 57.8353 | 55.8192 | 53.7743 | 46.4545 | 42.1732 | 40.6884 | 40.2234 | 52.9745 | 52.2689 | 50.8307 | 49.1686 | 47.3344 | 45.361 | 43.2355 | 41.0072 | 38.6824 | 36.3102 | 31.1578 | 27.6429 | 25.6098 | 24.8293 | 70.9745 | 70.2689 | 68.8307 | 67.1686 | 65.3344 | 63.361 | 61.2355 | 59.0072 | 56.6824 | 54.3102 | 49.1578 | 45.6429 | 43.6098 | 42.8293 | 51.2571 | 49.355 | 48.5915 | 47.4288 | 45.9453 | 44.1523 | 42.2325 | 40.2911 | 38.3983 | 36.5827 | 29.9622 | 26.6798 | 25.6364 | 25.7815 | 69.2571 | 67.355 | 66.5915 | 65.4288 | 63.9453 | 62.1523 | 60.2325 | 58.2911 | 56.3983 | 54.5827 | 47.9622 | 44.6798 | 43.6364 | 43.7815 | 51.5598 | 49.7588 | 49.1085 | 48.0709 | 46.7125 | 45.007 | 43.2251 | 41.4305 | 39.6845 | 37.9715 | 30.5164 | 10.9923 | -5.0714 | -17.2492 | 69.5598 | 67.7588 | 67.1085 | 66.0709 | 64.7125 | 63.007 | 61.2251 | 59.4305 | 57.6845 | 55.9715 | 48.5164 | 28.9923 | 12.9286 | 0.7508 | 51.404 | 49.3216 | 48.6372 | 47.7356 | 46.5637 | 45.1341 | 43.5382 | 41.9947 | 40.4417 | 38.5959 | 16.9891 | -1.6128 | -13.6133 | -11.0897 | 69.404 | 67.3216 | 66.6372 | 65.7356 | 64.5637 | 63.1341 | 61.5382 | 59.9947 | 58.4417 | 56.5959 | 34.9891 | 16.3872 | 4.3867 | 6.9103 | 380272 | 411184 | KEARSLEY
| Buxton | 34.3153 | 33.3684 | 33.3876 | 33.1359 | 32.7223 | 32.1784 | 31.6179 | 31.0746 | 30.5599 | 27.4891 | 15.6191 | 13.7482 | 13.3177 | 13.4533 | 65.8153 | 64.8684 | 64.8876 | 64.6359 | 64.2223 | 63.6784 | 63.1179 | 62.5746 | 62.0599 | 58.9891 | 47.1191 | 45.2482 | 44.8177 | 44.9533 | 35.3929 | 35.3036 | 34.9098 | 34.3652 | 33.761 | 33.1144 | 32.4119 | 31.7034 | 30.9889 | 30.2787 | 28.4474 | 27.0584 | 26.2208 | 25.7374 | 66.8929 | 66.8036 | 66.4098 | 65.8652 | 65.261 | 64.6144 | 63.9119 | 63.2034 | 62.4889 | 61.7787 | 59.9474 | 58.5584 | 57.7208 | 57.2374 | 34.3266 | 33.3914 | 33.4227 | 33.1834 | 32.7843 | 32.2567 | 31.7127 | 31.186 | 30.6942 | 27.6673 | 15.9568 | 14.3826 | 14.3475 | 14.7857 | 65.8266 | 64.8914 | 64.9227 | 64.6834 | 64.2843 | 63.7567 | 63.2127 | 62.686 | 62.1942 | 59.1673 | 47.4568 | 45.8826 | 45.8475 | 46.2857 | 34.417 | 33.5985 | 20.8328 | 7.8028 | 7.5529 | 7.214 | 6.8477 | 6.4584 | 6.0001 | 3.7037 | -5.1208 | -11.4909 | -15.6721 | -17.9899 | 65.917 | 65.0985 | 52.3328 | 39.3028 | 39.0529 | 38.714 | 38.3477 | 37.9584 | 37.5001 | 35.2037 | 26.3792 | 20.0091 | 15.8279 | 13.5101 | 34.4249 | 33.5961 | 20.8488 | 7.8672 | 7.6608 | 7.3743 | 6.9636 | 6.603 | 6.1268 | 3.2742 | -10.901 | -16.0489 | -18.562 | -16.6695 | 65.9249 | 65.0961 | 52.3488 | 39.3672 | 39.1608 | 38.8743 | 38.4636 | 38.103 | 37.6268 | 34.7742 | 20.599 | 15.4511 | 12.938 | 14.8305 | 407769 | 375476 | STALYBRIDGE
| Carlisle | 30.0513 | 27.1813 | 25.791 | 20.8674 | 15.4256 | 9.4991 | 3.1748 | -2.3181 | -8.3239 | -16.7573 | -35.9147 | -48.4476 | -52.5104 | -51.3894 | 53.0513 | 50.1813 | 48.791 | 43.8674 | 38.4256 | 32.4991 | 26.1748 | 20.6819 | 14.6761 | 6.2427 | -12.9147 | -25.4476 | -29.5104 | -28.3894 | 32.0425 | 30.8029 | 28.6536 | 25.8079 | 22.5592 | 18.936 | 14.8738 | 10.8758 | 6.7517 | 2.5618 | -8.297 | -17.263 | -24.1294 | -28.2996 | 55.0425 | 53.8029 | 51.6536 | 48.8079 | 45.5592 | 41.936 | 37.8738 | 33.8758 | 29.7517 | 25.5618 | 14.703 | 5.737 | -1.1294 | -5.2996 | 30.1057 | 27.2623 | 25.8684 | 20.9984 | 15.625 | 9.7806 | 3.5422 | -1.8609 | -7.7302 | -15.866 | -34.0331 | -43.8677 | -46.1315 | -43.7604 | 53.1057 | 50.2623 | 48.8684 | 43.9984 | 38.625 | 32.7806 | 26.5422 | 21.1391 | 15.2698 | 7.134 | -11.0331 | -20.8677 | -23.1315 | -20.7604 | 30.1709 | 27.3432 | 26.0376 | 21.2221 | 15.8989 | 10.0605 | 3.6838 | -1.8267 | -7.6691 | -17.1347 | -43.7519 | -80.0538 | -103.2847 | -118.3895 | 53.1709 | 50.3432 | 49.0376 | 44.2221 | 38.8989 | 33.0605 | 26.6838 | 21.1733 | 15.3309 | 5.8653 | -20.7519 | -57.0538 | -80.2847 | -95.3895 | 30.3148 | 27.3912 | 26.006 | 21.3301 | 16.0929 | 9.9857 | -0.024505 | -10.2742 | -16.5345 | -27.7707 | -69.2302 | -99.2676 | -114.0766 | -107.9115 | 53.3148 | 50.3912 | 49.006 | 44.3301 | 39.0929 | 32.9857 | 22.9755 | 12.7258 | 6.4655 | -4.7707 | -46.2302 | -76.2676 | -91.0766 | -84.9115 | 338655 | 556583 | HARKER
| Carlisle North | 9.9883 | 7.8213 | 6.883 | 6.8032 | 6.6693 | 6.4795 | 6.2702 | 6.0612 | 5.8563 | 5.6489 | 4.5508 | 3.1149 | 2.0505 | 0.84978 | 30.4883 | 28.3213 | 27.383 | 27.3032 | 27.1693 | 26.9795 | 26.7702 | 26.5612 | 26.3563 | 26.1489 | 25.0508 | 23.6149 | 22.5505 | 21.3498 | 11.2722 | 10.3053 | 9.6871 | 9.4873 | 9.2631 | 9.0158 | 8.7339 | 8.4374 | 8.1262 | 7.8039 | 6.9974 | 6.1472 | 5.2867 | 4.6366 | 31.7722 | 30.8053 | 30.1871 | 29.9873 | 29.7631 | 29.5158 | 29.2339 | 28.9374 | 28.6262 | 28.3039 | 27.4974 | 26.6472 | 25.7867 | 25.1366 | 9.9969 | 7.8382 | 6.9082 | 6.8368 | 6.7121 | 6.5324 | 6.3341 | 6.1366 | 5.9461 | 5.7623 | 4.8794 | 4.1139 | 3.379 | 2.8093 | 30.4969 | 28.3382 | 27.4082 | 27.3368 | 27.2121 | 27.0324 | 26.8341 | 26.6366 | 26.4461 | 26.2623 | 25.3794 | 24.6139 | 23.879 | 23.3093 | 10.0134 | 7.8723 | 6.9593 | 6.9039 | 6.7941 | 6.6035 | 6.369 | 6.1129 | 5.8422 | 5.5596 | 3.4002 | 0.75293 | -0.92107 | -2.245 | 30.5134 | 28.3723 | 27.4593 | 27.4039 | 27.2941 | 27.1035 | 26.869 | 26.6129 | 26.3422 | 26.0596 | 23.9002 | 21.2529 | 19.5789 | 18.255 | 10.0086 | 7.8475 | 6.9235 | 6.8671 | 6.7551 | 6.5373 | 6.2403 | 5.9002 | 5.5214 | 5.0301 | 2.2333 | -0.22439 | -1.9143 | -1.7137 | 30.5086 | 28.3475 | 27.4235 | 27.3671 | 27.2551 | 27.0373 | 26.7403 | 26.4002 | 26.0214 | 25.5301 | 22.7333 | 20.2756 | 18.5857 | 18.7863 | 338547 | 560280 | HARKER
| Carrington BSP | 31.5203 | 30.4207 | 29.8698 | 29.4511 | 28.9149 | 28.3026 | 27.6391 | 26.9602 | 25.1398 | 24.3903 | 18.2021 | 12.8836 | 10.9439 | 8.806 | 52.5203 | 51.4207 | 50.8698 | 50.4511 | 49.9149 | 49.3026 | 48.6391 | 47.9602 | 46.1398 | 45.3903 | 39.2021 | 33.8836 | 31.9439 | 29.806 | 32.0828 | 31.5015 | 30.9407 | 30.4661 | 29.9287 | 29.3342 | 28.6834 | 28.0008 | 27.1507 | 26.2364 | 24.0836 | 21.9375 | 19.8082 | 17.994 | 53.0828 | 52.5015 | 51.9407 | 51.4661 | 50.9287 | 50.3342 | 49.6834 | 49.0008 | 48.1507 | 47.2364 | 45.0836 | 42.9375 | 40.8082 | 38.994 | 31.525 | 30.4302 | 29.8854 | 29.4738 | 28.9471 | 28.3465 | 27.6949 | 27.0276 | 25.2274 | 24.5279 | 18.6674 | 14.6004 | 13.1221 | 11.9308 | 52.525 | 51.4302 | 50.8854 | 50.4738 | 49.9471 | 49.3465 | 48.6949 | 48.0276 | 46.2274 | 45.5279 | 39.6674 | 35.6004 | 34.1221 | 32.9308 | 31.5405 | 30.4755 | 29.9745 | 29.6115 | 29.1643 | 28.6491 | 28.0645 | 27.4598 | 25.7657 | 25.176 | 11.7068 | -3.3668 | -12.1375 | -18.3595 | 52.5405 | 51.4755 | 50.9745 | 50.6115 | 50.1643 | 49.6491 | 49.0645 | 48.4598 | 46.7657 | 46.176 | 32.7068 | 17.6332 | 8.8625 | 2.6405 | 31.5466 | 30.4431 | 29.9319 | 29.6015 | 26.0928 | 25.7982 | 25.3861 | 24.9206 | 23.2602 | 21.3296 | 1.7222 | -8.0212 | -14.361 | -14.4871 | 52.5466 | 51.4431 | 50.9319 | 50.6015 | 47.0928 | 46.7982 | 46.3861 | 45.9206 | 44.2602 | 42.3296 | 22.7222 | 12.9788 | 6.639 | 6.5129 | 373110 | 393020 | CARRINGTON
| Castleton | 59.5426 | 56.9743 | 54.1596 | 48.7944 | 43.1587 | 32.7228 | 29.5707 | 27.3364 | 25.4419 | 23.6199 | 16.4338 | 10.5323 | 7.1235 | 3.8546 | 77.5426 | 74.9743 | 72.1596 | 66.7944 | 61.1587 | 50.7228 | 47.5707 | 45.3364 | 43.4419 | 41.6199 | 34.4338 | 28.5323 | 25.1235 | 21.8546 | 61.1643 | 60.0442 | 57.4858 | 53.0471 | 48.4547 | 40.3158 | 37.586 | 35.5146 | 34.0941 | 32.6575 | 27.2637 | 22.6691 | 19.2098 | 16.5395 | 79.1643 | 78.0442 | 75.4858 | 71.0471 | 66.4547 | 58.3158 | 55.586 | 53.5146 | 52.0941 | 50.6575 | 45.2637 | 40.6691 | 37.2098 | 34.5395 | 59.5903 | 57.07 | 54.3013 | 48.9716 | 43.3852 | 32.9924 | 29.8968 | 27.7209 | 25.963 | 24.4813 | 18.0806 | 13.412 | 10.887 | 8.7045 | 77.5903 | 75.07 | 72.3013 | 66.9716 | 61.3852 | 50.9924 | 47.8968 | 45.7209 | 43.963 | 42.4813 | 36.0806 | 31.412 | 28.887 | 26.7045 | 59.5969 | 57.07 | 54.2665 | 48.8714 | 43.2083 | 32.6542 | 29.2449 | 26.6685 | 24.5848 | 22.9641 | 11.026 | -12.6972 | -30.9065 | -43.0537 | 77.5969 | 75.07 | 72.2665 | 66.8714 | 61.2083 | 50.6542 | 47.2449 | 44.6685 | 42.5848 | 40.9641 | 29.026 | 5.3028 | -12.9065 | -25.0537 | 59.5949 | 57.029 | 54.2368 | 48.8971 | 43.2755 | 32.1817 | 28.2195 | 25.1833 | 23.2246 | 18.711 | -6.8114 | -28.2193 | -40.5621 | -38.6385 | 77.5949 | 75.029 | 72.2368 | 66.8971 | 61.2755 | 50.1817 | 46.2195 | 43.1833 | 41.2246 | 36.711 | 11.1886 | -10.2193 | -22.5621 | -20.6385 | 388461 | 411290 | ROCHDALE
| Chadderton | 24.5812 | 21.6036 | 19.6927 | 17.6661 | 15.0411 | 12.1311 | 9.0537 | 5.9087 | 2.7389 | -0.83065 | -15.2007 | -24.2736 | -28.1795 | -29.3993 | 42.5812 | 39.6036 | 37.6927 | 35.6661 | 33.0411 | 30.1311 | 27.0537 | 23.9087 | 20.7389 | 17.1693 | 2.7993 | -6.2736 | -10.1795 | -11.3993 | 26.154 | 24.5482 | 22.3419 | 20.346 | 17.9866 | 15.4222 | 12.6641 | 9.8199 | 6.9176 | 3.9922 | -6.3598 | -14.2252 | -19.1837 | -22.5447 | 44.154 | 42.5482 | 40.3419 | 38.346 | 35.9866 | 33.4222 | 30.6641 | 27.8199 | 24.9176 | 21.9922 | 11.6402 | 3.7748 | -1.1837 | -4.5447 | 24.6707 | 21.7839 | 19.9643 | 18.0154 | 15.4999 | 12.7052 | 9.7417 | 6.7087 | 3.7062 | 0.49346 | -12.3906 | -19.8314 | -22.8915 | -23.4192 | 42.6707 | 39.7839 | 37.9643 | 36.0154 | 33.4999 | 30.7052 | 27.7417 | 24.7087 | 21.7062 | 18.4935 | 5.6094 | -1.8314 | -4.8915 | -5.4192 | 24.6717 | 21.7856 | 19.9598 | 17.9918 | 15.5265 | 12.7116 | 9.519 | 6.2142 | 3.2237 | 0.1832 | -19.1444 | -52.5831 | -78.9546 | -97.4177 | 42.6717 | 39.7856 | 37.9598 | 35.9918 | 33.5265 | 30.7116 | 27.519 | 24.2142 | 21.2237 | 18.1832 | -1.1444 | -34.5831 | -60.9546 | -79.4177 | 24.6204 | 21.4762 | 19.5661 | 17.7156 | 15.3282 | 12.7507 | 9.8313 | 6.8818 | 3.4312 | -4.3574 | -42.6513 | -74.2328 | -92.3269 | -88.2711 | 42.6204 | 39.4762 | 37.5661 | 35.7156 | 33.3282 | 30.7507 | 27.8313 | 24.8818 | 21.4312 | 13.6426 | -24.6513 | -56.2328 | -74.3269 | -70.2711 | 389137 | 403821 | WHITEGATE
| Droylsden | 48.2208 | 46.7594 | 45.7079 | 44.4089 | 42.6971 | 40.7501 | 38.3132 | 36.0937 | 33.6603 | 30.7776 | 20.574 | 15.1327 | 13.6612 | 14.0257 | 66.2208 | 64.7594 | 63.7079 | 62.4089 | 60.6971 | 58.7501 | 56.3132 | 54.0937 | 51.6603 | 48.7776 | 38.574 | 33.1327 | 31.6612 | 32.0257 | 48.8165 | 47.9443 | 46.597 | 45.2832 | 43.6935 | 41.8934 | 39.8797 | 37.769 | 35.571 | 33.3278 | 26.4344 | 21.1509 | 18.0412 | 16.0366 | 66.8165 | 65.9443 | 64.597 | 63.2832 | 61.6935 | 59.8934 | 57.8797 | 55.769 | 53.571 | 51.3278 | 44.4344 | 39.1509 | 36.0412 | 34.0366 | 48.3226 | 46.9774 | 46.0111 | 44.7839 | 43.1692 | 41.3217 | 38.9838 | 36.7303 | 34.3229 | 31.7121 | 22.5498 | 18.0361 | 16.9209 | 17.5441 | 66.3226 | 64.9774 | 64.0111 | 62.7839 | 61.1692 | 59.3217 | 56.9838 | 54.7303 | 52.3229 | 49.7121 | 40.5498 | 36.0361 | 34.9209 | 35.5441 | 48.2534 | 46.8264 | 45.8275 | 44.5776 | 43.0124 | 41.2091 | 38.8475 | 36.6917 | 34.7717 | 32.8181 | 19.5399 | -7.752 | -29.1241 | -43.6068 | 66.2534 | 64.8264 | 63.8275 | 62.5776 | 61.0124 | 59.2091 | 56.8475 | 54.6917 | 52.7717 | 50.8181 | 37.5399 | 10.248 | -11.1241 | -25.6068 | 48.3661 | 46.9005 | 45.9265 | 44.8439 | 43.4307 | 41.8906 | 39.8175 | 38.0062 | 35.6472 | 29.0754 | -1.6618 | -26.4062 | -40.5801 | -36.611 | 66.3661 | 64.9005 | 63.9265 | 62.8439 | 61.4307 | 59.8906 | 57.8175 | 56.0062 | 53.6472 | 47.0754 | 16.3382 | -8.4062 | -22.5801 | -18.611 | 390140 | 398146 | STALYBRIDGE
| Egremont | 81.2703 | 80.1658 | 79.5355 | 78.5594 | 77.3236 | 66.9911 | 56.542 | 54.9568 | 53.4077 | 51.4012 | 44.5617 | 41.5904 | 41.6648 | 43.9582 | 99.2703 | 98.1658 | 97.5355 | 96.5594 | 95.3236 | 84.9911 | 74.542 | 72.9568 | 71.4077 | 69.4012 | 62.5617 | 59.5904 | 59.6648 | 61.9582 | 82.1257 | 81.7326 | 80.807 | 79.9309 | 78.8986 | 77.7203 | 76.4099 | 75.0344 | 73.625 | 72.1981 | 68.3676 | 65.4696 | 64.0685 | 63.8442 | 100.1257 | 99.7326 | 98.807 | 97.9309 | 96.8986 | 95.7203 | 94.4099 | 93.0344 | 91.625 | 90.1981 | 86.3676 | 83.4696 | 82.0685 | 81.8442 | 81.3047 | 80.2574 | 79.6902 | 78.7785 | 77.6136 | 67.3541 | 56.9777 | 55.4637 | 54.0124 | 52.2339 | 46.2088 | 43.837 | 44.1986 | 46.4915 | 99.3047 | 98.2574 | 97.6902 | 96.7785 | 95.6136 | 85.3541 | 74.9777 | 73.4637 | 72.0124 | 70.2339 | 64.2088 | 61.837 | 62.1986 | 64.4915 | 81.3275 | 80.2285 | 79.6171 | 78.706 | 77.5182 | 67.1977 | 56.6375 | 54.9314 | 53.5123 | 52.0587 | 44.6766 | 31.5493 | 23.2093 | 17.7137 | 99.3275 | 98.2285 | 97.6171 | 96.706 | 95.5182 | 85.1977 | 74.6375 | 72.9314 | 71.5123 | 70.0587 | 62.6766 | 49.5493 | 41.2093 | 35.7137 | 81.3046 | 80.0553 | 79.3814 | 78.4834 | 77.284 | 67.0873 | 56.7491 | 55.3609 | 54.0555 | 50.6437 | 34.9961 | 24.1342 | 19.2893 | 22.9017 | 99.3046 | 98.0553 | 97.3814 | 96.4834 | 95.284 | 85.0873 | 74.7491 | 73.3609 | 72.0555 | 68.6437 | 52.9961 | 42.1342 | 37.2893 | 40.9017 | 301070 | 513074 | HARKER
| Frederick Rd | 26.5886 | 16.2601 | 11.2214 | 8.3778 | 6.8844 | 5.0762 | 3.2658 | 70.4873 | 68.6966 | 66.6439 | 58.0605 | 51.1615 | 46.8165 | 44.3278 | 68.5886 | 58.2601 | 53.2214 | 50.3778 | 48.8844 | 47.0762 | 45.2658 | 43.4873 | 41.6966 | 39.6439 | 31.0605 | 24.1615 | 19.8165 | 17.3278 | 32.2274 | 27.4946 | 23.8406 | 21.3113 | 19.4614 | 17.484 | 15.3976 | 82.2743 | 80.0968 | 77.8806 | 70.7962 | 63.8825 | 58.7477 | 54.9631 | 74.2274 | 69.4946 | 65.8406 | 63.3113 | 61.4614 | 59.484 | 57.3976 | 55.2743 | 53.0968 | 50.8806 | 43.7962 | 36.8825 | 31.7477 | 27.9631 | 26.6353 | 16.4033 | 11.4672 | 8.6969 | 7.289 | 5.5659 | 3.8405 | 71.1478 | 69.4686 | 67.6095 | 59.8293 | 54.0852 | 50.3408 | 48.5688 | 68.6353 | 58.4033 | 53.4672 | 50.6969 | 49.289 | 47.5659 | 45.8405 | 44.1478 | 42.4686 | 40.6095 | 32.8293 | 27.0852 | 23.3408 | 21.5688 | 26.7087 | 16.4928 | 11.5537 | 8.7523 | 7.2792 | 5.3919 | 3.2966 | 70.1783 | 68.1495 | 66.08 | 54.9786 | 34.5727 | 17.7939 | 6.0554 | 68.7087 | 58.4928 | 53.5537 | 50.7523 | 49.2792 | 47.3919 | 45.2966 | 43.1783 | 41.1495 | 39.08 | 27.9786 | 7.5727 | -9.2061 | -20.9446 | 26.7654 | 16.5432 | 11.6499 | 8.9231 | 7.4284 | 5.5227 | 3.5472 | 70.5564 | 68.4899 | 64.0578 | 41.9383 | 21.6806 | 9.9655 | 11.0877 | 68.7654 | 58.5432 | 53.6499 | 50.9231 | 49.4284 | 47.5227 | 45.5472 | 43.5564 | 41.4899 | 37.0578 | 14.9383 | -5.3194 | -17.0345 | -15.9123 | 381795 | 399250 | KEARSLEY
| Golborne | 49.368 | 47.4212 | 45.6767 | 44.021 | 41.9125 | 39.1244 | 36.1384 | 33.3053 | 30.4727 | 27.4408 | 17.1011 | 10.5751 | 8.2612 | 6.7769 | 67.368 | 65.4212 | 63.6767 | 62.021 | 59.9125 | 57.1244 | 54.1384 | 51.3053 | 48.4727 | 45.4408 | 35.1011 | 28.5751 | 26.2612 | 24.7769 | 50.7164 | 50.2939 | 48.5482 | 47.1054 | 45.4319 | 43.4059 | 41.1833 | 38.9341 | 36.6145 | 34.3085 | 26.8702 | 21.4984 | 17.9857 | 15.5706 | 68.7164 | 68.2939 | 66.5482 | 65.1054 | 63.4319 | 61.4059 | 59.1833 | 56.9341 | 54.6145 | 52.3085 | 44.8702 | 39.4984 | 35.9857 | 33.5706 | 49.7678 | 47.4625 | 45.7883 | 44.1673 | 42.0954 | 39.3959 | 36.498 | 33.7505 | 31.039 | 28.2743 | 19.0695 | 14.28 | 12.7175 | 12.8327 | 67.7678 | 65.4625 | 63.7883 | 62.1673 | 60.0954 | 57.3959 | 54.498 | 51.7505 | 49.039 | 46.2743 | 37.0695 | 32.28 | 30.7175 | 30.8327 | 49.4491 | 47.5326 | 45.874 | 44.3227 | 42.4516 | 39.8938 | 37.0964 | 34.4484 | 32.0606 | 29.7627 | 16.1602 | -8.9558 | -27.9461 | -40.4463 | 67.4491 | 65.5326 | 63.874 | 62.3227 | 60.4516 | 57.8938 | 55.0964 | 52.4484 | 50.0606 | 47.7627 | 34.1602 | 9.0442 | -9.9461 | -22.4463 | 49.3702 | 47.366 | 45.6771 | 44.2217 | 42.4671 | 40.1481 | 37.5192 | 35.0836 | 32.2781 | 26.2355 | -1.7736 | -24.1927 | -36.6186 | -33.6076 | 67.3702 | 65.366 | 63.6771 | 62.2217 | 60.4671 | 58.1481 | 55.5192 | 53.0836 | 50.2781 | 44.2355 | 16.2264 | -6.1927 | -18.6186 | -15.6076 | 360607 | 397690 | BOLD
| Greenhill | 44.6056 | 42.7381 | 41.8844 | 40.7304 | 39.2277 | 37.4643 | 35.616 | 33.7379 | 31.819 | 29.5813 | 21.5033 | 15.9546 | 13.5216 | 13.0846 | 62.6056 | 60.7381 | 59.8844 | 58.7304 | 57.2277 | 55.4643 | 53.616 | 51.7379 | 49.819 | 47.5813 | 39.5033 | 33.9546 | 31.5216 | 31.0846 | 45.778 | 44.8851 | 43.4905 | 42.0938 | 40.4877 | 38.7219 | 36.8077 | 34.8184 | 32.7587 | 30.6296 | 24.579 | 19.4223 | 16.0263 | 13.8165 | 63.778 | 62.8851 | 61.4905 | 60.0938 | 58.4877 | 56.7219 | 54.8077 | 52.8184 | 50.7587 | 48.6296 | 42.579 | 37.4223 | 34.0263 | 31.8165 | 44.6827 | 42.8879 | 42.1087 | 41.0256 | 39.6066 | 37.9284 | 36.165 | 34.3716 | 32.5681 | 30.5487 | 23.2825 | 18.7361 | 16.8258 | 16.7952 | 62.6827 | 60.8879 | 60.1087 | 59.0256 | 57.6066 | 55.9284 | 54.165 | 52.3716 | 50.5681 | 48.5487 | 41.2825 | 36.7361 | 34.8258 | 34.7952 | 44.6608 | 42.8345 | 42.0179 | 40.8907 | 39.4349 | 37.6484 | 35.6159 | 33.516 | 31.5839 | 29.6451 | 17.8626 | -6.9928 | -26.9522 | -40.1709 | 62.6608 | 60.8345 | 60.0179 | 58.8907 | 57.4349 | 55.6484 | 53.6159 | 51.516 | 49.5839 | 47.6451 | 35.8626 | 11.0072 | -8.9522 | -22.1709 | 44.7487 | 42.9491 | 42.2206 | 41.2658 | 39.9162 | 38.3225 | 36.5381 | 34.7192 | 32.4092 | 26.3397 | -1.5317 | -24.0184 | -36.9483 | -33.5877 | 62.7487 | 60.9491 | 60.2206 | 59.2658 | 57.9162 | 56.3225 | 54.5381 | 52.7192 | 50.4092 | 44.3397 | 16.4683 | -6.0184 | -18.9483 | -15.5877 | 393262 | 404755 | WHITEGATE
| Hartshead-Heyrod | 30.7573 | 28.9139 | 27.5696 | 25.6107 | 23.2635 | 20.5421 | 17.437 | 14.1539 | 10.852 | 7.0569 | -6.0343 | -12.6593 | -14.0977 | -12.8366 | 92.7573 | 90.9139 | 89.5696 | 87.6107 | 85.2635 | 82.5421 | 79.437 | 76.1539 | 72.852 | 69.0569 | 55.9657 | 49.3407 | 47.9023 | 49.1634 | 31.676 | 30.5605 | 28.7035 | 26.7742 | 24.6492 | 22.1984 | 19.4545 | 16.5716 | 13.5751 | 10.5346 | 1.2677 | -5.3113 | -9.1061 | -11.2507 | 93.676 | 92.5605 | 90.7035 | 88.7742 | 86.6492 | 84.1984 | 81.4545 | 78.5716 | 75.5751 | 72.5346 | 63.2677 | 56.6887 | 52.8939 | 50.7493 | 30.8387 | 29.1012 | 27.867 | 26.0096 | 23.784 | 21.0941 | 18.0493 | 14.877 | 11.7365 | 8.3056 | -3.4648 | -8.9423 | -9.9172 | -8.3956 | 92.8387 | 91.1012 | 89.867 | 88.0096 | 85.784 | 83.0941 | 80.0493 | 76.877 | 73.7365 | 70.3056 | 58.5352 | 53.0577 | 52.0828 | 53.6044 | 30.8351 | 29.0536 | 27.8134 | 25.9968 | 23.8669 | 21.3556 | 18.4637 | 15.4582 | 12.8248 | 10.1226 | -6.3441 | -39.0178 | -63.8332 | -80.2822 | 92.8351 | 91.0536 | 89.8134 | 87.9968 | 85.8669 | 83.3556 | 80.4637 | 77.4582 | 74.8248 | 72.1226 | 55.6559 | 22.9822 | -1.8332 | -18.2822 | 30.9442 | 29.0375 | 27.8112 | 26.2317 | 24.3342 | 22.2183 | 19.6897 | 17.1303 | 14.1467 | 6.1709 | -31.1567 | -60.3738 | -76.3842 | -70.595 | 92.9442 | 91.0375 | 89.8112 | 88.2317 | 86.3342 | 84.2183 | 81.6897 | 79.1303 | 76.1467 | 68.1709 | 30.8433 | 1.6262 | -14.3842 | -8.595 | 397322 | 399942 | STALYBRIDGE
| Hazel Grove | 47.011 | 45.5923 | 44.3687 | 42.911 | 39.4179 | 35.7172 | 33.5848 | 31.3287 | 29.0393 | 26.2703 | 16.8007 | 10.0177 | 9.4416 | 10.596 | 65.011 | 63.5923 | 62.3687 | 60.911 | 57.4179 | 53.7172 | 51.5848 | 49.3287 | 47.0393 | 44.2703 | 34.8007 | 28.0177 | 27.4416 | 28.596 | 47.4044 | 46.3819 | 45.0091 | 43.6794 | 42.106 | 40.3283 | 38.3693 | 36.2943 | 34.1032 | 31.892 | 25.1598 | 20.3401 | 17.4149 | 15.5988 | 65.4044 | 64.3819 | 63.0091 | 61.6794 | 60.106 | 58.3283 | 56.3693 | 54.2943 | 52.1032 | 49.892 | 43.1598 | 38.3401 | 35.4149 | 33.5988 | 47.0316 | 45.7306 | 44.5758 | 43.1738 | 39.7483 | 36.143 | 34.1032 | 31.9363 | 29.7763 | 27.2997 | 18.8286 | 12.7461 | 12.4035 | 13.5543 | 65.0316 | 63.7306 | 62.5758 | 61.1738 | 57.7483 | 54.143 | 52.1032 | 49.9363 | 47.7763 | 45.2997 | 36.8286 | 30.7461 | 30.4035 | 31.5543 | 47.0573 | 45.7075 | 44.5939 | 43.2771 | 40.1363 | 36.7906 | 34.8583 | 32.8359 | 31.0824 | 29.235 | 13.2285 | -10.8603 | -28.6401 | -40.7781 | 65.0573 | 63.7075 | 62.5939 | 61.2771 | 58.1363 | 54.7906 | 52.8583 | 50.8359 | 49.0824 | 47.235 | 31.2285 | 7.1397 | -10.6401 | -22.7781 | 47.0456 | 45.5181 | 44.435 | 43.2954 | 41.7756 | 35.6733 | 30.1063 | 28.8297 | 27.0485 | 21.6866 | -4.9252 | -26.291 | -37.6141 | -33.4415 | 65.0456 | 63.5181 | 62.435 | 61.2954 | 59.7756 | 53.6733 | 48.1063 | 46.8297 | 45.0485 | 39.6866 | 13.0748 | -8.291 | -19.6141 | -15.4415 | 391313 | 386877 | BREDBURY
| Huncoat | 29.2281 | 27.2545 | 26.6171 | 25.8357 | 24.749 | 23.3906 | 21.9665 | 20.5316 | 19.0823 | 17.1729 | 8.0653 | 2.7304 | 1.0853 | 1.115 | 47.2281 | 45.2545 | 44.6171 | 43.8357 | 42.749 | 41.3906 | 39.9665 | 38.5316 | 37.0823 | 35.1729 | 26.0653 | 20.7304 | 19.0853 | 19.115 | 30.8973 | 30.3008 | 29.2551 | 28.2522 | 27.1129 | 25.8459 | 24.476 | 23.0709 | 21.6284 | 19.6444 | 13.4616 | 9.0864 | 6.5402 | 5.1951 | 48.8973 | 48.3008 | 47.2551 | 46.2522 | 45.1129 | 43.8459 | 42.476 | 41.0709 | 39.6284 | 37.6444 | 31.4616 | 27.0864 | 24.5402 | 23.1951 | 29.2539 | 27.3115 | 26.709 | 25.9643 | 24.9212 | 23.6099 | 22.233 | 20.8449 | 19.4658 | 17.9816 | 10.2029 | 6.1033 | 5.0517 | 5.7245 | 47.2539 | 45.3115 | 44.709 | 43.9643 | 42.9212 | 41.6099 | 40.233 | 38.8449 | 37.4658 | 35.9816 | 28.2029 | 24.1033 | 23.0517 | 23.7245 | 29.307 | 27.3929 | 26.7881 | 26.01 | 24.8967 | 23.4338 | 21.7692 | 20.017 | 18.3499 | 16.5792 | 4.4431 | -22.516 | -43.7193 | -58.6136 | 47.307 | 45.3929 | 44.7881 | 44.01 | 42.8967 | 41.4338 | 39.7692 | 38.017 | 36.3499 | 34.5792 | 22.4431 | -4.516 | -25.7193 | -40.6136 | 29.32 | 27.3088 | 26.6775 | 25.9599 | 24.8947 | 23.434 | 21.8488 | 20.2029 | 17.9327 | 12.0161 | -16.794 | -41.6056 | -57.8506 | -53.3202 | 47.32 | 45.3088 | 44.6775 | 43.9599 | 42.8947 | 41.434 | 39.8488 | 38.2029 | 35.9327 | 30.0161 | 1.206 | -23.6056 | -39.8506 | -35.3202 | 377997 | 431083 | PADIHAM
| Hyde | 59.0726 | 57.5828 | 56.2647 | 53.9929 | 50.4933 | 48.2266 | 45.762 | 43.2235 | 40.662 | 37.8335 | 27.4068 | 22.0927 | 20.7779 | 21.2665 | 77.0726 | 75.5828 | 74.2647 | 71.9929 | 68.4933 | 66.2266 | 63.762 | 61.2235 | 58.662 | 55.8335 | 45.4068 | 40.0927 | 38.7779 | 39.2665 | 59.776 | 58.8496 | 57.2164 | 55.1145 | 52.2709 | 50.2346 | 47.9865 | 45.6365 | 43.2006 | 40.7381 | 34.2436 | 30.2365 | 28.2591 | 27.46 | 77.776 | 76.8496 | 75.2164 | 73.1145 | 70.2709 | 68.2346 | 65.9865 | 63.6365 | 61.2006 | 58.7381 | 52.2436 | 48.2365 | 46.2591 | 45.46 | 59.1133 | 57.6652 | 56.3907 | 54.1777 | 50.5764 | 48.3873 | 45.9976 | 43.5296 | 41.0798 | 38.5075 | 29.0431 | 24.566 | 23.5537 | 24.2777 | 77.1133 | 75.6652 | 74.3907 | 72.1777 | 68.5764 | 66.3873 | 63.9976 | 61.5296 | 59.0798 | 56.5075 | 47.0431 | 42.566 | 41.5537 | 42.2777 | 59.1486 | 57.749 | 56.5633 | 54.4639 | 50.6799 | 48.5527 | 46.1819 | 43.7198 | 41.4156 | 39.0977 | 25.7242 | 3.5406 | -12.6933 | -23.0458 | 77.1486 | 75.749 | 74.5633 | 72.4639 | 68.6799 | 66.5527 | 64.1819 | 61.7198 | 59.4156 | 57.0977 | 43.7242 | 21.5406 | 5.3067 | -5.0458 | 59.0698 | 57.3473 | 56.0422 | 54.044 | 50.2388 | 48.2951 | 46.1099 | 43.9273 | 41.3141 | 35.7093 | 9.986 | -9.116 | -18.9793 | -15.2301 | 77.0698 | 75.3473 | 74.0422 | 72.044 | 68.2388 | 66.2951 | 64.1099 | 61.9273 | 59.3141 | 53.7093 | 27.986 | 8.884 | -0.97931 | 2.7699 | 395522 | 395647 | STALYBRIDGE
| Kendal (Parkside Rd) | 24.5836 | 22.3596 | 20.6297 | 18.5682 | 16.1252 | 13.3431 | 7.4828 | 4.2677 | -1.527 | -5.7588 | -21.5801 | -34.1483 | -39.5906 | -37.3767 | 42.5836 | 40.3596 | 38.6297 | 36.5682 | 34.1252 | 31.3431 | 25.4828 | 22.2677 | 16.473 | 12.2412 | -3.5801 | -16.1483 | -21.5906 | -19.3767 | 25.3019 | 23.7134 | 21.5826 | 19.5203 | 17.1692 | 14.4482 | 11.2263 | 7.8193 | 4.2323 | 0.50598 | -8.8914 | -17.6022 | -23.8772 | -27.9074 | 43.3019 | 41.7134 | 39.5826 | 37.5203 | 35.1692 | 32.4482 | 29.2263 | 25.8193 | 22.2323 | 18.506 | 9.1086 | 0.39775 | -5.8772 | -9.9074 | 24.6555 | 22.5745 | 21.0261 | 19.1424 | 16.9183 | 14.3039 | 8.6148 | 5.5708 | -0.005019 | -3.7593 | -18.1671 | -29.563 | -34.4243 | -32.0005 | 42.6555 | 40.5745 | 39.0261 | 37.1424 | 34.9183 | 32.3039 | 26.6148 | 23.5708 | 17.995 | 14.2407 | -0.1671 | -11.563 | -16.4243 | -14.0005 | 24.6229 | 22.3243 | 20.5288 | 18.3986 | 15.7492 | 12.6582 | 6.4345 | 2.7287 | -2.8952 | -6.3981 | -34.5552 | -61.432 | -77.8508 | -89.4835 | 42.6229 | 40.3243 | 38.5288 | 36.3986 | 33.7492 | 30.6582 | 24.4345 | 20.7287 | 15.1048 | 11.6019 | -16.5552 | -43.432 | -59.8508 | -71.4835 | 24.6154 | 22.1717 | 20.5124 | 18.6141 | 16.1213 | 6.2305 | 0.99905 | -1.9988 | -4.8805 | -11.455 | -44.7784 | -67.5715 | -78.2436 | -73.1628 | 42.6154 | 40.1717 | 38.5124 | 36.6141 | 34.1213 | 24.2305 | 18.9991 | 16.0012 | 13.1195 | 6.545 | -26.7784 | -49.5715 | -60.2436 | -55.1628 | 351915 | 491858 | HUTTON
| Lancaster | 25.7034 | 22.8326 | 20.8836 | 18.6327 | 14.3043 | 11.287 | 8.0041 | 4.6413 | 0.98507 | -5.7415 | -22.0639 | -68.5046 | -70.6653 | -66.4968 | 25.7034 | 22.8326 | 20.8836 | 18.6327 | 14.3043 | 11.287 | 8.0041 | 4.6413 | 0.98507 | -5.7415 | -22.0639 | -68.5046 | -70.6653 | -66.4968 | 26.958 | 25.1568 | 22.7725 | 20.5594 | 17.9442 | 14.9918 | 11.7157 | 8.3109 | 4.7786 | 1.1558 | -8.961 | -17.6797 | -23.3515 | -26.9792 | 26.958 | 25.1568 | 22.7725 | 20.5594 | 17.9442 | 14.9918 | 11.7157 | 8.3109 | 4.7786 | 1.1558 | -8.961 | -17.6797 | -23.3515 | -26.9792 | 25.7861 | 23.0874 | 21.3164 | 19.2145 | 15.0548 | 12.2042 | 9.0743 | 5.5145 | 2.0067 | -4.2969 | -19.0373 | -63.8799 | -65.2413 | -60.4662 | 25.7861 | 23.0874 | 21.3164 | 19.2145 | 15.0548 | 12.2042 | 9.0743 | 5.5145 | 2.0067 | -4.2969 | -19.0373 | -63.8799 | -65.2413 | -60.4662 | 25.7716 | 22.8919 | 20.9566 | 18.7305 | 14.4894 | 11.3968 | 7.8014 | 2.9587 | -0.24425 | -5.7182 | -26.3177 | -98.9203 | -122.9435 | -136.7908 | 25.7716 | 22.8919 | 20.9566 | 18.7305 | 14.4894 | 11.3968 | 7.8014 | 2.9587 | -0.24425 | -5.7182 | -26.3177 | -98.9203 | -122.9435 | -136.7908 | 25.7945 | 22.8478 | 21.0468 | 19.0914 | 16.5373 | 10.3407 | 4.5593 | 0.63242 | -2.4277 | -10.8038 | -90.9867 | -119.0708 | -134.4145 | -125.3994 | 25.7945 | 22.8478 | 21.0468 | 19.0914 | 16.5373 | 10.3407 | 4.5593 | 0.63242 | -2.4277 | -10.8038 | -90.9867 | -119.0708 | -134.4145 | -125.3994 | 348644 | 463628 | HEYSHAM
| Leyland | 33.7628 | 30.9057 | 28.8231 | 26.6751 | 23.9907 | 20.9903 | 17.6702 | 14.2759 | 10.8544 | 6.9993 | -8.9745 | -17.6354 | -21.0248 | -23.5228 | 51.7628 | 48.9057 | 46.8231 | 44.6751 | 41.9907 | 38.9903 | 35.6702 | 32.2759 | 28.8544 | 24.9993 | 9.0255 | 0.36459 | -3.0248 | -5.5228 | 35.0572 | 33.3442 | 31.0681 | 29.0624 | 26.7193 | 24.1236 | 21.2189 | 18.2346 | 15.1489 | 12.0464 | 1.4176 | -6.5273 | -11.6515 | -15.1682 | 53.0572 | 51.3442 | 49.0681 | 47.0624 | 44.7193 | 42.1236 | 39.2189 | 36.2346 | 33.1489 | 30.0464 | 19.4176 | 11.4727 | 6.3485 | 2.8318 | 33.8106 | 31.0475 | 29.0587 | 26.9927 | 24.4294 | 21.558 | 18.3676 | 15.1006 | 11.8569 | 8.3775 | -5.8951 | -12.4066 | -14.6575 | -15.2389 | 51.8106 | 49.0475 | 47.0587 | 44.9927 | 42.4294 | 39.558 | 36.3676 | 33.1006 | 29.8569 | 26.3775 | 12.1049 | 5.5934 | 3.3425 | 2.7611 | 33.8321 | 31.0535 | 29.0947 | 27.0839 | 24.7009 | 22.014 | 18.9584 | 15.8551 | 13.0376 | 10.2087 | -9.0633 | -40.4756 | -61.1604 | -75.5021 | 51.8321 | 49.0535 | 47.0947 | 45.0839 | 42.7009 | 40.014 | 36.9584 | 33.8551 | 31.0376 | 28.2087 | 8.9367 | -22.4756 | -43.1604 | -57.5021 | 33.6068 | 30.4246 | 28.4118 | 26.5369 | 24.3261 | 21.8992 | 19.0429 | 16.2034 | 13.0542 | 4.0408 | -31.319 | -56.3461 | -69.9839 | -67.5902 | 51.6068 | 48.4246 | 46.4118 | 44.5369 | 42.3261 | 39.8992 | 37.0429 | 34.2034 | 31.0542 | 22.0408 | -13.319 | -38.3461 | -51.9839 | -49.5902 | 354121 | 423373 | PENWORTHAM
| Longsight | 41.2788 | 36.0683 | 29.5211 | 23.7318 | 19.8765 | 15.7527 | 11.582 | 8.7079 | 5.8287 | 1.01 | -7.1602 | -11.203 | -12.7587 | -12.4538 | 59.2788 | 54.0683 | 47.5211 | 41.7318 | 37.8765 | 33.7527 | 29.582 | 26.7079 | 23.8287 | 19.01 | 10.8398 | 6.797 | 5.2413 | 5.5462 | 43.9144 | 41.6773 | 36.259 | 31.303 | 27.2865 | 23.1192 | 18.8407 | 15.828 | 12.7763 | 9.6959 | 4.2658 | -0.005771 | -2.5027 | -3.8755 | 61.9144 | 59.6773 | 54.259 | 49.303 | 45.2865 | 41.1192 | 36.8407 | 33.828 | 30.7763 | 27.6959 | 22.2658 | 17.9942 | 15.4973 | 14.1245 | 41.3247 | 36.1776 | 29.6856 | 23.9379 | 20.1405 | 16.0764 | 11.9651 | 9.1542 | 6.3614 | 1.7026 | -5.884 | -9.3929 | -10.6998 | -10.2178 | 59.3247 | 54.1776 | 47.6856 | 41.9379 | 38.1405 | 34.0764 | 29.9651 | 27.1542 | 24.3614 | 19.7026 | 12.116 | 8.6071 | 7.3002 | 7.7822 | 41.3814 | 36.2833 | 29.8524 | 24.1561 | 20.4437 | 16.462 | 12.3212 | 9.4659 | 6.8085 | 2.4787 | -7.7492 | -26.2562 | -38.928 | -46.6436 | 59.3814 | 54.2833 | 47.8524 | 42.1561 | 38.4437 | 34.462 | 30.3212 | 27.4659 | 24.8085 | 20.4787 | 10.2508 | -8.2562 | -20.928 | -28.6436 | 41.4479 | 36.3518 | 29.9783 | 24.4076 | 20.7805 | 16.9589 | 13.0276 | 10.4106 | 7.5973 | -1.5889 | -22.268 | -37.5695 | -45.7405 | -42.1146 | 59.4479 | 54.3518 | 47.9783 | 42.4076 | 38.7805 | 34.9589 | 31.0276 | 28.4106 | 25.5973 | 16.4111 | -4.268 | -19.5695 | -27.7405 | -24.1146 | 385592 | 396016 | BREDBURY
| Lower Darwen | 4.6795 | 1.9447 | 0.98037 | 0.24586 | -0.82335 | -2.1503 | -4.2769 | 13.4794 | 11.2296 | 8.717 | -2.5588 | -8.6067 | -9.8539 | -9.3474 | 54.6795 | 51.9447 | 50.9804 | 50.2459 | 49.1766 | 47.8497 | 45.7231 | 43.4794 | 41.2296 | 38.717 | 27.4412 | 21.3933 | 20.1461 | 20.6526 | 6.7244 | 5.7535 | 4.5078 | 3.5016 | 2.1661 | 0.41337 | -1.6151 | 16.1393 | 13.7998 | 11.417 | 5.5073 | 1.5501 | -0.61502 | -1.4604 | 56.7244 | 55.7535 | 54.5078 | 53.5016 | 52.1661 | 50.4134 | 48.3849 | 46.1393 | 43.7998 | 41.417 | 35.5073 | 31.5501 | 29.385 | 28.5396 | 4.7226 | 2.0487 | 1.1486 | 0.47624 | -0.51969 | -1.7647 | -3.5691 | 14.2587 | 12.1165 | 9.8346 | -0.69499 | -5.8469 | -6.7362 | -5.7773 | 54.7226 | 52.0487 | 51.1486 | 50.4762 | 49.4803 | 48.2353 | 46.4309 | 44.2587 | 42.1165 | 39.8346 | 29.305 | 24.1531 | 23.2638 | 24.2227 | 4.7586 | 2.0805 | 1.1515 | 0.42616 | -0.65315 | -2.0533 | -3.7554 | 14.42 | 12.7384 | 11.0384 | -3.7523 | -29.9374 | -49.3946 | -61.5846 | 54.7586 | 52.0805 | 51.1515 | 50.4262 | 49.3469 | 47.9467 | 46.2446 | 44.42 | 42.7384 | 41.0384 | 26.2477 | 0.062563 | -19.3946 | -31.5846 | 4.8043 | 2.0942 | 1.1998 | 0.58589 | -0.53781 | -1.7955 | -3.2439 | 15.279 | 12.5675 | 4.0729 | -25.5683 | -48.1747 | -60.641 | -55.8942 | 54.8043 | 52.0942 | 51.1998 | 50.5859 | 49.4622 | 48.2045 | 46.7561 | 45.279 | 42.5675 | 34.0729 | 4.4317 | -18.1747 | -30.641 | -25.8942 | 369695 | 424981 | ROCHDALE
| Lytham | 44.7342 | 43.917 | 43.1238 | 42.1738 | 41.0428 | 39.8342 | 38.561 | 37.2672 | 35.9656 | 34.5266 | 29.6202 | 27.0717 | 26.3622 | 26.5612 | 33.7342 | 32.917 | 32.1238 | 31.1738 | 30.0428 | 28.8342 | 27.561 | 26.2672 | 24.9656 | 23.5266 | 18.6202 | 16.0717 | 15.3622 | 15.5612 | 44.8989 | 44.2191 | 43.299 | 42.4136 | 41.3951 | 40.2729 | 39.0601 | 37.8095 | 36.5184 | 35.2087 | 31.396 | 28.652 | 27.0102 | 25.8817 | 33.8989 | 33.2191 | 32.299 | 31.4136 | 30.3951 | 29.2729 | 28.0601 | 26.8095 | 25.5184 | 24.2087 | 20.396 | 17.652 | 16.0102 | 14.8817 | 44.7558 | 44.0121 | 43.2932 | 42.3905 | 41.3189 | 40.1688 | 38.952 | 37.7132 | 36.4865 | 35.194 | 30.7817 | 28.582 | 27.9966 | 28.2394 | 33.7558 | 33.0121 | 32.2932 | 31.3905 | 30.3189 | 29.1688 | 27.952 | 26.7132 | 25.4865 | 24.194 | 19.7817 | 17.582 | 16.9966 | 17.2394 | 44.7636 | 43.9741 | 43.231 | 42.3167 | 41.2664 | 40.1236 | 38.8773 | 37.6301 | 36.5126 | 35.4075 | 29.3333 | 18.3044 | 10.3095 | 4.6832 | 33.7636 | 32.9741 | 32.231 | 31.3167 | 30.2664 | 29.1236 | 27.8773 | 26.6301 | 25.5126 | 24.4075 | 18.3333 | 7.3044 | -0.69049 | -6.3168 | 44.7225 | 43.8167 | 43.0744 | 42.2462 | 41.2833 | 40.2952 | 39.2224 | 38.1875 | 37.0616 | 34.2624 | 21.3207 | 11.4301 | 6.0332 | 7.7665 | 33.7225 | 32.8167 | 32.0744 | 31.2462 | 30.2833 | 29.2952 | 28.2224 | 27.1875 | 26.0616 | 23.2624 | 10.3207 | 0.43009 | -4.9668 | -3.2335 | 335361 | 429316 | PENWORTHAM
| Moss Nook | 45.792 | 43.1744 | 33.5411 | 23.777 | 17.5781 | 11.1639 | 4.6083 | 50.009 | 44.9821 | 42.0814 | 30.4529 | 23.6706 | 21.515 | 21.7131 | 72.792 | 70.1744 | 60.5411 | 50.777 | 44.5781 | 38.1639 | 31.6083 | 25.009 | 19.9821 | 17.0814 | 5.4529 | -1.3294 | -3.485 | -3.2869 | 47.1002 | 45.6319 | 35.7272 | 25.9948 | 19.9925 | 13.8107 | 7.4418 | 52.9985 | 50.4933 | 47.9857 | 40.0188 | 34.1899 | 30.8532 | 29.0079 | 74.1002 | 72.6319 | 62.7272 | 52.9948 | 46.9925 | 40.8107 | 34.4418 | 27.9985 | 25.4933 | 22.9857 | 15.0188 | 9.1899 | 5.8532 | 4.0079 | 45.8224 | 43.2418 | 33.6495 | 23.9282 | 17.7856 | 11.436 | 4.9438 | 50.4058 | 45.4796 | 42.8306 | 32.0354 | 25.9598 | 24.1159 | 24.4063 | 72.8224 | 70.2418 | 60.6495 | 50.9282 | 44.7856 | 38.436 | 31.9438 | 25.4058 | 20.4796 | 17.8306 | 7.0354 | 0.95979 | -0.88413 | -0.59367 | 45.9064 | 43.4266 | 33.9517 | 24.3123 | 18.3267 | 12.1194 | 5.6618 | 51.1603 | 46.5432 | 44.3113 | 30.7636 | 8.4465 | -6.4645 | -16.5031 | 72.9064 | 70.4266 | 60.9517 | 51.3123 | 45.3267 | 39.1194 | 32.6618 | 26.1603 | 21.5432 | 19.3113 | 5.7636 | -16.5535 | -31.4645 | -41.5031 | 45.57 | 42.6636 | 33.2352 | 23.825 | 18.0526 | 12.1755 | 6.0456 | 51.3884 | 46.7493 | 41.7841 | 16.3854 | -1.6044 | -11.0614 | -8.1946 | 72.57 | 69.6636 | 60.2352 | 50.825 | 45.0526 | 39.1755 | 33.0456 | 26.3884 | 21.7493 | 16.7841 | -8.6146 | -26.6044 | -36.0614 | -33.1946 | 384073 | 385068 | MACCLESFIELD
| Moss Nook Primary | 17.6665 | 17.2103 | 17.1088 | 16.9662 | 16.7588 | 16.4945 | 16.2161 | 15.9326 | 15.4958 | 15.0192 | 13.3965 | 12.6502 | 12.5707 | 12.8164 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.0617 | 17.9461 | 17.7534 | 17.539 | 17.2988 | 17.0404 | 16.7602 | 16.3558 | 15.8513 | 15.3368 | 14.2394 | 13.6426 | 13.4234 | 13.4371 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.6722 | 17.222 | 17.127 | 16.9913 | 16.7921 | 16.5372 | 16.2684 | 15.9947 | 15.6805 | 15.243 | 13.6779 | 13.0158 | 12.9536 | 13.1936 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.6959 | 17.2717 | 17.2019 | 17.0897 | 16.9136 | 16.679 | 16.4262 | 16.1648 | 15.8974 | 15.6155 | 13.9086 | 10.5357 | 7.5715 | 5.5553 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.6893 | 17.2409 | 17.1668 | 17.0695 | 16.9115 | 16.7073 | 16.481 | 16.2579 | 16.0219 | 15.4921 | 11.2932 | 7.8373 | 5.871 | 6.5596 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 384084 | 385010 | SOUTH MANCHESTER
| Nelson | 8.5478 | 6.4295 | 5.6893 | 5.0549 | 4.1498 | 3.0203 | 1.8167 | 0.60832 | -0.61938 | -2.1048 | -7.1056 | -9.7138 | -10.3064 | -9.5434 | 29.9606 | 27.8423 | 27.1021 | 26.4677 | 25.5626 | 24.4331 | 23.2295 | 22.0211 | 20.7934 | 19.308 | 14.3072 | 11.699 | 11.1064 | 11.8694 | 10.1167 | 9.3261 | 8.2734 | 7.3797 | 6.3291 | 5.1603 | 3.8677 | 2.5305 | 1.1375 | -0.29399 | -3.4774 | -5.9132 | -7.2839 | -7.7814 | 31.5295 | 30.7389 | 29.6862 | 28.7925 | 27.7419 | 26.5731 | 25.2805 | 23.9433 | 22.5503 | 21.1188 | 17.9354 | 15.4996 | 14.1289 | 13.6314 | 8.5956 | 6.5348 | 5.8534 | 5.276 | 4.4338 | 3.3675 | 2.2269 | 1.0809 | -0.062502 | -1.386 | -5.885 | -7.938 | -8.3008 | -7.3689 | 30.0084 | 27.9476 | 27.2662 | 26.6888 | 25.8466 | 24.7803 | 23.6397 | 22.4937 | 21.3503 | 20.0268 | 15.5278 | 13.4748 | 13.112 | 14.0439 | 8.6274 | 6.5631 | 5.8724 | 5.2895 | 4.4234 | 3.2886 | 1.992 | 0.66366 | -0.53514 | -1.7427 | -9.8539 | -28.6791 | -42.878 | -51.2666 | 30.0402 | 27.9759 | 27.2852 | 26.7023 | 25.8362 | 24.7014 | 23.4048 | 22.0765 | 20.8777 | 19.6701 | 11.5589 | -7.2663 | -21.4652 | -29.8538 | 8.7166 | 6.6839 | 6.0623 | 5.6159 | 4.8585 | 3.8973 | 2.8004 | 1.7078 | 0.10552 | -4.6399 | -26.1406 | -42.8312 | -51.4695 | -46.6273 | 30.1294 | 28.0967 | 27.4751 | 27.0287 | 26.2713 | 25.3101 | 24.2132 | 23.1206 | 21.5183 | 16.7729 | -4.7278 | -21.4184 | -30.0567 | -25.2145 | 385989 | 438643 | PADIHAM
| New Mills | 32.9512 | 32.2999 | 32.1655 | 31.4189 | 30.5023 | 29.4727 | 28.3148 | 27.1213 | 25.8245 | 24.4209 | 19.5887 | 17.2585 | 16.9955 | 17.7096 | 41.4512 | 40.7999 | 40.6655 | 39.9189 | 39.0023 | 37.9727 | 36.8148 | 35.6213 | 34.3245 | 32.9209 | 28.0887 | 25.7585 | 25.4955 | 26.2096 | 33.5591 | 33.4033 | 32.6705 | 31.9691 | 31.1891 | 30.3063 | 29.2925 | 28.228 | 27.116 | 25.9808 | 23.0178 | 20.9529 | 19.8049 | 19.1223 | 42.0591 | 41.9033 | 41.1705 | 40.4691 | 39.6891 | 38.8063 | 37.7925 | 36.728 | 35.616 | 34.4808 | 31.5178 | 29.4529 | 28.3049 | 27.6223 | 32.9591 | 32.316 | 32.1908 | 31.7086 | 30.8194 | 29.8208 | 28.6942 | 27.5311 | 26.2803 | 24.9773 | 20.4376 | 18.3825 | 18.1897 | 18.9898 | 41.4591 | 40.816 | 40.6908 | 40.2086 | 39.3194 | 38.3208 | 37.1942 | 36.0311 | 34.7803 | 33.4773 | 28.9376 | 26.8825 | 26.6897 | 27.4898 | 32.999 | 32.3983 | 32.2928 | 31.59 | 30.7668 | 29.6515 | 28.5648 | 27.4477 | 26.4908 | 25.525 | 17.6669 | 8.6244 | 3.1334 | -1.0987 | 41.499 | 40.8983 | 40.7928 | 40.09 | 39.2668 | 38.1515 | 37.0648 | 35.9477 | 34.9908 | 34.025 | 26.1669 | 17.1244 | 11.6334 | 7.4013 | 32.9983 | 32.3677 | 32.101 | 31.4758 | 30.5568 | 29.7629 | 28.8294 | 24.3616 | 23.7269 | 22.1559 | 12.3541 | 4.9864 | 1.6877 | 2.9793 | 41.4983 | 40.8677 | 40.601 | 39.9758 | 39.0568 | 38.2629 | 37.3294 | 32.8616 | 32.2269 | 30.6559 | 20.8541 | 13.4864 | 10.1877 | 11.4793 | 401141 | 383916 | STALYBRIDGE
| Orrell | 11.3624 | 9.8808 | 8.9775 | 7.8867 | 6.4606 | 4.769 | 2.9258 | 1.0525 | -0.79201 | -2.8439 | -18.244 | -22.9569 | -24.4664 | -24.1128 | 68.3624 | 66.8808 | 65.9775 | 64.8867 | 63.4606 | 61.769 | 59.9258 | 58.0525 | 56.208 | 54.1561 | 38.756 | 34.0431 | 32.5336 | 32.8872 | 12.2254 | 11.495 | 10.3929 | 9.3504 | 8.1165 | 6.6562 | 5.0352 | 3.3671 | 1.6589 | -0.044068 | -5.3256 | -8.9842 | -11.0984 | -12.5054 | 69.2254 | 68.495 | 67.3929 | 66.3504 | 65.1165 | 63.6562 | 62.0352 | 60.3671 | 58.6589 | 56.9559 | 51.6744 | 48.0158 | 45.9016 | 44.4946 | 11.3735 | 9.9234 | 9.0536 | 7.9959 | 6.6148 | 5.003 | 3.1975 | 1.36 | -0.4207 | -2.311 | -17.0889 | -20.8831 | -21.9649 | -21.0833 | 68.3735 | 66.9234 | 66.0536 | 64.9959 | 63.6148 | 62.003 | 60.1975 | 58.36 | 56.5793 | 54.689 | 39.9111 | 36.1169 | 35.0351 | 35.9167 | 11.4244 | 10.0099 | 9.1988 | 8.2265 | 7.0001 | 5.573 | 3.945 | 2.2726 | 0.82713 | -0.6555 | -18.4512 | -39.3299 | -52.5669 | -60.5184 | 68.4244 | 67.0099 | 66.1988 | 65.2265 | 64.0001 | 62.573 | 60.945 | 59.2726 | 57.8271 | 56.3445 | 38.5488 | 17.6701 | 4.4331 | -3.5184 | 11.3718 | 9.8203 | 8.9977 | 8.123 | 6.9907 | 5.7106 | 4.2606 | 2.8162 | 1.1124 | -12.8329 | -31.5358 | -46.8595 | -55.3585 | -52.0706 | 68.3718 | 66.8203 | 65.9977 | 65.123 | 63.9907 | 62.7106 | 61.2606 | 59.8162 | 58.1124 | 44.1671 | 25.4642 | 10.1405 | 1.6415 | 4.9294 | 352784 | 404565 | KIRKBY
| Padiham | 23.841 | 20.8091 | 19.1482 | 17.8159 | 14.7052 | 12.5072 | 10.1044 | 7.6053 | 2.0836 | -1.1399 | -19.1023 | -38.371 | -40.4834 | -39.9543 | 55.341 | 52.3091 | 50.6482 | 49.3159 | 46.2052 | 44.0072 | 41.6044 | 39.1053 | 33.5836 | 30.3601 | 12.3977 | -6.871 | -8.9834 | -8.4543 | 25.3923 | 23.8004 | 22.1916 | 20.6845 | 18.9095 | 16.9154 | 14.7058 | 12.3899 | 9.9855 | 7.527 | -0.28118 | -6.8418 | -11.3704 | -14.4261 | 56.8923 | 55.3004 | 53.6916 | 52.1845 | 50.4095 | 48.4154 | 46.2058 | 43.8899 | 41.4855 | 39.027 | 31.2188 | 24.6582 | 20.1296 | 17.0739 | 23.8768 | 20.923 | 19.3481 | 18.1825 | 15.1738 | 13.0774 | 10.767 | 8.2361 | 2.8525 | -0.067232 | -16.8291 | -34.8969 | -36.4545 | -35.4629 | 55.3768 | 52.423 | 50.8481 | 49.6825 | 46.6738 | 44.5774 | 42.267 | 39.7361 | 34.3525 | 31.4328 | 14.6709 | -3.3969 | -4.9545 | -3.9629 | 23.8674 | 20.7799 | 19.0259 | 17.7702 | 14.692 | 12.466 | 9.9409 | 7.3287 | 2.2316 | -0.32074 | -26.8633 | -48.6796 | -62.4347 | -72.4003 | 55.3674 | 52.2799 | 50.5259 | 49.2702 | 46.192 | 43.966 | 41.4409 | 38.8287 | 33.7316 | 31.1793 | 4.6367 | -17.1796 | -30.9347 | -40.9003 | 23.8507 | 20.6584 | 18.9038 | 17.5979 | 14.5792 | 12.5345 | 7.1239 | 4.7373 | 0.86151 | -4.0393 | -41.8517 | -57.8582 | -67.457 | -65.6909 | 55.3507 | 52.1584 | 50.4038 | 49.0979 | 46.0792 | 44.0345 | 38.6239 | 36.2373 | 32.3615 | 27.4607 | -10.3517 | -26.3582 | -35.957 | -34.1909 | 378571 | 433224 | PADIHAM
| Peel | 13.8765 | 12.7187 | 12.3579 | 11.759 | 10.9634 | 10.0349 | 9.0141 | 7.9023 | 6.9014 | 5.7623 | 1.1381 | -1.8951 | -2.9634 | -2.96 | 22.3765 | 21.2187 | 20.8579 | 20.259 | 19.4634 | 18.5349 | 17.5141 | 16.4023 | 15.4014 | 14.2623 | 9.6381 | 6.6049 | 5.5366 | 5.54 | 14.7666 | 14.3635 | 13.643 | 12.8396 | 11.9704 | 10.9388 | 9.8328 | 8.6981 | 7.5149 | 5.8984 | 3.6065 | 1.7601 | 0.34874 | -0.41131 | 23.2666 | 22.8635 | 22.143 | 21.3396 | 20.4704 | 19.4388 | 18.3328 | 17.1981 | 16.0149 | 14.3984 | 12.1065 | 10.2601 | 8.8487 | 8.0887 | 13.9136 | 12.7839 | 12.4085 | 11.84 | 11.0918 | 10.1918 | 9.2053 | 8.1653 | 7.2291 | 6.1972 | 2.1651 | -0.4263 | -1.2889 | -1.2247 | 22.4136 | 21.2839 | 20.9085 | 20.34 | 19.5918 | 18.6918 | 17.7053 | 16.6653 | 15.7291 | 14.6972 | 10.6651 | 8.0737 | 7.2111 | 7.2753 | 13.9498 | 12.8628 | 12.4884 | 11.9003 | 11.1084 | 10.0312 | 8.8418 | 7.6211 | 6.4909 | 5.3353 | -1.1737 | -9.7498 | -15.2791 | -19.2289 | 22.4498 | 21.3628 | 20.9884 | 20.4003 | 19.6084 | 18.5312 | 17.3418 | 16.1211 | 14.9909 | 13.8353 | 7.3263 | -1.2498 | -6.7791 | -10.7289 | 13.9317 | 12.7764 | 12.3683 | 11.791 | 10.9362 | 9.9505 | 8.8626 | 6.3449 | 5.3588 | 2.9377 | -6.3474 | -13.1583 | -16.5951 | -15.4331 | 22.4317 | 21.2764 | 20.8683 | 20.291 | 19.4362 | 18.4505 | 17.3626 | 14.8449 | 13.8588 | 11.4377 | 2.1526 | -4.6583 | -8.0951 | -6.9331 | 335644 | 432080 | PENWORTHAM
| Penrith & Shap | 46.9241 | 44.929 | 43.6219 | 42.0746 | 40.3756 | 38.4834 | 36.3552 | 34.1842 | 31.8077 | 28.4313 | 8.6599 | -5.4935 | -10.1782 | -10.1613 | 50.7241 | 48.729 | 47.4219 | 45.8746 | 44.1756 | 42.2834 | 40.1552 | 37.9842 | 35.6077 | 32.2313 | 12.4599 | -1.6935 | -6.3782 | -6.3613 | 47.7656 | 46.4976 | 44.8371 | 43.2977 | 41.5672 | 39.61 | 37.3737 | 35.0387 | 32.6066 | 30.0494 | 22.644 | 13.8388 | 6.4834 | 1.3166 | 51.5656 | 50.2976 | 48.6371 | 47.0977 | 45.3672 | 43.41 | 41.1737 | 38.8387 | 36.4066 | 33.8494 | 26.444 | 17.6388 | 10.2834 | 5.1166 | 46.9793 | 45.0848 | 43.8856 | 42.4467 | 40.8478 | 39.0545 | 37.0249 | 34.9519 | 32.7005 | 29.5489 | 11.1798 | -0.99086 | -4.7329 | -3.8355 | 50.7793 | 48.8848 | 47.6856 | 46.2467 | 44.6478 | 42.8545 | 40.8249 | 38.7519 | 36.5005 | 33.3489 | 14.9798 | 2.8091 | -0.93291 | -0.035544 | 46.9714 | 44.8897 | 43.5052 | 41.8267 | 39.8255 | 37.4891 | 34.6693 | 31.8312 | 29.1977 | 26.5106 | 4.6299 | -19.4252 | -29.8326 | -35.2124 | 50.7714 | 48.6897 | 47.3052 | 45.6267 | 43.6255 | 41.2891 | 38.4693 | 35.6312 | 32.9977 | 30.3106 | 8.4299 | -15.6252 | -26.0326 | -31.4124 | 46.9647 | 44.8075 | 43.4706 | 41.8818 | 39.7291 | 37.3955 | 33.4725 | 30.4221 | 27.9336 | 22.3807 | -11.722 | -27.1069 | -33.4932 | -29.8339 | 50.7647 | 48.6075 | 47.2706 | 45.6818 | 43.5291 | 41.1955 | 37.2725 | 34.2221 | 31.7336 | 26.1807 | -7.922 | -23.3069 | -29.6932 | -26.0339 | 349996 | 530398 | HUTTON
| Preston East | 54.6557 | 52.8866 | 51.7342 | 50.4821 | 48.9353 | 47.1858 | 45.2368 | 43.2952 | 41.3413 | 39.0972 | 29.363 | 23.2477 | 20.3934 | 19.0183 | 72.6557 | 70.8866 | 69.7342 | 68.4821 | 66.9353 | 65.1858 | 63.2368 | 61.2952 | 59.3413 | 57.0972 | 47.363 | 41.2477 | 38.3934 | 37.0183 | 55.4783 | 54.3799 | 52.8637 | 51.4056 | 49.7417 | 47.8785 | 45.8088 | 43.6231 | 41.3156 | 38.9177 | 33.1027 | 28.5189 | 25.4561 | 23.5417 | 73.4783 | 72.3799 | 70.8637 | 69.4056 | 67.7417 | 65.8785 | 63.8088 | 61.6231 | 59.3156 | 56.9177 | 51.1027 | 46.5189 | 43.4561 | 41.5417 | 54.7089 | 52.999 | 51.9082 | 50.7201 | 49.2482 | 47.5847 | 45.726 | 43.8772 | 42.0461 | 40.0177 | 31.0145 | 26.2245 | 24.0856 | 23.7238 | 72.7089 | 70.999 | 69.9082 | 68.7201 | 67.2482 | 65.5847 | 63.726 | 61.8772 | 60.0461 | 58.0177 | 49.0145 | 44.2245 | 42.0856 | 41.7238 | 54.7212 | 53.0171 | 51.9453 | 50.7833 | 49.2975 | 47.6294 | 45.719 | 43.7402 | 41.8793 | 39.9607 | 26.1946 | 5.6846 | -8.5343 | -19.3239 | 72.7212 | 71.0171 | 69.9453 | 68.7833 | 67.2975 | 65.6294 | 63.719 | 61.7402 | 59.8793 | 57.9607 | 44.1946 | 23.6846 | 9.4657 | -1.3239 | 54.6539 | 52.7626 | 51.6935 | 50.6468 | 49.2701 | 47.7627 | 44.8729 | 43.1116 | 41.2393 | 37.0725 | 14.0206 | -3.9699 | -15.7331 | -13.9706 | 72.6539 | 70.7626 | 69.6935 | 68.6468 | 67.2701 | 65.7627 | 62.8729 | 61.1116 | 59.2393 | 55.0725 | 32.0206 | 14.0301 | 2.2669 | 4.0294 | 356774 | 432942 | PENWORTHAM
| Radcliffe | 9.6043 | 8.5257 | 7.8781 | 6.9986 | 5.8981 | 4.6896 | 3.4175 | 2.1276 | 0.84442 | -0.5618 | -5.8212 | -8.0049 | -8.1906 | -7.5891 | 16.6043 | 15.5257 | 14.8781 | 13.9986 | 12.8981 | 11.6896 | 10.4175 | 9.1276 | 7.8444 | 6.4382 | 1.1788 | -1.0049 | -1.1906 | -0.58912 | 10.3053 | 9.8178 | 9.037 | 8.2873 | 7.3711 | 6.3823 | 5.3217 | 4.2336 | 3.1277 | 2.0388 | -1.3926 | -3.5785 | -4.6468 | -5.0308 | 17.3053 | 16.8178 | 16.037 | 15.2873 | 14.3711 | 13.3823 | 12.3217 | 11.2336 | 10.1277 | 9.0388 | 5.6074 | 3.4215 | 2.3532 | 1.9692 | 9.6264 | 8.5853 | 7.9127 | 7.0548 | 5.9851 | 4.8094 | 3.568 | 2.3059 | 1.0718 | -0.21053 | -5.0157 | -6.8382 | -6.8455 | -6.1216 | 16.6264 | 15.5853 | 14.9127 | 14.0548 | 12.9851 | 11.8094 | 10.568 | 9.3059 | 8.0718 | 6.7895 | 1.9843 | 0.16178 | 0.15453 | 0.87844 | 9.6576 | 8.6382 | 8.0829 | 7.3368 | 6.4057 | 5.3871 | 4.2956 | 3.2117 | 2.2677 | 1.3475 | -5.0109 | -15.4374 | -22.6906 | -27.4167 | 16.6576 | 15.6382 | 15.0829 | 14.3368 | 13.4057 | 12.3871 | 11.2956 | 10.2117 | 9.2677 | 8.3475 | 1.9891 | -8.4374 | -15.6906 | -20.4167 | 9.5905 | 8.4207 | 7.6648 | 6.9262 | 6.0311 | 4.7152 | 3.3481 | 2.4785 | 1.4575 | -1.0248 | -12.984 | -22.0335 | -26.8049 | -24.4147 | 16.5905 | 15.4207 | 14.6648 | 13.9262 | 13.0311 | 11.7152 | 10.3481 | 9.4785 | 8.4575 | 5.9752 | -5.984 | -15.0335 | -19.8049 | -17.4147 | 377524 | 406160 | KEARSLEY
| Red Bank | 32.4194 | 27.1424 | 24.2031 | 21.9445 | 20.705 | 19.1426 | 17.5588 | 15.9839 | 14.4129 | 12.5255 | 5.0433 | 0.58526 | -1.1232 | -1.0835 | 50.4194 | 45.1424 | 42.2031 | 39.9445 | 38.705 | 37.1426 | 35.5588 | 33.9839 | 32.4129 | 30.5255 | 23.0433 | 18.5853 | 16.8768 | 16.9165 | 35.4625 | 33.2762 | 30.8193 | 28.7603 | 27.1901 | 25.4623 | 23.519 | 21.4191 | 19.2357 | 16.9721 | 11.193 | 6.7273 | 4.0509 | 2.4857 | 53.4625 | 51.2762 | 48.8193 | 46.7603 | 45.1901 | 43.4623 | 41.519 | 39.4191 | 37.2357 | 34.9721 | 29.193 | 24.7273 | 22.0509 | 20.4857 | 32.4823 | 27.2878 | 24.4383 | 22.2596 | 21.1111 | 19.6405 | 18.1494 | 16.6684 | 15.213 | 13.6491 | 6.952 | 3.102 | 1.6629 | 1.8538 | 50.4823 | 45.2878 | 42.4383 | 40.2596 | 39.1111 | 37.6405 | 36.1494 | 34.6684 | 33.213 | 31.6491 | 24.952 | 21.102 | 19.6629 | 19.8538 | 32.5209 | 27.3296 | 24.451 | 22.2085 | 20.9595 | 19.3218 | 17.5362 | 15.711 | 13.988 | 12.2478 | 3.7667 | -14.1398 | -27.6258 | -37.1142 | 50.5209 | 45.3296 | 42.451 | 40.2085 | 38.9595 | 37.3218 | 35.5362 | 33.711 | 31.988 | 30.2478 | 21.7667 | 3.8602 | -9.6258 | -19.1142 | 32.579 | 27.373 | 24.5446 | 22.4118 | 21.2536 | 19.773 | 18.1797 | 16.5866 | 14.9498 | 11.085 | -8.8699 | -25.2676 | -34.4297 | -31.7769 | 50.579 | 45.373 | 42.5446 | 40.4118 | 39.2536 | 37.773 | 36.1797 | 34.5866 | 32.9498 | 29.085 | 9.1301 | -7.2676 | -16.4297 | -13.7769 | 384542 | 399276 | WHITEGATE
| Ribble | 105.6219 | 100.8678 | 98.0275 | 95.6823 | 92.5537 | 88.9526 | 84.6354 | 80.4941 | 76.3009 | 71.4282 | 53.7815 | 43.9095 | 40.7505 | 41.9756 | 141.6219 | 136.8678 | 134.0275 | 131.6823 | 128.5537 | 124.9526 | 120.6354 | 116.4941 | 112.3009 | 107.4282 | 89.7815 | 79.9095 | 76.7505 | 77.9756 | 108.0975 | 105.5443 | 102.6287 | 100.2537 | 97.331 | 94.2062 | 90.484 | 86.691 | 82.7633 | 78.7988 | 66.1579 | 56.5136 | 50.3763 | 47.2228 | 144.0975 | 141.5443 | 138.6287 | 136.2537 | 133.331 | 130.2062 | 126.484 | 122.691 | 118.7633 | 114.7988 | 102.1579 | 92.5136 | 86.3763 | 83.2228 | 105.7272 | 101.0891 | 98.3677 | 96.1315 | 93.1375 | 89.7632 | 85.621 | 81.647 | 77.6924 | 73.3319 | 57.737 | 49.9782 | 47.8052 | 49.8431 | 141.7272 | 137.0891 | 134.3677 | 132.1315 | 129.1375 | 125.7632 | 121.621 | 117.647 | 113.6924 | 109.3319 | 93.737 | 85.9782 | 83.8052 | 85.8431 | 105.7472 | 101.1198 | 96.3218 | 90.9587 | 84.9513 | 79.7297 | 75.7443 | 71.8678 | 68.4323 | 64.9854 | 43.3046 | 3.4754 | -26.1483 | -44.6667 | 141.7472 | 137.1198 | 132.3218 | 126.9587 | 120.9513 | 115.7297 | 111.7443 | 107.8678 | 104.4323 | 100.9854 | 79.3046 | 39.4754 | 9.8517 | -8.6667 | 105.6944 | 100.8266 | 96.1113 | 91.0481 | 85.2717 | 80.2494 | 76.5857 | 73.2654 | 69.3616 | 59.8927 | 14.7523 | -20.6547 | -39.9579 | -33.1615 | 141.6944 | 136.8266 | 132.1113 | 127.0481 | 121.2717 | 116.2494 | 112.5857 | 109.2654 | 105.3616 | 95.8927 | 50.7523 | 15.3453 | -3.9579 | 2.8385 | 351794 | 429241 | PENWORTHAM
| Risley | 2.6955 | 1.6768 | 1.3018 | 1.101 | 0.82116 | 0.47134 | 0.097892 | -0.28271 | -0.66846 | -1.1068 | -2.9574 | -4.4475 | -5.2527 | -5.7894 | 13.3955 | 12.3768 | 12.0018 | 11.801 | 11.5212 | 11.1713 | 10.7979 | 10.4173 | 10.0315 | 9.5932 | 7.7426 | 6.2525 | 5.4473 | 4.9106 | 3.3894 | 2.9882 | 2.6386 | 2.4078 | 2.1432 | 1.8455 | 1.5214 | 1.1903 | 0.85266 | 0.51485 | -0.64992 | -1.6071 | -2.2991 | -2.7461 | 14.0894 | 13.6882 | 13.3386 | 13.1078 | 12.8432 | 12.5455 | 12.2214 | 11.8903 | 11.5527 | 11.2149 | 10.0501 | 9.0929 | 8.4009 | 7.9539 | 2.7035 | 1.694 | 1.3281 | 1.1358 | 0.868 | 0.53103 | 0.17049 | -0.19738 | -0.56448 | -0.95597 | -2.5473 | -3.6373 | -4.2436 | -4.5209 | 13.4035 | 12.394 | 12.0281 | 11.8358 | 11.568 | 11.231 | 10.8705 | 10.5026 | 10.1355 | 9.744 | 8.1527 | 7.0627 | 6.4564 | 6.1791 | 2.7037 | 1.6904 | 1.3136 | 1.1017 | 0.80646 | 0.42524 | -0.010798 | -0.47489 | -0.93277 | -1.4084 | -4.3321 | -9.6027 | -13.6869 | -16.4042 | 13.4037 | 12.3904 | 12.0136 | 11.8017 | 11.5065 | 11.1252 | 10.6892 | 10.2251 | 9.7672 | 9.2916 | 6.3679 | 1.0973 | -2.9869 | -5.7042 | 2.6732 | 1.6053 | 1.2079 | 0.99288 | 0.69698 | 0.32079 | -0.18478 | -0.64832 | -1.1751 | -2.4131 | -8.1688 | -12.8875 | -15.6365 | -15.1686 | 13.3732 | 12.3053 | 11.9079 | 11.6929 | 11.397 | 11.0208 | 10.5152 | 10.0517 | 9.5249 | 8.2869 | 2.5312 | -2.1875 | -4.9365 | -4.4686 | 365181 | 392989 | BOLD
| Rochdale Central | 47.2051 | 46.0647 | 45.3133 | 44.5493 | 43.5914 | 42.5355 | 41.3846 | 40.1933 | 38.9308 | 37.3655 | 31.6343 | 28.4697 | 27.4682 | 27.178 | 59.2051 | 58.0647 | 57.3133 | 56.5493 | 55.5914 | 54.5355 | 53.3846 | 52.1933 | 50.9308 | 49.3655 | 43.6343 | 40.4697 | 39.4682 | 39.178 | 47.6409 | 46.8827 | 46.0049 | 45.2275 | 44.2574 | 43.1446 | 41.9322 | 40.6437 | 39.2867 | 37.8774 | 34.5584 | 31.5614 | 29.6829 | 28.4102 | 59.6409 | 58.8827 | 58.0049 | 57.2275 | 56.2574 | 55.1446 | 53.9322 | 52.6437 | 51.2867 | 49.8774 | 46.5584 | 43.5614 | 41.6829 | 40.4102 | 47.1401 | 46.0618 | 45.3142 | 44.5902 | 43.6834 | 42.6805 | 41.5828 | 40.4441 | 39.1249 | 37.6466 | 32.428 | 29.7806 | 29.0296 | 29.2546 | 59.1401 | 58.0618 | 57.3142 | 56.5902 | 55.6834 | 54.6805 | 53.5828 | 52.4441 | 51.1249 | 49.6466 | 44.428 | 41.7806 | 41.0296 | 41.2546 | 47.2481 | 46.1407 | 45.3742 | 44.6428 | 43.7624 | 42.7802 | 41.6582 | 40.5011 | 39.4569 | 38.3978 | 31.6904 | 19.0588 | 9.5726 | 3.3685 | 59.2481 | 58.1407 | 57.3742 | 56.6428 | 55.7624 | 54.7802 | 53.6582 | 52.5011 | 51.4569 | 50.3978 | 43.6904 | 31.0588 | 21.5726 | 15.3685 | 47.2415 | 46.0903 | 45.3779 | 44.74 | 43.9441 | 43.0994 | 42.1278 | 41.15 | 39.9616 | 36.9829 | 22.7826 | 11.5666 | 5.3164 | 6.9862 | 59.2415 | 58.0903 | 57.3779 | 56.74 | 55.9441 | 55.0994 | 54.1278 | 53.15 | 51.9616 | 48.9829 | 34.7826 | 23.5666 | 17.3164 | 18.9862 | 389111 | 413393 | ROCHDALE
| Rossendale | 55.9425 | 54.2068 | 52.9111 | 51.3852 | 49.4844 | 47.3398 | 45.0164 | 42.6009 | 37.2596 | 34.5328 | 24.3178 | 19.222 | 18.2531 | 19.1067 | 73.9425 | 72.2068 | 70.9111 | 69.3852 | 67.4844 | 65.3398 | 63.0164 | 60.6009 | 55.2596 | 52.5328 | 42.3178 | 37.222 | 36.2531 | 37.1067 | 56.6837 | 55.5579 | 53.905 | 52.3342 | 50.5261 | 48.5109 | 46.2927 | 43.9636 | 41.5426 | 39.0656 | 32.1256 | 27.1675 | 24.159 | 22.2578 | 74.6837 | 73.5579 | 71.905 | 70.3342 | 68.5261 | 66.5109 | 64.2927 | 61.9636 | 59.5426 | 57.0656 | 50.1256 | 45.1675 | 42.159 | 40.2578 | 55.99 | 54.3183 | 53.0887 | 51.6269 | 49.8048 | 47.7441 | 45.5037 | 43.1694 | 37.852 | 35.2409 | 25.9786 | 21.7488 | 21.0623 | 22.1394 | 73.99 | 72.3183 | 71.0887 | 69.6269 | 67.8048 | 65.7441 | 63.5037 | 61.1694 | 55.852 | 53.2409 | 43.9786 | 39.7488 | 39.0623 | 40.1394 | 56.0004 | 54.3291 | 53.1374 | 51.7364 | 50.0511 | 48.15 | 46.0276 | 43.841 | 39.2104 | 37.4322 | 20.7099 | -5.2786 | -24.6087 | -36.966 | 74.0004 | 72.3291 | 71.1374 | 69.7364 | 68.0511 | 66.15 | 64.0276 | 61.841 | 57.2104 | 55.4322 | 38.7099 | 12.7214 | -6.6087 | -18.966 | 56.0035 | 54.1906 | 53.0659 | 51.9009 | 50.4523 | 48.8868 | 44.2503 | 42.6362 | 40.4592 | 34.2469 | 4.1253 | -19.0489 | -31.521 | -26.6731 | 74.0035 | 72.1906 | 71.0659 | 69.9009 | 68.4523 | 66.8868 | 62.2503 | 60.6362 | 58.4592 | 52.2469 | 22.1253 | -1.0489 | -13.521 | -8.6731 | 380261 | 422010 | PADIHAM
| Royton | 31.1241 | 30.2629 | 29.6772 | 29.006 | 28.1531 | 27.1249 | 25.8818 | 24.5917 | 23.2907 | 21.8286 | 16.5174 | 13.3237 | 12.0883 | 11.6698 | 97.5369 | 96.6757 | 96.09 | 95.4188 | 94.5659 | 93.5377 | 92.2946 | 91.0045 | 89.7035 | 88.2414 | 82.9302 | 79.7365 | 78.5011 | 78.0826 | 31.4949 | 30.9558 | 30.2444 | 29.5701 | 28.7808 | 27.9003 | 26.9381 | 25.8987 | 24.7279 | 22.9126 | 19.6594 | 16.7883 | 14.88 | 13.5478 | 97.9077 | 97.3686 | 96.6572 | 95.9829 | 95.1936 | 94.3131 | 93.3509 | 92.3115 | 91.1407 | 89.3254 | 86.0722 | 83.2011 | 81.2928 | 79.9606 | 31.1455 | 30.3122 | 29.7554 | 29.1092 | 28.2861 | 27.3062 | 26.1012 | 24.8476 | 23.6031 | 22.2725 | 17.526 | 15.0284 | 14.0952 | 14.0491 | 97.5583 | 96.725 | 96.1682 | 95.522 | 94.6989 | 93.719 | 92.514 | 91.2604 | 90.0159 | 88.6853 | 83.9388 | 81.4412 | 80.508 | 80.4619 | 31.1406 | 30.2964 | 29.7395 | 29.0992 | 28.3129 | 27.4077 | 26.3369 | 25.1331 | 24.0627 | 22.9852 | 15.4096 | 0.097762 | -11.8908 | -19.9306 | 97.5534 | 96.7092 | 96.1523 | 95.512 | 94.7257 | 93.8205 | 92.7497 | 91.5459 | 90.4755 | 89.398 | 81.8224 | 66.5106 | 54.522 | 46.4822 | 31.2222 | 30.3753 | 29.8326 | 29.2839 | 28.588 | 27.6988 | 26.6441 | 25.5703 | 24.1979 | 20.647 | 3.7 | -10.1568 | -18.1881 | -16.372 | 97.635 | 96.7881 | 96.2454 | 95.6967 | 95.0008 | 94.1116 | 93.0569 | 91.9831 | 90.6107 | 87.0598 | 70.1128 | 56.256 | 48.2247 | 50.0408 | 392426 | 407533 | WHITEGATE
| Sale | 24.4899 | 23.2778 | 22.2811 | 21.0685 | 19.5731 | 17.8357 | 15.97 | 14.0363 | 12.0289 | 9.7066 | 1.5735 | -2.7444 | -3.982 | -3.594 | 36.4899 | 35.2778 | 34.2811 | 33.0685 | 31.5731 | 29.8357 | 27.97 | 26.0363 | 24.0289 | 21.7066 | 13.5735 | 9.2556 | 8.018 | 8.406 | 24.8708 | 23.9981 | 22.8409 | 21.7024 | 20.3674 | 18.8587 | 17.217 | 15.4991 | 13.6995 | 11.8475 | 6.0534 | 1.716 | -0.92287 | -2.6209 | 36.8708 | 35.9981 | 34.8409 | 33.7024 | 32.3674 | 30.8587 | 29.217 | 27.4991 | 25.6995 | 23.8475 | 18.0534 | 13.716 | 11.0771 | 9.3791 | 24.5675 | 23.4634 | 22.5743 | 21.4265 | 19.9527 | 18.2806 | 16.4896 | 14.5756 | 12.6106 | 10.5055 | 3.1631 | -0.45644 | -1.4031 | -0.80731 | 36.5675 | 35.4634 | 34.5743 | 33.4265 | 31.9527 | 30.2806 | 28.4896 | 26.5756 | 24.6106 | 22.5055 | 15.1631 | 11.5436 | 10.5969 | 11.1927 | 24.5106 | 23.3286 | 22.3874 | 21.2134 | 19.8163 | 18.2194 | 16.3687 | 14.4584 | 12.768 | 11.0684 | 1.184 | -17.8821 | -32.1159 | -41.8829 | 36.5106 | 35.3286 | 34.3874 | 33.2134 | 31.8163 | 30.2194 | 28.3687 | 26.4584 | 24.768 | 23.0684 | 13.184 | -5.8821 | -20.1159 | -29.8829 | 24.5007 | 23.1951 | 22.2898 | 21.2847 | 19.9964 | 18.5892 | 16.9924 | 15.3866 | 13.6121 | 8.9771 | -12.7031 | -29.8187 | -39.2984 | -36.5083 | 36.5007 | 35.1951 | 34.2898 | 33.2847 | 31.9964 | 30.5892 | 28.9924 | 27.3866 | 25.6121 | 20.9771 | -0.70306 | -17.8187 | -27.2984 | -24.5083 | 378726 | 392892 | CARRINGTON
| Skelmersdale | 55.4219 | 54.1387 | 53.5235 | 52.6934 | 51.6234 | 50.1137 | 48.7674 | 47.396 | 45.9828 | 44.1681 | 37.2139 | 32.3503 | 28.9386 | 26.6062 | 73.4219 | 72.1387 | 71.5235 | 70.6934 | 69.6234 | 68.1137 | 66.7674 | 65.396 | 63.9828 | 62.1681 | 55.2139 | 50.3503 | 46.9386 | 44.6062 | 56.2936 | 55.7268 | 54.8358 | 53.9759 | 52.9421 | 51.7701 | 50.4667 | 49.1146 | 47.7202 | 46.2864 | 41.9113 | 37.6025 | 34.147 | 31.7245 | 74.2936 | 73.7268 | 72.8358 | 71.9759 | 70.9421 | 69.7701 | 68.4667 | 67.1146 | 65.7202 | 64.2864 | 59.9113 | 55.6025 | 52.147 | 49.7245 | 55.4773 | 54.2683 | 53.7299 | 52.9607 | 51.9576 | 50.5131 | 49.2303 | 47.9214 | 46.6006 | 44.9828 | 38.9512 | 35.3104 | 33.1674 | 32.0041 | 73.4773 | 72.2683 | 71.7299 | 70.9607 | 69.9576 | 68.5131 | 67.2303 | 65.9214 | 64.6006 | 62.9828 | 56.9512 | 53.3104 | 51.1674 | 50.0041 | 55.4543 | 54.1577 | 53.516 | 52.6349 | 51.4864 | 49.8093 | 48.1152 | 46.3478 | 44.7183 | 43.0545 | 32.3184 | 14.6644 | 1.3078 | -8.2278 | 73.4543 | 72.1577 | 71.516 | 70.6349 | 69.4864 | 67.8093 | 66.1152 | 64.3478 | 62.7183 | 61.0545 | 50.3184 | 32.6644 | 19.3078 | 9.7722 | 55.4723 | 54.1258 | 53.4991 | 52.6736 | 51.5174 | 49.8889 | 48.2858 | 46.6242 | 44.8184 | 40.6488 | 20.822 | 4.4931 | -5.0404 | -3.6544 | 73.4723 | 72.1258 | 71.4991 | 70.6736 | 69.5174 | 67.8889 | 66.2858 | 64.6242 | 62.8184 | 58.6488 | 38.822 | 22.4931 | 12.9596 | 14.3456 | 347172 | 407455 | WASHWAY FARM
| Spadeadam 11/33kV | 4.6682 | 4.558 | 4.4499 | 4.3205 | 4.1773 | 4.0164 | 3.8241 | 3.6241 | 3.4075 | 3.1375 | 2.178 | 1.7514 | 1.6377 | 1.8312 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7025 | 4.6193 | 4.4895 | 4.3651 | 4.2274 | 4.0684 | 3.8692 | 3.6037 | 3.313 | 2.9987 | 2.5503 | 2.2571 | 1.8892 | 1.6312 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.673 | 4.5678 | 4.4651 | 4.3413 | 4.2048 | 4.0513 | 3.8667 | 3.6742 | 3.4683 | 3.2199 | 2.3543 | 1.9426 | 1.8283 | 2.0491 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6728 | 4.5613 | 4.4565 | 4.3333 | 4.1909 | 4.0236 | 3.8126 | 3.6065 | 3.4141 | 3.2291 | 2.4223 | 1.7408 | 1.4425 | 1.3026 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6484 | 4.5094 | 4.4051 | 4.2906 | 4.1262 | 3.9536 | 3.7589 | 3.5785 | 3.4124 | 3.2054 | 2.3479 | 2.0517 | 2.0461 | 2.1298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 361282 | 570359 | HARKER
| Spadeadam 132/11kV | 25.9801 | 25.8063 | 25.8812 | 25.9017 | 25.889 | 25.8468 | 25.8075 | 25.7773 | 25.7564 | 25.738 | 25.7354 | 25.8335 | 26.0094 | 26.2416 | 32.9801 | 32.8063 | 32.8812 | 32.9017 | 32.889 | 32.8468 | 32.8075 | 32.7773 | 32.7564 | 32.738 | 32.7354 | 32.8335 | 33.0094 | 33.2416 | 26.2539 | 26.2994 | 26.2801 | 26.2306 | 26.1716 | 26.1109 | 26.0447 | 25.9834 | 25.9262 | 25.8751 | 25.7958 | 25.7825 | 25.8688 | 26.0636 | 33.2539 | 33.2994 | 33.2801 | 33.2306 | 33.1716 | 33.1109 | 33.0447 | 32.9834 | 32.9262 | 32.8751 | 32.7958 | 32.7825 | 32.8688 | 33.0636 | 25.9807 | 25.8075 | 25.8831 | 25.9042 | 25.8923 | 25.851 | 25.8126 | 25.7833 | 25.7636 | 25.7475 | 25.7498 | 25.8501 | 26.0258 | 26.2565 | 32.9807 | 32.8075 | 32.8831 | 32.9042 | 32.8923 | 32.851 | 32.8126 | 32.7833 | 32.7636 | 32.7475 | 32.7498 | 32.8501 | 33.0258 | 33.2565 | 26.0045 | 25.8588 | 25.9625 | 26.0127 | 26.0312 | 26.0274 | 26.0279 | 26.0388 | 26.0606 | 26.0834 | 26.2126 | 26.3805 | 26.628 | 26.9412 | 33.0045 | 32.8588 | 32.9625 | 33.0127 | 33.0312 | 33.0274 | 33.0279 | 33.0388 | 33.0606 | 33.0834 | 33.2126 | 33.3805 | 33.628 | 33.9412 | 26.0027 | 25.8546 | 25.9585 | 26.0103 | 26.0307 | 26.0298 | 26.033 | 26.0475 | 26.072 | 26.0846 | 26.1674 | 26.3474 | 26.6145 | 26.9786 | 33.0027 | 32.8546 | 32.9585 | 33.0103 | 33.0307 | 33.0298 | 33.033 | 33.0475 | 33.072 | 33.0846 | 33.1674 | 33.3474 | 33.6145 | 33.9786 | 361282 | 570359 | HARKER
| Stainburn & Siddick | 42.9286 | 39.9058 | 38.2151 | 36.1256 | 33.5317 | 30.6463 | 27.5147 | 24.3261 | 21.1852 | 17.2252 | -3.9983 | -11.4309 | -13.3446 | -10.7847 | 87.0286 | 84.0058 | 82.3151 | 80.2256 | 77.6317 | 74.7463 | 71.6147 | 68.4261 | 65.2852 | 61.3252 | 40.1017 | 32.6691 | 30.7554 | 33.3153 | 44.9989 | 43.7357 | 41.5751 | 39.6065 | 37.3139 | 34.82 | 32.0471 | 29.1641 | 26.1973 | 23.1898 | 14.3425 | 7.3736 | 3.3405 | 1.476 | 89.0989 | 87.8357 | 85.6751 | 83.7065 | 81.4139 | 78.92 | 76.1471 | 73.2641 | 70.2973 | 67.2898 | 58.4425 | 51.4736 | 47.4405 | 45.576 | 42.9729 | 40.0232 | 38.4163 | 36.4295 | 33.951 | 31.1892 | 28.1842 | 25.1217 | 22.1407 | 18.5592 | -1.2482 | -7.322 | -8.6396 | -5.7262 | 87.0729 | 84.1232 | 82.5163 | 80.5295 | 78.051 | 75.2892 | 72.2842 | 69.2217 | 66.2407 | 62.6592 | 42.8518 | 36.778 | 35.4604 | 38.3738 | 43.0352 | 40.0022 | 38.3034 | 36.2895 | 33.7514 | 30.8717 | 27.5716 | 24.1997 | 21.2735 | 17.0987 | -7.5406 | -33.7859 | -49.6287 | -59.7933 | 87.1352 | 84.1022 | 82.4034 | 80.3895 | 77.8514 | 74.9717 | 71.6716 | 68.2997 | 65.3735 | 61.1987 | 36.5594 | 10.3141 | -5.5287 | -15.6933 | 42.8973 | 39.4844 | 37.5612 | 35.407 | 32.7522 | 26.2428 | 22.0685 | 18.2799 | 15.7112 | 9.2864 | -22.8871 | -44.2981 | -54.1504 | -48.2017 | 86.9973 | 83.5844 | 81.6612 | 79.507 | 76.8522 | 70.3428 | 66.1685 | 62.3799 | 59.8112 | 53.3864 | 21.2129 | -0.19807 | -10.0504 | -4.1017 | 302535 | 529330 | HARKER
| Stretford | 38.1009 | 34.4974 | 33.1939 | 32.4936 | 30.8297 | 29.7136 | 28.5628 | 27.3583 | 25.9617 | 24.4143 | 12.4265 | 0.28427 | -5.5362 | -8.4975 | 69.6009 | 65.9974 | 64.6939 | 63.9936 | 62.3297 | 61.2136 | 60.0628 | 58.8583 | 57.4617 | 55.9143 | 43.9265 | 31.7843 | 25.9638 | 23.0025 | 40.4176 | 38.9163 | 37.6192 | 36.6824 | 35.6468 | 34.5159 | 33.3056 | 32.0627 | 30.787 | 29.5014 | 25.2375 | 20.8281 | 17.0229 | 14.2102 | 71.9176 | 70.4163 | 69.1192 | 68.1824 | 67.1468 | 66.0159 | 64.8056 | 63.5627 | 62.287 | 61.0014 | 56.7375 | 52.3281 | 48.5229 | 45.7102 | 38.1301 | 34.5682 | 33.3076 | 32.642 | 31.0193 | 29.9454 | 28.7562 | 27.4135 | 26.0682 | 24.6456 | 13.5327 | 3.2401 | -1.6738 | -3.126 | 69.6301 | 66.0682 | 64.8076 | 64.142 | 62.5193 | 61.4454 | 60.2562 | 58.9135 | 57.5682 | 56.1456 | 45.0327 | 34.7401 | 29.8262 | 28.374 | 38.1672 | 34.6232 | 29.7975 | 25.5514 | 23.9067 | 22.7031 | 21.3257 | 19.8128 | 18.0708 | 16.254 | -8.0632 | -31.2267 | -45.0626 | -53.617 | 69.6672 | 66.1232 | 61.2975 | 57.0514 | 55.4067 | 54.2031 | 52.8257 | 51.3128 | 49.5708 | 47.754 | 23.4368 | 0.27329 | -13.5626 | -22.117 | 38.1341 | 34.4899 | 29.6293 | 25.3945 | 23.7272 | 22.4845 | 20.9836 | 18.7625 | 15.0528 | 4.6379 | -23.0817 | -39.3703 | -49.9031 | -47.8136 | 69.6341 | 65.9899 | 61.1293 | 56.8945 | 55.2272 | 53.9845 | 52.4836 | 50.2625 | 46.5528 | 36.1379 | 8.4183 | -7.8703 | -18.4031 | -16.3136 | 380069 | 395104 | SOUTH MANCHESTER
| Stuart St | 122.8306 | 117.6015 | 90.6122 | 77.7601 | 60.5272 | 40.8943 | 21.1574 | 16.6269 | 12.1187 | 8.5338 | 1.3811 | -4.4632 | -7.0933 | -8.0846 | 50.8306 | 45.6015 | 18.6122 | 5.7601 | -11.4728 | -31.1057 | -50.8426 | -55.3731 | -59.8813 | -63.4662 | -70.6189 | -76.4632 | -79.0933 | -80.0846 | 126.4564 | 124.4852 | 98.1772 | 84.7209 | 67.0907 | 47.3079 | 27.313 | 22.4527 | 17.5482 | 14.6066 | 9.1282 | 4.6878 | 1.8858 | 0.54658 | 54.4564 | 52.4852 | 26.1772 | 12.7209 | -4.9093 | -24.6921 | -44.687 | -49.5473 | -54.4518 | -57.3934 | -62.8718 | -67.3122 | -70.1142 | -71.4534 | 122.8788 | 117.7101 | 90.9681 | 78.1773 | 61.0147 | 41.4531 | 21.7887 | 17.3361 | 12.9275 | 9.5237 | 3.1075 | -1.6664 | -3.7596 | -4.1022 | 50.8788 | 45.7101 | 18.9681 | 6.1773 | -10.9853 | -30.5469 | -50.2113 | -54.6639 | -59.0725 | -62.4763 | -68.8925 | -73.6664 | -75.7596 | -76.1022 | 122.9313 | 117.7898 | 90.9747 | 78.1904 | 60.9924 | 41.327 | 21.4228 | 16.6691 | 12.0118 | 9.3644 | -0.093261 | -16.7418 | -28.9566 | -37.7527 | 50.9313 | 45.7898 | 18.9747 | 6.1904 | -11.0076 | -30.673 | -50.5772 | -55.3309 | -59.9882 | -62.6356 | -72.0933 | -88.7418 | -100.9566 | -109.7527 | 122.9407 | 117.7472 | 90.9671 | 78.2469 | 61.0835 | 41.4918 | 21.6776 | 17.0299 | 12.342 | 7.2768 | -11.9729 | -27.1598 | -35.9779 | -33.2798 | 50.9407 | 45.7472 | 18.9671 | 6.2469 | -10.9165 | -30.5082 | -50.3224 | -54.9701 | -59.658 | -64.7232 | -83.9729 | -99.1598 | -107.9779 | -105.2798 | 387247 | 398875 | STALYBRIDGE
| Thornton | 13.7264 | 12.7209 | 12.2341 | 11.5882 | 10.334 | 8.8762 | 7.2508 | 5.5909 | 3.9543 | 2.0805 | -6.1232 | -11.8581 | -13.0929 | -12.1038 | 28.7264 | 27.7209 | 27.2341 | 26.5882 | 25.334 | 23.8762 | 22.2508 | 20.5909 | 18.9543 | 17.0805 | 8.8768 | 3.1419 | 1.9071 | 2.8962 | 14.2928 | 13.7247 | 12.8788 | 11.9448 | 10.9209 | 9.7867 | 8.5087 | 6.5696 | 4.3691 | 2.0236 | -1.5322 | -4.9916 | -7.6957 | -9.6255 | 29.2928 | 28.7247 | 27.8788 | 26.9448 | 25.9209 | 24.7867 | 23.5087 | 21.5696 | 19.3691 | 17.0236 | 13.4678 | 10.0084 | 7.3043 | 5.3745 | 13.7762 | 12.8229 | 12.388 | 11.3469 | 10.0685 | 8.6516 | 7.067 | 5.4461 | 3.8729 | 2.1487 | -5.0614 | -10.2381 | -11.2687 | -10.2782 | 28.7762 | 27.8229 | 27.388 | 26.3469 | 25.0685 | 23.6516 | 22.067 | 20.4461 | 18.8729 | 17.1487 | 9.9386 | 4.7619 | 3.7313 | 4.7218 | 13.7827 | 12.8453 | 12.4401 | 11.8707 | 10.9345 | 9.6932 | 7.8689 | 5.9636 | 4.2894 | -5.9203 | -15.6697 | -31.4992 | -41.7864 | -49.4618 | 28.7827 | 27.8453 | 27.4401 | 26.8707 | 25.9345 | 24.6932 | 22.8689 | 20.9636 | 19.2894 | 9.0797 | -0.66973 | -16.4992 | -26.7864 | -34.4618 | 13.7745 | 12.7867 | 12.4277 | 11.7449 | 10.7157 | 9.667 | 8.2708 | 6.6888 | 5.004 | 1.2214 | -23.9752 | -36.4501 | -43.2724 | -42.0578 | 28.7745 | 27.7867 | 27.4277 | 26.7449 | 25.7157 | 24.667 | 23.2708 | 21.6888 | 20.004 | 16.2214 | -8.9752 | -21.4501 | -28.2724 | -27.0578 | 334559 | 443368 | STANAH
| Trimpell | 20.0617 | 19.9596 | 19.9288 | 19.8892 | 19.8343 | 19.7644 | 19.6902 | 19.6158 | 19.5395 | 19.4484 | 18.9337 | 18.1607 | 17.5224 | 16.8341 | 20.0467 | 19.9446 | 19.9138 | 19.8742 | 19.8193 | 19.7494 | 19.6752 | 19.6008 | 19.5245 | 19.4334 | 18.9187 | 18.1457 | 17.5074 | 16.8191 | 20.144 | 20.11 | 20.0591 | 20.0044 | 19.9413 | 19.8699 | 19.7919 | 19.7121 | 19.6303 | 19.5471 | 19.1941 | 18.7578 | 18.2423 | 17.7786 | 20.129 | 20.095 | 20.0441 | 19.9894 | 19.9263 | 19.8549 | 19.7769 | 19.6971 | 19.6153 | 19.5321 | 19.1791 | 18.7428 | 18.2273 | 17.7636 | 20.0629 | 19.9638 | 19.9358 | 19.8976 | 19.8444 | 19.7764 | 19.7041 | 19.6316 | 19.5586 | 19.4747 | 19.0396 | 18.6119 | 18.1371 | 17.7567 | 20.0479 | 19.9488 | 19.9208 | 19.8826 | 19.8294 | 19.7614 | 19.6891 | 19.6166 | 19.5436 | 19.4597 | 19.0246 | 18.5969 | 18.1221 | 17.7417 | 20.0644 | 19.9652 | 19.9378 | 19.9004 | 19.8488 | 19.7725 | 19.6774 | 19.5751 | 19.4713 | 19.3634 | 18.2464 | 16.453 | 15.0371 | 14.1682 | 20.0494 | 19.9502 | 19.9228 | 19.8854 | 19.8338 | 19.7575 | 19.6624 | 19.5601 | 19.4563 | 19.3484 | 18.2314 | 16.438 | 15.0221 | 14.1532 | 20.064 | 19.9606 | 19.9297 | 19.8882 | 19.8261 | 19.7325 | 19.6148 | 19.4811 | 19.3196 | 19.0053 | 17.221 | 15.3764 | 14.3438 | 14.2874 | 20.049 | 19.9456 | 19.9147 | 19.8732 | 19.8111 | 19.7175 | 19.5998 | 19.4661 | 19.3046 | 18.9903 | 17.206 | 15.3614 | 14.3288 | 14.2724 | 341861 | 458979 | HEYSHAM
| Ulverston | 60.304 | 58.5368 | 57.3941 | 56.2261 | 54.8754 | 53.3344 | 51.6171 | 49.8495 | 48.0723 | 45.7125 | 35.9734 | 30.2848 | 25.837 | 27.4132 | 78.304 | 76.5368 | 75.3941 | 74.2261 | 72.8754 | 71.3344 | 69.6171 | 67.8495 | 66.0723 | 63.7125 | 53.9734 | 48.2848 | 43.837 | 45.4132 | 61.1695 | 60.1795 | 58.8938 | 57.847 | 56.6522 | 55.2779 | 53.713 | 52.0745 | 50.3664 | 48.5231 | 43.9305 | 39.7657 | 36.9811 | 35.4155 | 79.1695 | 78.1795 | 76.8938 | 75.847 | 74.6522 | 73.2779 | 71.713 | 70.0745 | 68.3664 | 66.5231 | 61.9305 | 57.7657 | 54.9811 | 53.4155 | 60.3381 | 58.6502 | 57.5926 | 56.5041 | 55.2318 | 53.7658 | 52.1209 | 50.4232 | 48.7545 | 46.6329 | 37.7293 | 32.6287 | 28.4545 | 29.9506 | 78.3381 | 76.6502 | 75.5926 | 74.5041 | 73.2318 | 71.7658 | 70.1209 | 68.4232 | 66.7545 | 64.6329 | 55.7293 | 50.6287 | 46.4545 | 47.9506 | 60.334 | 58.5076 | 57.3148 | 56.1204 | 54.6655 | 52.9614 | 50.9595 | 48.9031 | 47.1281 | 45.3338 | 29.6701 | 12.3639 | 1.363 | -6.1962 | 78.334 | 76.5076 | 75.3148 | 74.1204 | 72.6655 | 70.9614 | 68.9595 | 66.9031 | 65.1281 | 63.3338 | 47.6701 | 30.3639 | 19.363 | 11.8038 | 60.3487 | 58.4609 | 57.3133 | 56.2301 | 54.8355 | 53.2555 | 51.5505 | 49.0537 | 45.9196 | 38.2155 | 16.9588 | 3.0127 | -3.9013 | -0.46128 | 78.3487 | 76.4609 | 75.3133 | 74.2301 | 72.8355 | 71.2555 | 69.5505 | 67.0537 | 63.9196 | 56.2155 | 34.9588 | 21.0127 | 14.0987 | 17.5387 | 327495 | 477808 | HARKER
| Vernon Park | 37.7036 | 33.6124 | 30.8304 | 27.75 | 24.2275 | 20.5109 | 16.6163 | 11.3201 | 8.6739 | 5.6119 | -12.2671 | -18.3418 | -21.524 | -20.7637 | 55.7036 | 51.6124 | 48.8304 | 45.75 | 42.2275 | 38.5109 | 34.6163 | 29.3201 | 26.6739 | 23.6119 | 5.7329 | -0.34178 | -3.524 | -2.7637 | 38.3604 | 34.8363 | 31.8147 | 28.7691 | 25.4132 | 21.8399 | 18.0595 | 15.4866 | 12.7801 | 9.9985 | 2.3495 | -3.3829 | -7.116 | -9.6244 | 56.3604 | 52.8363 | 49.8147 | 46.7691 | 43.4132 | 39.8399 | 36.0595 | 33.4866 | 30.7801 | 27.9985 | 20.3495 | 14.6171 | 10.884 | 8.3756 | 37.7862 | 33.8358 | 31.1946 | 28.2124 | 24.8059 | 21.2036 | 17.4187 | 12.2295 | 9.7368 | 6.9868 | -9.7874 | -14.7521 | -17.4722 | -16.2759 | 55.7862 | 51.8358 | 49.1946 | 46.2124 | 42.8059 | 39.2036 | 35.4187 | 30.2295 | 27.7368 | 24.9868 | 8.2126 | 3.2479 | 0.52785 | 1.7241 | 37.7327 | 33.6764 | 30.9778 | 27.9851 | 24.609 | 21.0032 | 17.0922 | 9.9817 | 7.7925 | 5.4631 | -16.7349 | -47.5752 | -70.8044 | -86.0384 | 55.7327 | 51.6764 | 48.9778 | 45.9851 | 42.609 | 39.0032 | 35.0922 | 27.9817 | 25.7925 | 23.4631 | 1.2651 | -29.5752 | -52.8044 | -68.0384 | 37.8307 | 33.6721 | 31.0141 | 28.2618 | 25.0788 | 17.2228 | 13.9662 | 9.4195 | 7.0095 | -3.0613 | -39.4748 | -67.157 | -82.4146 | -76.9126 | 55.8307 | 51.6721 | 49.0141 | 46.2618 | 43.0788 | 35.2228 | 31.9662 | 27.4195 | 25.0095 | 14.9387 | -21.4748 | -49.157 | -64.4146 | -58.9126 | 391131 | 390929 | BREDBURY
| West Didsbury | 23.9034 | 21.0171 | 18.8314 | 16.372 | 13.2745 | 9.8525 | 6.2145 | 2.5129 | -1.2374 | -5.4958 | -20.5676 | -28.3933 | -30.2222 | -29.4586 | 61.9034 | 59.0171 | 56.8314 | 54.372 | 51.2745 | 47.8525 | 44.2145 | 40.5129 | 36.7626 | 32.5042 | 17.4324 | 9.6067 | 7.7778 | 8.5414 | 25.1806 | 23.408 | 20.8278 | 18.5293 | 15.7587 | 12.6518 | 9.2625 | 5.7624 | 2.1403 | -1.5562 | -13.0139 | -21.1397 | -25.4755 | -28.0081 | 63.1806 | 61.408 | 58.8278 | 56.5293 | 53.7587 | 50.6518 | 47.2625 | 43.7624 | 40.1403 | 36.4438 | 24.9861 | 16.8603 | 12.5245 | 9.9919 | 24.008 | 21.2905 | 19.2779 | 16.9498 | 14.0189 | 10.7645 | 7.2912 | 3.7507 | 0.22242 | -3.5972 | -17.1459 | -23.8306 | -25.1445 | -24.0256 | 62.008 | 59.2905 | 57.2779 | 54.9498 | 52.0189 | 48.7645 | 45.2912 | 41.7507 | 38.2224 | 34.4028 | 20.8541 | 14.1694 | 12.8555 | 13.9744 | 23.9789 | 21.1422 | 19.0272 | 16.595 | 13.6255 | 10.2658 | 6.5086 | 2.6866 | -0.70482 | -4.1433 | -23.0102 | -57.2991 | -81.8376 | -98.3907 | 61.9789 | 59.1422 | 57.0272 | 54.595 | 51.6255 | 48.2658 | 44.5086 | 40.6866 | 37.2952 | 33.8567 | 14.9898 | -19.2991 | -43.8376 | -60.3907 | 23.7986 | 20.5968 | 18.4871 | 16.2802 | 13.5358 | 10.5872 | 7.2907 | 4.0421 | 0.64318 | -8.0882 | -48.614 | -79.0466 | -95.109 | -89.0906 | 61.7986 | 58.5968 | 56.4871 | 54.2802 | 51.5358 | 48.5872 | 45.2907 | 42.0421 | 38.6432 | 29.9118 | -10.614 | -41.0466 | -57.109 | -51.0906 | 382900 | 393269 | SOUTH MANCHESTER
| Westhoughton | 57.0407 | 55.1023 | 53.6684 | 52.2354 | 50.4874 | 48.5325 | 46.3847 | 44.1731 | 42.0034 | 39.4931 | 30.0593 | 24.7908 | 23.2961 | 23.592 | 75.0407 | 73.1023 | 71.6684 | 70.2354 | 68.4874 | 66.5325 | 64.3847 | 62.1731 | 60.0034 | 57.4931 | 48.0593 | 42.7908 | 41.2961 | 41.592 | 58.0991 | 57.1034 | 55.6676 | 54.412 | 52.9822 | 51.3805 | 49.6137 | 47.7847 | 45.9104 | 44.0359 | 37.8821 | 33.579 | 31.0301 | 29.6356 | 76.0991 | 75.1034 | 73.6676 | 72.412 | 70.9822 | 69.3805 | 67.6137 | 65.7847 | 63.9104 | 62.0359 | 55.8821 | 51.579 | 49.0301 | 47.6356 | 57.0648 | 55.1711 | 53.7933 | 52.3987 | 50.7028 | 48.8048 | 46.7132 | 44.5612 | 42.4858 | 40.1935 | 31.6878 | 27.5137 | 26.4938 | 27.3246 | 75.0648 | 73.1711 | 71.7933 | 70.3987 | 68.7028 | 66.8048 | 64.7132 | 62.5612 | 60.4858 | 58.1935 | 49.6878 | 45.5137 | 44.4938 | 45.3246 | 57.1079 | 55.2322 | 53.8891 | 52.6068 | 51.0591 | 49.2906 | 47.2622 | 45.1734 | 43.3505 | 41.5079 | 30.141 | 10.8569 | -2.6688 | -11.8675 | 75.1079 | 73.2322 | 71.8891 | 70.6068 | 69.0591 | 67.2906 | 65.2622 | 63.1734 | 61.3505 | 59.5079 | 48.141 | 28.8569 | 15.3312 | 6.1325 | 56.9362 | 54.7567 | 53.3912 | 52.2263 | 50.8031 | 49.2415 | 47.4131 | 45.6046 | 43.6438 | 39.1437 | 17.4436 | 0.51151 | -8.7788 | -5.424 | 74.9362 | 72.7567 | 71.3912 | 70.2263 | 68.8031 | 67.2415 | 65.4131 | 63.6046 | 61.6438 | 57.1437 | 35.4436 | 18.5115 | 9.2212 | 12.576 | 365831 | 407025 | KEARSLEY
| Wigan | 7.1301 | 5.6249 | 4.6119 | 2.5595 | 0.11829 | -3.6725 | -7.7587 | 1.8655 | -1.6448 | -5.0542 | -14.2761 | -19.204 | -20.523 | -20.0498 | 70.1301 | 68.6249 | 67.6119 | 65.5595 | 63.1183 | 59.3275 | 55.2413 | 51.8655 | 48.3552 | 44.9458 | 35.7239 | 30.796 | 29.477 | 29.9502 | 7.9329 | 7.061 | 5.5976 | 3.8859 | 1.947 | -0.44191 | -3.0434 | 7.416 | 4.7763 | 2.1648 | -4.0725 | -8.3316 | -10.6379 | -11.8724 | 70.9329 | 70.061 | 68.5976 | 66.8859 | 64.947 | 62.5581 | 59.9566 | 57.416 | 54.7763 | 52.1648 | 45.9275 | 41.6684 | 39.3621 | 38.1276 | 7.2185 | 5.7916 | 4.826 | 2.8247 | 0.446 | -3.3544 | -7.3687 | 2.2344 | -1.1591 | -4.3153 | -12.5795 | -16.5558 | -17.4447 | -16.632 | 70.2185 | 68.7916 | 67.826 | 65.8247 | 63.446 | 59.6456 | 55.6313 | 52.2344 | 48.8409 | 45.6847 | 37.4205 | 33.4442 | 32.5553 | 33.368 | 7.1962 | 5.7839 | 4.9105 | 3.0054 | 0.6948 | -3.0255 | -6.9828 | 2.8001 | -0.19371 | -2.8231 | -14.6143 | -38.0684 | -56.3079 | -68.2955 | 70.1962 | 68.7839 | 67.9105 | 66.0054 | 63.6948 | 59.9745 | 56.0172 | 52.8001 | 49.8063 | 47.1769 | 35.3857 | 11.9316 | -6.3079 | -18.2955 | 7.2016 | 5.6382 | 4.7493 | 3.0005 | 0.80131 | -2.7344 | -6.4697 | 3.592 | 0.23842 | -6.2523 | -32.8267 | -54.0142 | -66.0098 | -62.4082 | 70.2016 | 68.6382 | 67.7493 | 66.0005 | 63.8013 | 60.2656 | 56.5303 | 53.592 | 50.2384 | 43.7477 | 17.1733 | -4.0142 | -16.0098 | -12.4082 | 358343 | 404626 | KIRKBY
| Wrightington | 24.127 | 20.2262 | 17.3937 | 14.8117 | 11.6818 | 8.2222 | 4.4677 | 0.58883 | -3.6955 | -9.1061 | -29.8244 | -41.4507 | -45.072 | -45.0535 | 42.127 | 38.2262 | 35.3937 | 32.8117 | 29.6818 | 26.2222 | 22.4677 | 18.5888 | 14.3045 | 8.8939 | -11.8244 | -23.4507 | -27.072 | -27.0535 | 25.73 | 23.3301 | 20.533 | 18.3678 | 15.7725 | 12.8773 | 9.6879 | 6.3591 | 2.906 | -0.60644 | -12.8749 | -22.7527 | -28.9484 | -32.9995 | 43.73 | 41.3301 | 38.533 | 36.3678 | 33.7725 | 30.8773 | 27.6879 | 24.3591 | 20.906 | 17.3936 | 5.1251 | -4.7527 | -10.9484 | -14.9995 | 24.185 | 20.4384 | 17.764 | 15.3243 | 12.3698 | 9.0867 | 5.5065 | 1.793 | -2.4711 | -7.3609 | -26.1978 | -35.827 | -38.5971 | -37.7855 | 42.185 | 38.4384 | 35.764 | 33.3243 | 30.3698 | 27.0867 | 23.5065 | 19.793 | 15.5289 | 10.6391 | -8.1978 | -17.827 | -20.5971 | -19.7855 | 24.2113 | 20.264 | 17.3872 | 14.8256 | 11.7677 | 8.2508 | 4.1994 | -0.027376 | -3.7294 | -7.5305 | -29.4835 | -60.0185 | -79.3606 | -95.7471 | 42.2113 | 38.264 | 35.3872 | 32.8256 | 29.7677 | 26.2508 | 22.1994 | 17.9726 | 14.2706 | 10.4695 | -11.4835 | -42.0185 | -61.3606 | -77.7471 | 24.1025 | 19.8626 | 16.9576 | 14.4676 | 11.5025 | 8.2931 | 4.6909 | 1.0901 | -2.4587 | -10.0019 | -46.2375 | -72.2812 | -85.103 | -82.9126 | 42.1025 | 37.8626 | 34.9576 | 32.4676 | 29.5025 | 26.2931 | 22.6909 | 19.0901 | 15.5413 | 7.9981 | -28.2375 | -54.2812 | -67.103 | -64.9126 | 354460 | 413610 | PENWORTHAM

## Gen Primary Headroom
Click the scenario name to move directly to the associated results | Best View
Steady Progression
System Transformation
Consumer Transformation
Leading the Way
[5 empty] | Central Outlook | [55 empty] | Steady Progression | [55 empty] | System Transformation | [55 empty] | Consumer Transformation | [55 empty] | Leading The Way
Primary Substation Headroom |  |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2036 |  |  |  | 2041 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2036 |  |  |  | 2041 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2036 |  |  |  | 2041 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2036 |  |  |  | 2041 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2036 |  |  |  | 2041 |  |  |  | 2046 |  |  |  | 2051
Primary Substation | BSP Group | GSP Group | Primary Substation Location |  | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW)
|  |  | Easting | Northing | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 31.2135 | 15.1131 | 11.0248 | 13.2438 | 31.2683 | 14.8923 | 10.8637 | 12.9946 | 31.2888 | 14.6479 | 10.6855 | 12.7491 | 31.3403 | 14.3478 | 10.4665 | 12.4519 | 31.4176 | 13.9633 | 10.186 | 12.1515 | 31.5153 | 13.7036 | 9.9966 | 11.9212 | 31.627 | 13.8102 | 10.0743 | 11.5 | 31.7495 | 13.8352 | 10.0926 | 11.1531 | 31.8821 | 13.8341 | 10.0918 | 10.8182 | 32.029 | 13.7815 | 10.0534 | 10.3422 | 32.513 | 13.5069 | 9.8531 | 8.8126 | 33.7164 | 13.7841 | 10.0553 | 7.3506 | 33.9293 | 15.61 | 11.3873 | 7.3395 | 34.0219 | 16.7476 | 12.2171 | 7.7011 | 31.1695 | 15.2111 | 11.0963 | 13.4244 | 31.1923 | 15.0537 | 10.9815 | 13.3239 | 31.2459 | 14.8528 | 10.8349 | 13.0251 | 31.3135 | 14.6107 | 10.6583 | 12.7025 | 31.3935 | 14.4085 | 10.5108 | 12.4322 | 31.4831 | 14.1937 | 10.3541 | 12.2267 | 31.5835 | 14.1202 | 10.3005 | 11.8286 | 31.6917 | 14.0524 | 10.251 | 11.5018 | 31.8083 | 13.9774 | 10.1963 | 11.1773 | 31.9316 | 13.8856 | 10.1293 | 10.7651 | 32.1672 | 13.7427 | 10.0251 | 9.7317 | 32.3429 | 14.127 | 10.3054 | 9.1195 | 32.447 | 15.718 | 11.466 | 8.754 | 32.5024 | 16.351 | 11.9278 | 8.7137 | 31.2135 | 15.2025 | 11.09 | 13.2538 | 31.2684 | 15.1626 | 11.0609 | 13.0178 | 31.2889 | 15.035 | 10.9678 | 12.7868 | 31.3404 | 14.8909 | 10.8627 | 12.5028 | 31.4174 | 14.7343 | 10.7485 | 12.2191 | 31.5145 | 14.5249 | 10.5957 | 12.0046 | 31.6256 | 14.4538 | 10.5438 | 11.6012 | 31.7479 | 14.3899 | 10.4972 | 11.2705 | 31.8786 | 14.2858 | 10.4213 | 10.9579 | 32.0181 | 14.247 | 10.393 | 10.5301 | 32.4749 | 14.0025 | 10.2146 | 9.1324 | 33.6438 | 14.3377 | 10.4592 | 7.7785 | 33.8385 | 16.5114 | 12.0448 | 7.7989 | 33.9337 | 17.6151 | 12.8499 | 8.1868 | 31.209 | 15.1131 | 11.0248 | 13.2551 | 31.2633 | 14.9121 | 10.8782 | 13.0192 | 31.2944 | 14.683 | 10.711 | 12.7948 | 31.368 | 14.4031 | 10.5069 | 12.5237 | 31.4814 | 14.0805 | 10.2715 | 12.2715 | 31.6303 | 13.8303 | 10.089 | 12.0978 | 31.8112 | 13.8785 | 10.1241 | 11.7338 | 31.9965 | 13.8849 | 10.1289 | 11.4483 | 32.1714 | 13.8505 | 10.1038 | 11.2329 | 32.3669 | 13.7589 | 10.0369 | 10.9334 | 33.6309 | 13.094 | 9.5519 | 8.2361 | 34.5092 | 12.4537 | 9.0848 | 2.767 | 34.8643 | 13.3119 | 9.7108 | -1.5092 | 35.0575 | 13.9542 | 10.1794 | -4.0935 | 31.1966 | 15.1217 | 11.0311 | 13.2924 | 31.2507 | 15.1423 | 11.0461 | 13.0588 | 31.2838 | 15.0914 | 11.009 | 12.844 | 31.3507 | 14.9565 | 10.9105 | 12.6183 | 31.5818 | 14.865 | 10.8438 | 12.29 | 31.7135 | 14.844 | 10.8285 | 12.1876 | 31.8797 | 14.7561 | 10.7644 | 11.8914 | 32.0207 | 14.6892 | 10.7156 | 11.6825 | 32.3312 | 14.5863 | 10.6405 | 11.2207 | 33.1529 | 14.2482 | 10.3939 | 9.4186 | 34.0221 | 14.6532 | 10.6893 | 3.4165 | 34.4248 | 13.5293 | 9.8695 | -1.1995 | 34.5536 | 14.7066 | 10.7283 | -3.9639 | 34.4338 | 14.5973 | 10.6485 | -2.7679
ALDERLEY & CHELFORD | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 33.6532 | 5.8911 | 4.234 | 16.9603 | 33.7943 | 5.6821 | 4.0838 | 15.7963 | 33.8207 | 5.5683 | 4.0021 | 15.3661 | 32.9959 | 5.4325 | 3.9045 | 14.8884 | 31.8637 | 5.2461 | 3.7705 | 14.3369 | 30.7517 | 5.063 | 3.6389 | 13.7004 | 29.4782 | 4.8534 | 3.4882 | 12.9241 | 28.4273 | 4.6803 | 3.3638 | 12.3825 | 24.8963 | 4.099 | 2.946 | 9.317 | 23.6887 | 3.9002 | 2.8031 | 8.608 | 18.3561 | 3.0222 | 2.1721 | 5.3846 | 17.899 | 2.9469 | 2.118 | 3.4979 | 30.6108 | 5.0398 | 3.6222 | 3.1665 | 39.9524 | 6.5779 | 4.7276 | 3.44 | 33.5725 | 5.9923 | 4.3068 | 17.5657 | 33.6467 | 5.8718 | 4.2202 | 16.9467 | 33.7567 | 5.7565 | 4.1373 | 16.4519 | 33.8717 | 5.635 | 4.05 | 15.9733 | 33.4363 | 5.505 | 3.9566 | 15.4639 | 32.6297 | 5.3722 | 3.8611 | 14.8944 | 31.6993 | 5.2191 | 3.751 | 14.1738 | 30.9812 | 5.1008 | 3.6661 | 13.6614 | 30.1775 | 4.9685 | 3.571 | 13.0389 | 29.3881 | 4.8385 | 3.4775 | 12.4243 | 27.0825 | 4.4589 | 3.2047 | 10.519 | 27.1939 | 4.4773 | 3.2179 | 9.0366 | 35.6728 | 6.264 | 4.5021 | 8.1989 | 35.8029 | 7.6537 | 5.5009 | 7.7754 | 33.6532 | 5.9893 | 4.3046 | 16.9676 | 33.7944 | 5.8592 | 4.2112 | 15.8252 | 33.8635 | 5.7217 | 4.1123 | 15.415 | 33.85 | 5.5731 | 4.0055 | 14.9539 | 32.8835 | 5.414 | 3.8912 | 14.4246 | 31.8907 | 5.2506 | 3.7737 | 13.8113 | 30.7807 | 5.0678 | 3.6423 | 13.0585 | 29.7296 | 4.8947 | 3.518 | 12.5362 | 28.5895 | 4.707 | 3.383 | 9.504 | 27.456 | 4.5204 | 3.2489 | 8.8702 | 24.3717 | 4.0126 | 2.8839 | 5.9118 | 24.6358 | 4.0561 | 2.9152 | 4.2132 | 38.8516 | 6.3966 | 4.5974 | 3.9609 | 39.9315 | 7.7521 | 5.5716 | 4.2488 | 33.648 | 5.8969 | 4.2382 | 17.0076 | 33.7931 | 5.691 | 4.0902 | 15.8939 | 33.8131 | 5.5671 | 4.0012 | 15.5222 | 32.9533 | 5.4255 | 3.8994 | 15.1031 | 31.8349 | 5.2414 | 3.7671 | 14.6213 | 30.6961 | 5.0539 | 3.6323 | 14.0563 | 29.3545 | 4.833 | 3.4736 | 13.3298 | 28.2551 | 4.652 | 3.3435 | 12.8457 | 24.7236 | 4.0706 | 2.9256 | 9.9348 | 23.5503 | 3.8774 | 2.7868 | 9.4476 | 17.3804 | 2.8615 | 2.0566 | 6.262 | 12.4233 | 2.0454 | 1.4701 | 1.4657 | 22.6759 | 3.7334 | 2.6833 | -0.47471 | 28.7371 | 4.7313 | 3.4005 | -1.6256 | 33.6635 | 5.8666 | 4.2164 | 16.8168 | 33.8348 | 5.6192 | 4.0386 | 15.5087 | 33.279 | 5.4791 | 3.938 | 15.1587 | 32.3299 | 5.3229 | 3.8257 | 14.7976 | 31.0671 | 5.115 | 3.6762 | 14.3525 | 29.8579 | 4.9159 | 3.5331 | 13.8553 | 28.5201 | 4.6956 | 3.3748 | 13.206 | 27.0942 | 4.4609 | 3.2061 | 12.2609 | 23.6451 | 3.893 | 2.798 | 9.3976 | 22.2586 | 3.6647 | 2.6339 | 8.5386 | 23.1874 | 3.8176 | 2.7438 | 2.8737 | 18.1834 | 2.9938 | 2.1517 | 0.19312 | 33.5899 | 5.5303 | 3.9747 | -0.81511 | 31.1235 | 5.1243 | 3.6829 | 0.042465
ALSTON | PENRITH & SHAP | HARKER / HUTTON | 372125 | 546499 | 2.9499 | 2.9499 | 2.9499 | 1.3038 | 2.9639 | 2.9639 | 2.9639 | 1.2154 | 2.9795 | 2.9795 | 2.9795 | 1.1695 | 2.9996 | 2.9996 | 2.9996 | 1.1362 | 3.0237 | 3.0237 | 3.0237 | 1.0632 | 3.0484 | 3.0484 | 3.0484 | 0.98846 | 3.0726 | 3.0726 | 3.0726 | 0.92169 | 3.0993 | 3.0993 | 3.0993 | 0.87999 | 3.1287 | 3.1287 | 3.1287 | 0.79903 | 3.1638 | 3.1638 | 3.1638 | 0.63883 | 3.3058 | 3.3058 | 3.3058 | -0.042412 | 3.4206 | 3.4206 | 3.4206 | -0.442 | 3.4895 | 3.4895 | 3.4895 | -0.66005 | 3.519 | 3.519 | 3.519 | -0.59816 | 2.9529 | 2.9529 | 2.9529 | 1.3481 | 2.9702 | 2.9702 | 2.9702 | 1.2985 | 2.9929 | 2.9929 | 2.9929 | 1.2434 | 3.0177 | 3.0177 | 3.0177 | 1.1702 | 3.046 | 3.046 | 3.046 | 1.116 | 3.0765 | 3.0765 | 3.0765 | 1.0355 | 3.1055 | 3.1055 | 3.1055 | 0.95084 | 3.1351 | 3.1351 | 3.1351 | 0.85696 | 3.1672 | 3.1672 | 3.1672 | 0.75346 | 3.2022 | 3.2022 | 3.2022 | 0.66548 | 3.291 | 3.291 | 3.291 | 0.45775 | 3.3631 | 3.3631 | 3.3631 | 0.014459 | 3.406 | 3.406 | 3.406 | -0.35798 | 3.4303 | 3.4303 | 3.4303 | -0.61303 | 2.9506 | 2.9506 | 2.9506 | 1.3052 | 2.9648 | 2.9648 | 2.9648 | 1.2187 | 2.9806 | 2.9806 | 2.9806 | 1.1746 | 3.0008 | 3.0008 | 3.0008 | 1.1428 | 3.0247 | 3.0247 | 3.0247 | 1.0724 | 3.0486 | 3.0486 | 3.0486 | 1.0003 | 3.0723 | 3.0723 | 3.0723 | 0.93601 | 3.0984 | 3.0984 | 3.0984 | 0.89613 | 3.1268 | 3.1268 | 3.1268 | 0.81866 | 3.1599 | 3.1599 | 3.1599 | 0.70129 | 3.2925 | 3.2925 | 3.2925 | 0.074975 | 3.3909 | 3.3909 | 3.3909 | -0.28317 | 3.4429 | 3.4429 | 3.4429 | -0.47384 | 3.4636 | 3.4636 | 3.4636 | -0.41303 | 2.951 | 2.951 | 2.951 | 1.3046 | 2.9669 | 2.9669 | 2.9669 | 1.2131 | 2.9865 | 2.9865 | 2.9865 | 1.1633 | 3.0127 | 3.0127 | 3.0127 | 1.1127 | 3.0404 | 3.0404 | 3.0404 | 1.0095 | 3.0687 | 3.0687 | 3.0687 | 0.92384 | 3.1051 | 3.1051 | 3.1051 | 0.78237 | 3.1465 | 3.1465 | 3.1465 | 0.69786 | 3.1922 | 3.1922 | 3.1922 | 0.56489 | 3.2435 | 3.2435 | 3.2435 | 0.40463 | 3.4324 | 3.4324 | 3.4324 | -0.26078 | 3.5759 | 3.5759 | 3.5759 | -1.1232 | 3.6452 | 3.6452 | 3.6452 | -1.6554 | 3.6762 | 3.6762 | 3.6762 | -2.0155 | 2.9506 | 2.9506 | 2.9506 | 1.3016 | 2.9678 | 2.9678 | 2.9678 | 1.2033 | 2.9873 | 2.9873 | 2.9873 | 1.1521 | 3.0123 | 3.0123 | 3.0123 | 1.1027 | 3.0335 | 3.0335 | 3.0335 | 0.98907 | 3.0597 | 3.0597 | 3.0597 | 0.90174 | 3.0942 | 3.0942 | 3.0942 | 0.7685 | 3.1329 | 3.1329 | 3.1329 | 0.69266 | 3.1755 | 3.1755 | 3.1755 | 0.54433 | 3.2256 | 3.2256 | 3.2256 | 0.2749 | 3.3993 | 3.3993 | 3.3993 | -0.80816 | 3.5029 | 3.5029 | 3.5029 | -1.5528 | 3.5415 | 3.5415 | 3.5415 | -1.8942 | 3.5434 | 3.5434 | 3.5434 | -1.7921
AMBLESIDE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 337602 | 503506 | 28.6006 | 25.0779 | 18.024 | 16.045 | 28.6493 | 24.9759 | 17.9507 | 15.5643 | 28.7043 | 24.8794 | 17.8813 | 15.2642 | 28.7765 | 24.7988 | 17.8234 | 15.1524 | 28.86 | 24.7101 | 17.7597 | 14.9912 | 28.9576 | 24.5783 | 17.6649 | 14.6564 | 29.0751 | 24.4535 | 17.5752 | 14.4022 | 29.2013 | 24.3623 | 17.5096 | 14.3106 | 29.294 | 24.2335 | 17.4171 | 14.0265 | 29.4203 | 24.0996 | 17.3208 | 13.7181 | 29.9558 | 23.544 | 16.9215 | 12.6275 | 30.3271 | 23.1918 | 16.6684 | 12.0324 | 30.4377 | 23.0056 | 16.5345 | 11.8268 | 30.4811 | 22.8821 | 16.4458 | 11.9809 | 28.6027 | 25.1176 | 18.0525 | 16.2356 | 28.6518 | 25.045 | 18.0003 | 15.8773 | 28.7148 | 24.9622 | 17.9408 | 15.5614 | 28.7708 | 24.8863 | 17.8863 | 15.351 | 28.8364 | 24.8078 | 17.8299 | 15.0984 | 28.9132 | 24.6877 | 17.7435 | 14.6708 | 29.0037 | 24.5815 | 17.6672 | 14.3069 | 29.1008 | 24.5017 | 17.6099 | 14.0863 | 29.2051 | 24.3849 | 17.5259 | 13.6378 | 29.3154 | 24.2501 | 17.429 | 13.163 | 29.5889 | 24.0606 | 17.2928 | 12.7081 | 29.8169 | 23.8772 | 17.161 | 12.3748 | 29.987 | 23.7687 | 17.083 | 12.2398 | 30.1062 | 23.6744 | 17.0152 | 12.1212 | 28.6014 | 25.117 | 18.0521 | 16.0823 | 28.6503 | 25.0414 | 17.9977 | 15.611 | 28.7055 | 24.9414 | 17.9259 | 15.4118 | 28.7778 | 24.8404 | 17.8532 | 15.1963 | 28.8609 | 24.7359 | 17.7782 | 15.0956 | 28.9576 | 24.5892 | 17.6728 | 14.8304 | 29.0738 | 24.4542 | 17.5757 | 14.5328 | 29.1985 | 24.3454 | 17.4975 | 14.4031 | 29.2912 | 24.1983 | 17.3918 | 14.1075 | 29.4131 | 24.034 | 17.2737 | 13.8283 | 29.9251 | 23.6575 | 17.0031 | 12.8282 | 30.2679 | 23.3684 | 16.7953 | 12.3011 | 30.3562 | 23.1476 | 16.6366 | 12.1296 | 30.3883 | 22.9006 | 16.4591 | 12.2882 | 28.6019 | 25.079 | 18.0248 | 16.0587 | 28.6617 | 24.9424 | 17.9266 | 15.589 | 28.7374 | 24.8418 | 17.8543 | 15.3341 | 28.8353 | 24.7443 | 17.7842 | 15.1946 | 28.9602 | 24.6505 | 17.7168 | 15.0718 | 29.1194 | 24.5108 | 17.6164 | 14.7685 | 29.2755 | 24.3603 | 17.5082 | 14.4473 | 29.435 | 24.2421 | 17.4233 | 14.2859 | 29.5966 | 24.096 | 17.3183 | 13.9809 | 29.776 | 23.9625 | 17.2223 | 13.7471 | 30.3161 | 23.2801 | 16.7319 | 12.4909 | 30.5785 | 22.4322 | 16.1225 | 9.9376 | 30.6971 | 21.8219 | 15.6838 | 8.0154 | 30.7316 | 21.3521 | 15.3462 | 6.673 | 28.6141 | 25.0736 | 18.0209 | 16.0317 | 28.6881 | 24.972 | 17.9479 | 15.5618 | 28.7635 | 24.859 | 17.8667 | 15.3322 | 28.8612 | 24.7447 | 17.7845 | 15.2097 | 28.9871 | 24.6357 | 17.7062 | 15.1168 | 29.1261 | 24.4769 | 17.592 | 14.868 | 29.2614 | 24.3187 | 17.4783 | 14.5839 | 29.408 | 24.1984 | 17.3919 | 14.4828 | 29.564 | 24.0514 | 17.2862 | 14.2199 | 29.8173 | 23.8272 | 17.1251 | 13.6055 | 30.1503 | 22.7959 | 16.3838 | 10.7125 | 30.334 | 21.8814 | 15.7266 | 8.4595 | 30.3711 | 21.4348 | 15.4056 | 7.1148 | 30.3088 | 21.3327 | 15.3322 | 7.4966
ANCOATS NORTH T11 & T12 | RED BANK | WHITEGATE | 385022 | 398830 | 32.837 | 6.6898 | 4.8801 | 10.2181 | 32.9588 | 6.4854 | 4.731 | 9.1942 | 32.9589 | 6.3432 | 4.6273 | 8.7941 | 32.9994 | 6.2327 | 4.5467 | 8.5776 | 33.0619 | 6.1071 | 4.455 | 8.3792 | 33.1495 | 5.9588 | 4.3469 | 8.1372 | 33.2365 | 5.8636 | 4.2774 | 7.8931 | 33.3233 | 5.7734 | 4.2116 | 7.6401 | 33.4106 | 5.6709 | 4.1369 | 7.3266 | 33.5055 | 5.5885 | 4.0767 | 7.0526 | 31.1214 | 5.0482 | 3.6826 | 5.9138 | 28.9408 | 4.6945 | 3.4246 | 4.9923 | 28.1144 | 4.5604 | 3.3268 | 4.4641 | 27.5109 | 4.4625 | 3.2554 | 4.2187 | 32.7135 | 6.7437 | 4.9194 | 10.7172 | 32.7411 | 6.6203 | 4.8294 | 10.1691 | 32.8101 | 6.5125 | 4.7507 | 9.7963 | 32.9081 | 6.4176 | 4.6816 | 9.5194 | 33.0189 | 6.3071 | 4.6009 | 9.2415 | 33.1407 | 6.2042 | 4.5259 | 8.908 | 33.2727 | 6.1176 | 4.4627 | 8.5796 | 33.4121 | 6.0091 | 4.3835 | 8.1628 | 33.5597 | 5.851 | 4.2683 | 7.4849 | 33.7162 | 5.6843 | 4.1466 | 6.776 | 33.7861 | 5.4804 | 3.9979 | 6.135 | 32.815 | 5.3229 | 3.883 | 5.7101 | 32.7658 | 5.3149 | 3.8772 | 5.3253 | 33.2486 | 5.3932 | 3.9343 | 4.9652 | 32.8371 | 6.7427 | 4.9187 | 10.2306 | 32.9591 | 6.6289 | 4.8357 | 9.2241 | 32.9595 | 6.5024 | 4.7434 | 8.8462 | 33.0004 | 6.3575 | 4.6377 | 8.6668 | 33.0631 | 6.2409 | 4.5527 | 8.512 | 33.1509 | 6.0869 | 4.4403 | 8.2933 | 33.2382 | 5.9818 | 4.3637 | 8.1068 | 33.3252 | 5.8526 | 4.2694 | 7.8683 | 33.4123 | 5.668 | 4.1347 | 7.6129 | 33.5051 | 5.4893 | 4.0044 | 7.3389 | 31.4419 | 5.1002 | 3.7205 | 6.1937 | 30.1759 | 4.8948 | 3.5707 | 5.4039 | 30.3024 | 4.9153 | 3.5857 | 4.9395 | 29.9219 | 4.8536 | 3.5406 | 4.762 | 32.8261 | 6.6919 | 4.8816 | 10.2288 | 32.9388 | 6.4941 | 4.7373 | 9.2109 | 32.9276 | 6.34 | 4.625 | 8.8224 | 32.9635 | 6.2174 | 4.5355 | 8.6192 | 33.0246 | 6.0927 | 4.4446 | 8.4162 | 33.1195 | 5.9375 | 4.3313 | 8.1573 | 33.2259 | 5.8264 | 4.2503 | 7.8769 | 33.3409 | 5.7163 | 4.1699 | 7.5715 | 33.4619 | 5.622 | 4.1012 | 7.2342 | 33.5921 | 5.5098 | 4.0193 | 6.9125 | 29.3924 | 4.7677 | 3.478 | 5.2833 | 23.711 | 3.8462 | 2.8057 | 2.1191 | 19.8747 | 3.2239 | 2.3518 | -0.42596 | 17.2715 | 2.8016 | 2.0437 | -2.2745 | 32.8144 | 6.6962 | 4.8848 | 10.242 | 32.9189 | 6.5301 | 4.7636 | 9.2306 | 32.8997 | 6.4104 | 4.6763 | 8.8719 | 32.9215 | 6.3018 | 4.597 | 8.7094 | 32.9693 | 6.144 | 4.482 | 8.5429 | 33.0539 | 6.0099 | 4.3841 | 8.3293 | 33.1553 | 5.9173 | 4.3166 | 8.0918 | 33.2674 | 5.7752 | 4.2129 | 7.7987 | 33.3895 | 5.6603 | 4.1291 | 7.4595 | 33.4604 | 5.4276 | 3.9594 | 6.7838 | 26.0981 | 4.2334 | 3.0882 | 3.1949 | 19.1831 | 3.1117 | 2.2699 | 0.18409 | 17.7537 | 2.8798 | 2.1008 | -1.5234 | 16.9045 | 2.7421 | 2.0003 | -1.2326
ANCOATS NORTH T14 | RED BANK | WHITEGATE | 385032 | 398840 | 19.6766 | 19.6766 | 15.6988 | 7.0565 | 19.7271 | 19.7271 | 15.641 | 6.7682 | 19.7431 | 19.7431 | 15.5841 | 6.7029 | 19.7695 | 19.7695 | 15.5149 | 6.6718 | 19.7988 | 19.7988 | 15.4838 | 6.5172 | 19.8335 | 19.8335 | 15.4437 | 6.3744 | 19.8683 | 19.8683 | 15.401 | 6.2183 | 19.9035 | 19.9035 | 15.3612 | 6.1443 | 19.9389 | 19.9389 | 15.3111 | 5.9624 | 19.9776 | 19.9776 | 15.2709 | 5.8283 | 20.1305 | 20.1305 | 15.0811 | 5.4647 | 20.3194 | 20.3194 | 14.9466 | 5.1964 | 20.4674 | 20.3586 | 14.8513 | 5.0762 | 20.6228 | 20.2879 | 14.7998 | 5.022 | 19.652 | 19.652 | 15.7249 | 7.2635 | 19.6859 | 19.6859 | 15.6958 | 7.1376 | 19.7343 | 19.7343 | 15.6532 | 6.9412 | 19.7851 | 19.7851 | 15.6088 | 6.7902 | 19.842 | 19.842 | 15.5545 | 6.5272 | 19.9056 | 19.9056 | 15.4968 | 6.2899 | 19.9758 | 19.9758 | 15.4429 | 5.9626 | 20.0526 | 20.0526 | 15.3711 | 5.5051 | 20.1364 | 20.1364 | 15.2826 | 4.9755 | 20.2282 | 20.2282 | 15.1987 | 4.4192 | 20.3438 | 20.3438 | 15.1426 | 4.1349 | 20.4666 | 20.4666 | 15.0998 | 3.957 | 20.5869 | 20.5869 | 15.073 | 3.8323 | 20.6859 | 20.6279 | 15.0478 | 3.7928 | 19.6767 | 19.6767 | 15.7247 | 7.0689 | 19.7273 | 19.7273 | 15.6879 | 6.7942 | 19.7435 | 19.7435 | 15.6208 | 6.7433 | 19.77 | 19.77 | 15.5598 | 6.7245 | 19.7996 | 19.7996 | 15.4738 | 6.5863 | 19.8345 | 19.8345 | 15.4309 | 6.4591 | 19.8696 | 19.8696 | 15.3776 | 6.32 | 19.9049 | 19.9049 | 15.2995 | 6.2604 | 19.9403 | 19.9403 | 15.2038 | 6.0991 | 19.9786 | 19.9786 | 15.1202 | 5.9877 | 20.1116 | 20.1116 | 14.9799 | 5.6517 | 20.2346 | 20.2346 | 14.9064 | 5.4438 | 20.3496 | 20.3496 | 14.8673 | 5.3519 | 20.4417 | 20.2921 | 14.8028 | 5.3464 | 19.6737 | 19.6737 | 15.7005 | 7.0724 | 19.7247 | 19.7247 | 15.6431 | 6.7997 | 19.743 | 19.743 | 15.5767 | 6.7497 | 19.7733 | 19.7733 | 15.5219 | 6.7324 | 19.8121 | 19.8121 | 15.4877 | 6.589 | 19.8644 | 19.8644 | 15.4453 | 6.4545 | 19.9237 | 19.9237 | 15.404 | 6.3038 | 19.9884 | 19.9884 | 15.364 | 6.2321 | 20.0536 | 20.0536 | 15.3272 | 6.0541 | 20.1238 | 20.1238 | 15.2639 | 5.9279 | 20.4534 | 20.4534 | 15.0626 | 5.508 | 20.8889 | 20.3305 | 14.8308 | 4.91 | 21.1532 | 20.1516 | 14.7003 | 4.5226 | 21.3016 | 20.0094 | 14.5966 | 4.1642 | 19.6673 | 19.6673 | 15.7027 | 7.0865 | 19.7126 | 19.7126 | 15.6551 | 6.8243 | 19.7243 | 19.7243 | 15.591 | 6.7935 | 19.7469 | 19.7469 | 15.5351 | 6.8017 | 19.7785 | 19.7785 | 15.489 | 6.6869 | 19.8256 | 19.8256 | 15.4295 | 6.5828 | 19.8823 | 19.8823 | 15.3846 | 6.4606 | 19.9463 | 19.9463 | 15.3409 | 6.4184 | 20.0064 | 20.0064 | 15.2683 | 6.2764 | 20.1079 | 20.1079 | 15.1912 | 6.1038 | 20.6157 | 20.3117 | 14.8171 | 5.3664 | 21.0123 | 19.8721 | 14.4964 | 4.6965 | 21.1831 | 19.6856 | 14.3603 | 4.2841 | 21.1461 | 19.6693 | 14.3485 | 4.5132
ANNIE PIT | STAINBURN & SIDDICK | HARKER / HUTTON | 300011 | 527810 | 26.1507 | 9.1333 | 6.5643 | 9.9859 | 26.2525 | 9.053 | 6.5066 | 9.6526 | 26.2652 | 8.9983 | 6.4672 | 9.6432 | 26.3148 | 8.8975 | 6.3948 | 9.3984 | 26.3943 | 8.7852 | 6.3141 | 9.1457 | 26.5008 | 8.6282 | 6.2013 | 8.837 | 26.6194 | 8.5397 | 6.1377 | 8.4273 | 26.7473 | 8.456 | 6.0775 | 8.018 | 26.8811 | 8.3591 | 6.0079 | 7.6566 | 27.0273 | 8.2648 | 5.9401 | 7.1804 | 27.6946 | 7.9961 | 5.747 | 5.6786 | 28.3477 | 9.6593 | 6.9423 | 4.5447 | 28.7934 | 12.5034 | 8.9864 | 4.1259 | 29.1708 | 12.8405 | 9.2287 | 4.0562 | 26.0581 | 9.1952 | 6.6088 | 10.3071 | 26.0894 | 9.1608 | 6.584 | 10.2161 | 26.1637 | 9.0664 | 6.5162 | 9.8669 | 26.2557 | 8.9503 | 6.4327 | 9.4073 | 26.3632 | 8.8239 | 6.3419 | 8.8603 | 26.482 | 8.7012 | 6.2537 | 8.4035 | 26.6145 | 8.5484 | 6.1439 | 7.7008 | 26.757 | 8.3917 | 6.0313 | 6.9983 | 26.9085 | 8.2354 | 5.9189 | 6.2834 | 27.068 | 8.0514 | 5.7867 | 5.4019 | 27.4214 | 7.9402 | 5.7067 | 4.5981 | 27.7495 | 8.9948 | 6.4648 | 4.1188 | 28.0099 | 10.7553 | 7.73 | 3.871 | 28.1902 | 11.0127 | 7.915 | 3.8977 | 26.1513 | 9.1909 | 6.6057 | 9.9417 | 26.2535 | 9.1514 | 6.5773 | 9.6171 | 26.2666 | 9.0364 | 6.4946 | 9.7662 | 26.3167 | 8.8942 | 6.3925 | 9.4748 | 26.3965 | 8.7316 | 6.2756 | 9.2875 | 26.5027 | 8.5632 | 6.1546 | 9.0416 | 26.6207 | 8.3436 | 5.9967 | 8.6491 | 26.748 | 8.1068 | 5.8265 | 8.3386 | 26.8798 | 7.8485 | 5.6409 | 8.0559 | 27.0188 | 7.5449 | 5.4227 | 7.5432 | 27.6161 | 7.1936 | 5.1702 | 6.1221 | 28.0981 | 8.9046 | 6.3999 | 5.1828 | 28.4444 | 11.4206 | 8.2082 | 4.8526 | 28.6925 | 12.1616 | 8.7408 | 4.8837 | 26.1427 | 9.1352 | 6.5656 | 10.0141 | 26.2392 | 9.056 | 6.5087 | 9.7106 | 26.2561 | 8.9841 | 6.4571 | 9.7088 | 26.3192 | 8.8374 | 6.3516 | 9.3398 | 26.4232 | 8.7244 | 6.2704 | 9.2798 | 26.5725 | 8.539 | 6.1371 | 8.8155 | 26.7551 | 8.4181 | 6.0502 | 8.3037 | 26.9666 | 8.3032 | 5.9677 | 7.8849 | 27.2003 | 8.1726 | 5.8738 | 7.5368 | 27.4602 | 7.9988 | 5.7489 | 6.9811 | 28.5814 | 7.271 | 5.2258 | 4.3742 | 29.7096 | 7.7136 | 5.5439 | -1.5372 | 30.3747 | 9.4558 | 6.796 | -6.3005 | 30.6308 | 9.0823 | 6.5276 | -9.4918 | 26.1245 | 9.1415 | 6.5701 | 10.0357 | 26.2132 | 9.0786 | 6.5249 | 9.7314 | 26.2285 | 9.0214 | 6.4839 | 9.8334 | 26.2838 | 8.8825 | 6.384 | 9.5532 | 26.3791 | 8.7674 | 6.3013 | 9.5409 | 26.521 | 8.6462 | 6.2142 | 9.1724 | 26.7056 | 8.5341 | 6.1337 | 8.7386 | 26.9183 | 8.5482 | 6.1438 | 8.4018 | 27.162 | 8.564 | 6.1551 | 7.9803 | 27.4732 | 8.4236 | 6.0542 | 6.4075 | 28.7273 | 12.8654 | 9.2466 | -0.26801 | 29.6353 | 11.1286 | 7.9984 | -5.5961 | 29.9916 | 9.9332 | 7.1392 | -8.8056 | 29.9097 | 9.6031 | 6.902 | -7.9333
ANSDELL | LYTHAM | PENWORTHAM WEST / STANAH | 334416 | 428229 | 21.18 | 10.3858 | 7.5763 | 9.4691 | 21.2265 | 10.4072 | 7.5919 | 9.137 | 21.2623 | 10.3535 | 7.5527 | 8.8052 | 21.3257 | 10.108 | 7.3737 | 8.4616 | 21.4014 | 9.8941 | 7.2176 | 8.1057 | 21.4894 | 9.8869 | 7.2124 | 7.7257 | 21.5863 | 9.7643 | 7.1229 | 7.2881 | 21.6893 | 9.6515 | 7.0407 | 6.86 | 21.7987 | 9.5208 | 6.9453 | 6.4293 | 21.9185 | 9.3756 | 6.8393 | 5.9377 | 22.4133 | 8.6788 | 6.3311 | 4.315 | 22.768 | 8.5672 | 6.2496 | 3.6281 | 22.9599 | 8.6064 | 6.2783 | 3.6258 | 23.0467 | 8.5891 | 6.2656 | 3.8834 | 21.1527 | 10.4188 | 7.6004 | 9.5738 | 21.1787 | 10.3865 | 7.5768 | 9.3398 | 21.2225 | 10.3333 | 7.538 | 9.0112 | 21.2806 | 10.2606 | 7.485 | 8.717 | 21.343 | 10.196 | 7.4379 | 8.4336 | 21.4106 | 10.1116 | 7.3762 | 8.1215 | 21.4837 | 10.018 | 7.308 | 7.7504 | 21.5594 | 9.9167 | 7.2341 | 7.3865 | 21.6382 | 9.8349 | 7.1744 | 7.0141 | 21.7184 | 9.7432 | 7.1075 | 6.6328 | 21.9538 | 9.4228 | 6.8738 | 5.4289 | 22.1308 | 9.1573 | 6.6801 | 4.6244 | 22.2443 | 9.025 | 6.5836 | 4.2031 | 22.3188 | 9.117 | 6.6508 | 3.9561 | 21.18 | 10.4189 | 7.6004 | 9.4735 | 21.2265 | 10.1876 | 7.4317 | 9.1632 | 21.2623 | 10.0754 | 7.3498 | 8.8535 | 21.3257 | 9.7195 | 7.0902 | 8.5222 | 21.401 | 9.709 | 7.0826 | 8.1823 | 21.4885 | 9.5147 | 6.9408 | 7.818 | 21.5849 | 9.4138 | 6.8672 | 7.3958 | 21.6876 | 9.3158 | 6.7958 | 6.962 | 21.7954 | 9.2148 | 6.7221 | 6.5261 | 21.9088 | 9.1078 | 6.644 | 6.0591 | 22.3739 | 8.7268 | 6.3661 | 4.5809 | 22.7032 | 8.4569 | 6.1692 | 3.9749 | 22.8865 | 8.4043 | 6.1308 | 3.9858 | 22.9708 | 8.283 | 6.0423 | 4.2213 | 21.1772 | 10.3898 | 7.5792 | 9.4813 | 21.2254 | 10.3948 | 7.5829 | 9.1634 | 21.2726 | 10.0444 | 7.3273 | 8.8559 | 21.3516 | 10.2051 | 7.4445 | 8.5388 | 21.4553 | 10.0307 | 7.3173 | 8.2308 | 21.5833 | 9.6783 | 7.0602 | 7.9001 | 21.734 | 9.4882 | 6.9215 | 7.5093 | 21.9023 | 9.4732 | 6.9106 | 7.1398 | 22.0857 | 9.4038 | 6.8599 | 6.8109 | 22.2757 | 9.3117 | 6.7928 | 6.4808 | 22.8352 | 8.6946 | 6.3426 | 4.7818 | 23.2855 | 7.9102 | 5.7704 | 2.007 | 23.5062 | 7.5173 | 5.4838 | 0.082229 | 23.619 | 7.1844 | 5.2409 | -1.1789 | 21.1815 | 10.386 | 7.5765 | 9.4385 | 21.2467 | 10.4381 | 7.6145 | 9.0518 | 21.2996 | 10.3149 | 7.5246 | 8.7285 | 21.3778 | 9.865 | 7.1964 | 8.4262 | 21.4819 | 9.9873 | 7.2856 | 8.1374 | 21.6035 | 9.7971 | 7.1468 | 7.8498 | 21.7479 | 9.6297 | 7.0248 | 7.505 | 21.9023 | 9.4591 | 6.9003 | 7.1973 | 22.0444 | 9.2248 | 6.7294 | 6.867 | 22.225 | 9.1662 | 6.6866 | 6.1108 | 22.784 | 8.4676 | 6.177 | 2.721 | 23.0749 | 7.7436 | 5.6489 | 0.29054 | 23.1287 | 7.5216 | 5.4869 | -0.90924 | 23.0436 | 7.4878 | 5.4623 | -0.31547
ARDWICK | STUART ST | STALYBRIDGE | 384753 | 397415 | 25.6233 | 11.9622 | 8.7262 | 6.9304 | 25.7387 | 11.9839 | 8.7421 | 6.39 | 25.741 | 11.5427 | 8.4202 | 4.28 | 25.7779 | 10.9616 | 7.9963 | 2.0644 | 25.8344 | 10.7203 | 7.8203 | 0.017597 | 25.9122 | 10.274 | 7.4947 | -2.2807 | 25.9928 | 9.8335 | 7.1734 | -4.531 | 26.074 | 9.581 | 6.9892 | -5.7508 | 26.1562 | 9.3369 | 6.8111 | -6.9738 | 26.2437 | 9.1126 | 6.6475 | -8.3364 | 26.5865 | 8.6969 | 6.3442 | -9.4146 | 26.8906 | 8.3144 | 6.0652 | -10.162 | 27.0855 | 8.3632 | 6.1009 | -10.5794 | 27.2378 | 8.192 | 5.976 | -10.7238 | 25.5128 | 12.1728 | 8.8799 | 7.3455 | 25.5388 | 11.9145 | 8.6914 | 7.1603 | 25.6016 | 11.6058 | 8.4662 | 4.9527 | 25.6877 | 11.2298 | 8.192 | 2.652 | 25.7846 | 10.8276 | 7.8986 | 0.5519 | 25.8903 | 10.3563 | 7.5548 | -1.7656 | 26.0055 | 9.9371 | 7.2489 | -4.0564 | 26.1271 | 9.7238 | 7.0933 | -5.3192 | 26.2561 | 9.5017 | 6.9314 | -6.5964 | 26.3931 | 9.2502 | 6.7479 | -7.989 | 26.6283 | 9.0641 | 6.6121 | -8.7432 | 26.8356 | 8.8975 | 6.4906 | -9.4324 | 26.9885 | 8.8722 | 6.4721 | -9.9113 | 27.0747 | 8.8207 | 6.4346 | -10.2026 | 25.6234 | 12.1688 | 8.877 | 6.938 | 25.7388 | 12.0516 | 8.7915 | 6.405 | 25.7413 | 11.7476 | 8.5697 | 4.3038 | 25.7784 | 11.2919 | 8.2373 | 2.0969 | 25.8351 | 10.8572 | 7.9201 | 0.059412 | 25.9128 | 10.3199 | 7.5282 | -2.2267 | 25.9934 | 9.8343 | 7.174 | -4.4666 | 26.0747 | 9.5438 | 6.9621 | -5.6761 | 26.1564 | 9.3325 | 6.8079 | -6.8852 | 26.2412 | 9.0575 | 6.6073 | -8.2238 | 26.5549 | 8.6855 | 6.3359 | -9.2056 | 26.7884 | 8.5068 | 6.2056 | -9.8464 | 26.9474 | 8.6069 | 6.2786 | -10.2 | 27.039 | 8.4787 | 6.1851 | -10.3033 | 25.6138 | 11.9683 | 8.7307 | 6.9483 | 25.721 | 11.9909 | 8.7472 | 6.425 | 25.7188 | 11.5182 | 8.4024 | 4.3308 | 25.755 | 11.013 | 8.0338 | 2.1259 | 25.8148 | 10.7305 | 7.8278 | 0.084195 | 25.9038 | 10.2543 | 7.4803 | -2.2192 | 26.0057 | 9.7986 | 7.1479 | -4.5054 | 26.1151 | 9.5462 | 6.9638 | -5.767 | 26.2313 | 9.3327 | 6.8081 | -7.0156 | 26.3556 | 9.0791 | 6.6231 | -8.3592 | 26.8219 | 8.4635 | 6.174 | -9.6355 | 27.225 | 7.9399 | 5.7921 | -11.7827 | 27.4045 | 7.5532 | 5.51 | -13.3409 | 27.4262 | 7.1888 | 5.2442 | -14.3893 | 25.609 | 11.9697 | 8.7317 | 6.951 | 25.7138 | 12.0638 | 8.8004 | 6.4229 | 25.7058 | 11.6129 | 8.4714 | 4.3354 | 25.7328 | 11.2883 | 8.2347 | 2.1453 | 25.7845 | 11 | 8.0244 | 0.094788 | 25.8652 | 10.4885 | 7.6512 | -2.2015 | 25.9612 | 10.066 | 7.343 | -4.463 | 26.0637 | 9.8165 | 7.161 | -5.6949 | 26.1736 | 9.5465 | 6.964 | -6.9256 | 26.301 | 9.1845 | 6.7 | -8.5575 | 26.7917 | 8.3083 | 6.0608 | -11.0389 | 27.1077 | 7.6425 | 5.5751 | -12.9544 | 27.1618 | 7.269 | 5.3026 | -13.9937 | 27.0499 | 7.1914 | 5.246 | -13.6873
ARNSIDE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 346495 | 478180 | 17.876 | 17.876 | 17.876 | 13.3332 | 17.8945 | 17.8945 | 17.8945 | 13.1069 | 17.9207 | 17.9207 | 17.9207 | 13.074 | 17.9491 | 17.9491 | 17.9491 | 12.9318 | 17.9834 | 17.9834 | 17.9834 | 12.8882 | 18.0232 | 18.0232 | 18.0232 | 12.6529 | 18.0712 | 18.0712 | 18.0712 | 12.4968 | 18.1244 | 18.1244 | 18.1244 | 12.3177 | 18.1777 | 18.1777 | 18.1777 | 12.104 | 18.2353 | 18.2353 | 18.2353 | 11.792 | 18.4742 | 18.4742 | 18.4742 | 10.6903 | 18.6606 | 18.6606 | 18.454 | 10.167 | 18.777 | 18.777 | 18.308 | 10.0268 | 18.8557 | 18.8557 | 18.204 | 10.2617 | 17.8824 | 17.8824 | 17.8824 | 13.4387 | 17.9063 | 17.9063 | 17.9063 | 13.2984 | 17.9354 | 17.9354 | 17.9354 | 13.2305 | 17.9625 | 17.9625 | 17.9625 | 13.1012 | 17.9936 | 17.9936 | 17.9936 | 13.0807 | 18.0291 | 18.0291 | 18.0291 | 12.8643 | 18.0703 | 18.0703 | 18.0703 | 12.728 | 18.1154 | 18.1154 | 18.1154 | 12.6734 | 18.1649 | 18.1649 | 18.1649 | 12.5003 | 18.2147 | 18.2147 | 18.2147 | 12.312 | 18.3053 | 18.3053 | 18.3053 | 11.7223 | 18.3874 | 18.3874 | 18.3874 | 11.1723 | 18.4545 | 18.4545 | 18.4545 | 10.7699 | 18.5058 | 18.5058 | 18.5058 | 10.5368 | 17.876 | 17.876 | 17.876 | 13.3344 | 17.8946 | 17.8946 | 17.8946 | 13.1149 | 17.9208 | 17.9208 | 17.9208 | 13.1099 | 17.9492 | 17.9492 | 17.9492 | 12.9815 | 17.9835 | 17.9835 | 17.9835 | 12.9156 | 18.023 | 18.023 | 18.023 | 12.7162 | 18.0708 | 18.0708 | 18.0708 | 12.5701 | 18.124 | 18.124 | 18.124 | 12.3798 | 18.1768 | 18.1768 | 18.1768 | 12.1756 | 18.2317 | 18.2317 | 18.2317 | 11.8914 | 18.4537 | 18.4537 | 18.4537 | 10.8932 | 18.6148 | 18.6148 | 18.5967 | 10.4389 | 18.7183 | 18.7183 | 18.3566 | 10.3231 | 18.7812 | 18.7812 | 18.1611 | 10.5477 | 17.8768 | 17.8768 | 17.8768 | 13.3395 | 17.8999 | 17.8999 | 17.8999 | 13.1039 | 17.931 | 17.931 | 17.931 | 13.0612 | 17.9698 | 17.9698 | 17.9698 | 12.9106 | 18.021 | 18.021 | 18.021 | 12.8279 | 18.0848 | 18.0848 | 18.0848 | 12.5512 | 18.159 | 18.159 | 18.159 | 12.327 | 18.2366 | 18.2366 | 18.2366 | 12.1955 | 18.3222 | 18.3222 | 18.3222 | 11.9803 | 18.4182 | 18.4182 | 18.4182 | 11.7491 | 18.7595 | 18.7595 | 18.5042 | 10.7446 | 19.0219 | 19.0219 | 18.1125 | 9.4862 | 19.144 | 19.144 | 17.8383 | 8.8298 | 19.2117 | 19.2117 | 17.6154 | 8.3489 | 17.881 | 17.881 | 17.881 | 13.3308 | 17.9074 | 17.9074 | 17.9074 | 13.08 | 17.9395 | 17.9395 | 17.9395 | 13.0334 | 17.9795 | 17.9795 | 17.9795 | 12.877 | 18.0317 | 18.0317 | 18.0317 | 12.774 | 18.0938 | 18.0938 | 18.0938 | 12.5039 | 18.164 | 18.164 | 18.164 | 12.2983 | 18.2372 | 18.2372 | 18.2372 | 12.1796 | 18.3163 | 18.3163 | 18.3163 | 11.9961 | 18.4118 | 18.4118 | 18.4118 | 11.6216 | 18.7438 | 18.7438 | 18.421 | 9.9596 | 18.9375 | 18.9375 | 18.0748 | 8.9761 | 18.9905 | 18.9905 | 17.8821 | 8.6075 | 18.9735 | 18.9735 | 17.7859 | 8.924
ASHTON (GOLBORNE) | GOLBORNE | WASHWAY FARM / KIRKBY | 357056 | 400663 | 27.117 | 13.5895 | 9.9134 | 10.0071 | 27.2304 | 11.4606 | 8.3603 | 8.8111 | 27.3 | 9.7644 | 7.123 | 8.3219 | 27.4129 | 8.0923 | 5.9032 | 7.8226 | 27.567 | 6.5627 | 4.7874 | 7.5496 | 27.768 | 5.0197 | 3.6618 | 6.8561 | 28.0078 | 4.9059 | 3.5788 | 6.1624 | 28.2793 | 4.7648 | 3.4758 | 5.5264 | 28.0117 | 4.5438 | 3.3146 | 4.7545 | 26.7404 | 4.3376 | 3.1642 | 3.8677 | 22.7208 | 3.6855 | 2.6886 | 0.86585 | 32.5658 | 5.8986 | 4.3029 | -1.2125 | 33.8715 | 10.1557 | 7.4085 | -2.4937 | 35.0369 | 10.8022 | 7.8801 | -3.2224 | 27.0488 | 13.6671 | 9.97 | 10.5153 | 27.1057 | 11.8116 | 8.6164 | 9.8224 | 27.2106 | 9.9247 | 7.2399 | 9.352 | 27.3338 | 8.1726 | 5.9618 | 8.86 | 27.4759 | 6.3738 | 4.6496 | 8.6177 | 27.6426 | 4.6334 | 3.38 | 8.0059 | 27.5745 | 4.4729 | 3.2629 | 7.4428 | 26.4207 | 4.2857 | 3.1264 | 6.937 | 25.5227 | 4.14 | 3.0201 | 6.257 | 24.3028 | 3.9422 | 2.8757 | 5.5522 | 22.2795 | 3.6139 | 2.6363 | 3.3646 | 30.8856 | 5.3802 | 3.9248 | 1.6193 | 31.7572 | 8.173 | 5.9621 | 0.39356 | 32.4706 | 8.7301 | 6.3685 | -0.31791 | 27.1245 | 13.6625 | 9.9666 | 10.009 | 27.241 | 11.7981 | 8.6065 | 8.7858 | 27.3134 | 9.9021 | 7.2235 | 8.3532 | 27.4285 | 8.0537 | 5.8751 | 7.8676 | 27.5837 | 6.2554 | 4.5633 | 7.6147 | 26.8445 | 4.3544 | 3.1765 | 6.9553 | 24.9653 | 4.0496 | 2.9541 | 6.2635 | 23.9715 | 3.8884 | 2.8365 | 5.6499 | 24.1056 | 3.9102 | 2.8524 | 4.9152 | 23.8988 | 3.8766 | 2.8279 | 4.1074 | 24.6749 | 4.0025 | 2.9198 | 1.4709 | 31.8068 | 6.4471 | 4.7031 | -0.02145 | 32.7677 | 10.5936 | 7.7279 | -0.70028 | 33.5242 | 11.2121 | 8.179 | -0.96217 | 27.1217 | 13.5949 | 9.9173 | 10.0204 | 27.2403 | 11.5125 | 8.3982 | 8.8529 | 27.3316 | 9.9875 | 7.2858 | 8.3837 | 27.4821 | 8.3551 | 6.0949 | 7.9184 | 27.6936 | 6.7451 | 4.9205 | 7.7273 | 28.0018 | 5.0629 | 3.6933 | 7.1167 | 28.4033 | 4.8763 | 3.5572 | 6.5233 | 28.821 | 4.6751 | 3.4104 | 5.975 | 27.3513 | 4.4367 | 3.2365 | 5.3559 | 25.5585 | 4.1458 | 3.0243 | 4.6627 | 18.3338 | 2.9739 | 2.1694 | 0.58632 | 28.2574 | 4.5836 | 3.3437 | -7.6265 | 35.8375 | 7.3751 | 5.3801 | -14.425 | 36.1518 | 7.4801 | 5.4566 | -18.3099 | 27.1265 | 13.6731 | 9.9743 | 10.0232 | 27.2724 | 13.5219 | 9.864 | 8.8019 | 27.393 | 13.4574 | 9.817 | 8.3367 | 27.5655 | 13.3157 | 9.7136 | 7.904 | 27.8021 | 13.144 | 9.5884 | 7.71 | 28.2176 | 12.9369 | 9.4373 | 7.1134 | 28.7155 | 12.6828 | 9.2519 | 6.5099 | 29.3174 | 12.4504 | 9.0824 | 5.9872 | 30.0014 | 12.1915 | 8.8935 | 5.1815 | 30.6469 | 11.6724 | 8.5148 | 3.3361 | 33.3507 | 11.2118 | 8.1788 | -5.0134 | 34.8888 | 9.4409 | 6.887 | -11.943 | 35.4165 | 8.3208 | 6.0699 | -16.3294 | 35.1673 | 8.1174 | 5.9215 | -15.991
ASHTON (RIBBLE) | RIBBLE | PENWORTHAM EAST / ROCHDALE | 350275 | 430526 | 5.4006 | 5.4006 | 5.4006 | 3.4157 | 5.4356 | 5.4356 | 5.4356 | 2.9963 | 5.4673 | 5.4673 | 5.4673 | 2.6512 | 5.5109 | 5.5109 | 5.5109 | 2.3138 | 5.5676 | 5.5676 | 5.5676 | 2.2181 | 5.635 | 5.635 | 5.635 | 1.8881 | 5.713 | 5.713 | 5.713 | 1.529 | 5.7987 | 5.7987 | 5.7987 | 1.1744 | 5.8914 | 5.8914 | 5.8914 | 0.84691 | 5.9948 | 5.9948 | 5.9948 | 0.34355 | 6.443 | 6.443 | 6.443 | -1.171 | 6.7972 | 6.7972 | 6.7972 | -1.7875 | 7.0236 | 7.0236 | 7.0236 | -1.8148 | 7.1972 | 7.1972 | 7.1972 | -1.4342 | 5.3835 | 5.3835 | 5.3835 | 3.6652 | 5.4044 | 5.4044 | 5.4044 | 3.4678 | 5.4409 | 5.4409 | 5.4409 | 3.1456 | 5.4801 | 5.4801 | 5.4801 | 2.8421 | 5.5249 | 5.5249 | 5.5249 | 2.7854 | 5.5751 | 5.5751 | 5.5751 | 2.5171 | 5.6314 | 5.6314 | 5.6314 | 2.2216 | 5.6918 | 5.6918 | 5.6918 | 1.9296 | 5.756 | 5.756 | 5.756 | 1.6642 | 5.8229 | 5.8229 | 5.8229 | 1.2923 | 6.0135 | 6.0135 | 6.0135 | 0.36361 | 6.1664 | 6.1664 | 6.1664 | -0.3368 | 6.2837 | 6.2837 | 6.2837 | -0.76798 | 6.3688 | 6.3688 | 6.3688 | -0.88093 | 5.4007 | 5.4007 | 5.4007 | 3.4201 | 5.4357 | 5.4357 | 5.4357 | 3.0067 | 5.4675 | 5.4675 | 5.4675 | 2.6686 | 5.5112 | 5.5112 | 5.5112 | 2.3383 | 5.5677 | 5.5677 | 5.5677 | 2.2487 | 5.6348 | 5.6348 | 5.6348 | 1.9272 | 5.7125 | 5.7125 | 5.7125 | 1.5762 | 5.798 | 5.798 | 5.798 | 1.2291 | 5.8894 | 5.8894 | 5.8894 | 0.91478 | 5.987 | 5.987 | 5.987 | 0.45087 | 6.399 | 6.399 | 6.399 | -0.93478 | 6.6978 | 6.6978 | 6.6978 | -1.449 | 6.8957 | 6.8957 | 6.8957 | -1.446 | 7.0335 | 7.0335 | 7.0335 | -1.0547 | 5.3996 | 5.3996 | 5.3996 | 3.4288 | 5.4368 | 5.4368 | 5.4368 | 3.0214 | 5.4776 | 5.4776 | 5.4776 | 2.6938 | 5.5367 | 5.5367 | 5.5367 | 2.3789 | 5.6172 | 5.6172 | 5.6172 | 2.3152 | 5.719 | 5.719 | 5.719 | 2.0214 | 5.8445 | 5.8445 | 5.8445 | 1.6907 | 5.9894 | 5.9894 | 5.9894 | 1.3735 | 6.1512 | 6.1512 | 6.1512 | 1.1266 | 6.3326 | 6.3326 | 6.3326 | 0.76937 | 7.0014 | 7.0014 | 7.0014 | -0.61038 | 7.5405 | 7.5405 | 7.5405 | -2.7746 | 7.8423 | 7.8423 | 7.8423 | -4.3908 | 7.9216 | 7.9216 | 7.9216 | -5.293 | 5.4042 | 5.4042 | 5.4042 | 3.3935 | 5.4546 | 5.4546 | 5.4546 | 2.9231 | 5.504 | 5.504 | 5.504 | 2.5714 | 5.5668 | 5.5668 | 5.5668 | 2.252 | 5.6503 | 5.6503 | 5.6503 | 2.1846 | 5.7511 | 5.7511 | 5.7511 | 1.9058 | 5.8781 | 5.8781 | 5.8781 | 1.5991 | 6.0189 | 6.0189 | 6.0189 | 1.3205 | 6.1754 | 6.1754 | 6.1754 | 1.0596 | 6.363 | 6.363 | 6.363 | 0.36639 | 7.01 | 7.01 | 7.01 | -2.3237 | 7.4017 | 7.4017 | 7.4017 | -4.1841 | 7.5354 | 7.5354 | 7.5354 | -5.2064 | 7.3933 | 7.3933 | 7.3933 | -4.6083
ASHTON ON MERSEY | SALE | CARRINGTON | 377188 | 392252 | 29.283 | 9.2909 | 6.7776 | 13.8121 | 29.3466 | 9.1558 | 6.679 | 13.1322 | 29.3837 | 9.0359 | 6.5916 | 12.7473 | 29.4489 | 8.8457 | 6.4528 | 12.3269 | 29.5354 | 8.7902 | 6.4123 | 12.1498 | 29.6391 | 8.6374 | 6.3009 | 11.8417 | 29.7528 | 8.4771 | 6.1839 | 11.3205 | 29.8752 | 8.3932 | 6.1227 | 10.9652 | 30.0072 | 8.2309 | 6.0043 | 10.2767 | 30.1563 | 8.103 | 5.911 | 9.7513 | 30.7664 | 7.4686 | 5.4482 | 7.8886 | 31.2342 | 7.0439 | 5.1384 | 6.9236 | 31.5363 | 6.897 | 5.0312 | 6.7875 | 31.7297 | 6.8969 | 5.0312 | 6.995 | 29.2467 | 9.3098 | 6.7913 | 14.0735 | 29.2803 | 9.1707 | 6.6899 | 13.655 | 29.3424 | 9.0585 | 6.608 | 13.2851 | 29.4198 | 8.9256 | 6.5111 | 12.89 | 29.5035 | 8.8285 | 6.4403 | 12.8199 | 29.5969 | 8.7569 | 6.3881 | 12.5229 | 29.6989 | 8.6455 | 6.3068 | 12.0307 | 29.8078 | 8.5626 | 6.2463 | 11.7184 | 29.9236 | 8.4588 | 6.1706 | 11.2252 | 30.0445 | 8.3699 | 6.1057 | 10.8552 | 30.3302 | 8.0953 | 5.9054 | 9.5833 | 30.5825 | 7.8453 | 5.723 | 8.4881 | 30.7683 | 7.7572 | 5.6588 | 7.8544 | 30.8976 | 7.6784 | 5.6013 | 7.3593 | 29.283 | 9.3075 | 6.7897 | 13.8197 | 29.3467 | 9.1596 | 6.6818 | 13.172 | 29.3838 | 9.0299 | 6.5872 | 12.7837 | 29.4491 | 8.8855 | 6.4819 | 12.3752 | 29.5352 | 8.8148 | 6.4303 | 12.1614 | 29.6383 | 8.6859 | 6.3363 | 11.9254 | 29.7514 | 8.559 | 6.2436 | 11.4193 | 29.8735 | 8.4662 | 6.176 | 11.0765 | 30.0037 | 8.3178 | 6.0677 | 10.4144 | 30.1455 | 8.2185 | 5.9953 | 9.9456 | 30.7178 | 7.7965 | 5.6874 | 8.2827 | 31.1434 | 7.4742 | 5.4523 | 7.4513 | 31.4228 | 7.3682 | 5.375 | 7.3568 | 31.5975 | 7.1612 | 5.224 | 7.5617 | 29.2796 | 9.2931 | 6.7792 | 13.8246 | 29.3448 | 9.1505 | 6.6751 | 13.1634 | 29.3943 | 9.0236 | 6.5826 | 12.7992 | 29.4834 | 8.8511 | 6.4568 | 12.4029 | 29.6053 | 8.7678 | 6.396 | 12.3407 | 29.7612 | 8.6383 | 6.3015 | 12.0319 | 29.9493 | 8.508 | 6.2065 | 11.4947 | 30.1616 | 8.3977 | 6.126 | 11.1538 | 30.3908 | 8.2406 | 6.0114 | 10.6694 | 30.6435 | 8.1339 | 5.9336 | 10.341 | 31.523 | 7.3654 | 5.373 | 8.1396 | 32.1735 | 6.227 | 4.5425 | 3.693 | 32.5273 | 5.4517 | 3.977 | 0.41509 | 30.6707 | 4.9751 | 3.6293 | -1.8539 | 29.2787 | 9.292 | 6.7784 | 13.8106 | 29.3533 | 9.1586 | 6.6811 | 13.0592 | 29.4054 | 9.0549 | 6.6054 | 12.718 | 29.49 | 8.9607 | 6.5367 | 12.39 | 29.6107 | 8.8973 | 6.4905 | 12.2768 | 29.7569 | 8.7558 | 6.3872 | 12.0172 | 29.9322 | 8.5949 | 6.2698 | 11.5794 | 30.1236 | 8.4971 | 6.1985 | 11.3188 | 30.3471 | 8.3237 | 6.072 | 10.7592 | 30.6647 | 8.0451 | 5.8688 | 9.7006 | 31.437 | 6.7441 | 4.9198 | 4.7072 | 31.8967 | 5.5114 | 4.0205 | 0.72954 | 31.4751 | 5.1056 | 3.7244 | -1.3523 | 31.541 | 5.1163 | 3.7322 | -0.60349
ASHTON UNDER LYNE T11 & T12 | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 32.8471 | 5.8313 | 4.2539 | 9.0719 | 32.9515 | 5.6359 | 4.1113 | 8.6427 | 32.9784 | 5.3885 | 3.9309 | 8.4018 | 30.8201 | 4.9993 | 3.6469 | 8.1257 | 30.22 | 4.902 | 3.5759 | 7.9233 | 29.6257 | 4.8056 | 3.5056 | 7.5431 | 28.6678 | 4.6502 | 3.3923 | 7.0733 | 27.5122 | 4.4627 | 3.2555 | 6.6912 | 25.8019 | 4.1853 | 3.0531 | 6.2437 | 25.0127 | 4.0573 | 2.9598 | 5.6906 | 22.1486 | 3.5927 | 2.6208 | 3.8278 | 18.9967 | 3.0815 | 2.2479 | 2.6905 | 18.3648 | 2.9789 | 2.1731 | 2.2115 | 16.9586 | 2.7509 | 2.0067 | 2.1665 | 32.7769 | 5.8705 | 4.2824 | 9.3777 | 32.8306 | 5.5864 | 4.0752 | 9.0503 | 32.9281 | 5.5772 | 4.0685 | 8.8052 | 32.6314 | 5.2931 | 3.8613 | 8.4215 | 33.1931 | 5.403 | 3.9414 | 8.1869 | 32.5822 | 5.2852 | 3.8554 | 7.6571 | 31.9615 | 5.1845 | 3.782 | 7.1817 | 31.4 | 5.0934 | 3.7156 | 6.7529 | 30.6242 | 4.9675 | 3.6238 | 6.1312 | 29.8009 | 4.834 | 3.5263 | 5.5315 | 27.9224 | 4.5293 | 3.304 | 4.3771 | 25.9905 | 4.2159 | 3.0755 | 3.4328 | 25.7784 | 4.1815 | 3.0504 | 2.925 | 25.5583 | 4.1458 | 3.0243 | 2.6828 | 32.8502 | 5.8613 | 4.2758 | 9.0878 | 32.9557 | 5.615 | 4.0961 | 8.6737 | 32.9833 | 5.5142 | 4.0225 | 8.4333 | 33.0539 | 5.4057 | 3.9434 | 8.1306 | 33.1539 | 5.3864 | 3.9293 | 7.9945 | 32.2592 | 5.2328 | 3.8172 | 7.5294 | 31.4041 | 5.0941 | 3.716 | 7.0761 | 30.4818 | 4.9444 | 3.6069 | 6.7089 | 29.1526 | 4.7288 | 3.4496 | 6.2841 | 28.2187 | 4.5774 | 3.3391 | 5.7824 | 24.7102 | 4.0082 | 2.924 | 4.0886 | 22.2863 | 3.6151 | 2.6371 | 3.1416 | 22.1049 | 3.5856 | 2.6157 | 2.734 | 20.5441 | 3.3324 | 2.431 | 2.6872 | 32.8416 | 5.8316 | 4.2541 | 9.0895 | 32.9402 | 5.6188 | 4.0988 | 8.6611 | 32.9611 | 5.3466 | 3.9003 | 8.4409 | 30.2556 | 4.9078 | 3.5801 | 8.1646 | 30.2481 | 4.9065 | 3.5792 | 7.9552 | 29.3058 | 4.7537 | 3.4677 | 7.5343 | 27.9302 | 4.5306 | 3.305 | 7.0189 | 25.8751 | 4.1972 | 3.0618 | 6.5805 | 25.6755 | 4.1648 | 3.0382 | 6.1022 | 25.0446 | 4.0625 | 2.9635 | 5.5608 | 19.1456 | 3.1056 | 2.2655 | 2.7944 | 9.6427 | 1.5641 | 1.141 | -2.5009 | 3.6263 | 0.58822 | 0.4291 | -6.9842 | -1.8597 | -0.30166 | -0.22006 | -9.9276 | 32.8223 | 5.8379 | 4.2587 | 9.112 | 32.9119 | 5.7312 | 4.1808 | 8.7082 | 32.9345 | 5.538 | 4.0399 | 8.4662 | 32.3553 | 5.2483 | 3.8286 | 8.2055 | 30.5945 | 4.9627 | 3.6202 | 8.0584 | 30.4748 | 4.9433 | 3.6061 | 7.6355 | 29.3891 | 4.7672 | 3.4776 | 7.1765 | 27.8991 | 4.5255 | 3.3013 | 6.813 | 26.4727 | 4.2941 | 3.1325 | 6.3102 | 25.1806 | 4.0845 | 2.9796 | 4.9937 | 15.7682 | 2.5578 | 1.8659 | -1.1068 | 5.4323 | 0.88117 | 0.6428 | -6.2991 | 0.19678 | 0.031919 | 0.023285 | -9.2616 | -0.59185 | -0.096005 | -0.070034 | -8.2733
ASHTON UNDER LYNE T13 | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 20.1815 | 20.1815 | 15.9139 | 11.5459 | 20.222 | 20.222 | 15.8645 | 11.3215 | 20.2268 | 20.2268 | 15.8254 | 11.3455 | 20.2466 | 20.2466 | 15.7716 | 11.253 | 20.2765 | 20.2765 | 15.7194 | 11.2549 | 20.3161 | 20.3161 | 15.6369 | 11.1129 | 20.3594 | 20.3594 | 15.6378 | 11.0289 | 20.4031 | 20.4031 | 15.609 | 10.9434 | 20.4367 | 20.4367 | 15.5612 | 10.8024 | 20.4726 | 20.4726 | 15.5073 | 10.6935 | 20.5924 | 20.5924 | 15.3561 | 10.2754 | 20.6698 | 20.6698 | 15.2495 | 10.0113 | 20.7039 | 20.7039 | 15.2003 | 9.9271 | 20.7115 | 20.7115 | 15.1294 | 9.9578 | 20.1456 | 20.1456 | 15.9255 | 11.6791 | 20.1586 | 20.1586 | 15.8962 | 11.5658 | 20.1876 | 20.1876 | 15.8275 | 11.5305 | 20.225 | 20.225 | 15.7664 | 11.4077 | 20.2675 | 20.2675 | 15.7394 | 11.3907 | 20.3143 | 20.3143 | 15.7172 | 11.2458 | 20.3659 | 20.3659 | 15.6978 | 11.1524 | 20.4211 | 20.4211 | 15.6796 | 11.054 | 20.4781 | 20.4781 | 15.6529 | 10.8961 | 20.5299 | 20.5299 | 15.6281 | 10.7792 | 20.6022 | 20.6022 | 15.556 | 10.5015 | 20.6559 | 20.6559 | 15.4814 | 10.2715 | 20.6814 | 20.6814 | 15.4759 | 10.1648 | 20.6821 | 20.6821 | 15.4998 | 10.1494 | 20.1815 | 20.1815 | 15.9203 | 11.549 | 20.222 | 20.222 | 15.8787 | 11.3303 | 20.2268 | 20.2268 | 15.8305 | 11.359 | 20.2466 | 20.2466 | 15.7367 | 11.2717 | 20.2764 | 20.2764 | 15.7361 | 11.2784 | 20.3158 | 20.3158 | 15.6928 | 11.1423 | 20.3589 | 20.3589 | 15.665 | 11.0636 | 20.4027 | 20.4027 | 15.6202 | 10.9783 | 20.436 | 20.436 | 15.5802 | 10.8411 | 20.4705 | 20.4705 | 15.5388 | 10.7475 | 20.5835 | 20.5835 | 15.4369 | 10.3633 | 20.6553 | 20.6553 | 15.3391 | 10.1274 | 20.6866 | 20.6866 | 15.3537 | 10.0548 | 20.6934 | 20.6934 | 15.2797 | 10.087 | 20.1773 | 20.1773 | 15.915 | 11.5557 | 20.2147 | 20.2147 | 15.8647 | 11.3396 | 20.2196 | 20.2196 | 15.8093 | 11.3698 | 20.2428 | 20.2428 | 15.7566 | 11.2818 | 20.2803 | 20.2803 | 15.7093 | 11.2853 | 20.3319 | 20.3319 | 15.6533 | 11.1426 | 20.3779 | 20.3779 | 15.6153 | 11.0529 | 20.4226 | 20.4226 | 15.5618 | 10.9589 | 20.4693 | 20.4693 | 15.4375 | 10.8161 | 20.5198 | 20.5198 | 15.4733 | 10.7175 | 20.6939 | 20.6939 | 15.2518 | 10.1231 | 20.8219 | 20.4659 | 14.9296 | 8.6956 | 20.8756 | 20.1575 | 14.7046 | 7.5598 | 20.8817 | 19.932 | 14.5401 | 6.8435 | 20.1714 | 20.1714 | 15.9164 | 11.5612 | 20.2064 | 20.2064 | 15.8829 | 11.3435 | 20.2097 | 20.2097 | 15.8531 | 11.376 | 20.2281 | 20.2281 | 15.7949 | 11.298 | 20.2603 | 20.2603 | 15.7752 | 11.3132 | 20.3036 | 20.3036 | 15.6977 | 11.1878 | 20.3367 | 20.3367 | 15.6871 | 11.1144 | 20.3723 | 20.3723 | 15.6366 | 11.0356 | 20.4155 | 20.4155 | 15.5565 | 10.8832 | 20.4781 | 20.4781 | 15.4912 | 10.5744 | 20.6543 | 20.6543 | 15.1661 | 9.0449 | 20.7415 | 20.3448 | 14.8412 | 7.7193 | 20.7424 | 20.09 | 14.6554 | 6.9988 | 20.6716 | 20.0398 | 14.6188 | 7.3396
ASHWOOD DALE | BUXTON | STALYBRIDGE | 406537 | 373050 | 32.2625 | 9.1651 | 6.6858 | 11.8667 | 32.3313 | 8.7019 | 6.3479 | 11.5197 | 32.3245 | 8.223 | 5.9986 | 11.5911 | 32.3665 | 7.8637 | 5.7365 | 11.3253 | 32.427 | 7.4721 | 5.4508 | 11.2508 | 32.5074 | 7.0524 | 5.1447 | 10.9041 | 32.5935 | 7.0792 | 5.1642 | 10.6056 | 32.6823 | 7.0395 | 5.1352 | 10.377 | 32.7741 | 6.9049 | 5.037 | 10.0009 | 32.8724 | 6.5836 | 4.8026 | 9.6195 | 33.2105 | 6.4304 | 4.6909 | 8.3041 | 33.4956 | 6.3353 | 4.6215 | 7.343 | 33.6777 | 8.3835 | 6.1157 | 6.8741 | 33.7906 | 8.2516 | 6.0194 | 6.7663 | 32.2031 | 9.1869 | 6.7017 | 11.8897 | 32.2328 | 8.6403 | 6.303 | 11.5435 | 32.2924 | 8.1767 | 5.9648 | 11.4964 | 32.3905 | 7.7155 | 5.6284 | 11.1743 | 32.5016 | 7.3151 | 5.3363 | 11.0503 | 32.6253 | 6.951 | 5.0707 | 10.6448 | 32.7626 | 6.8579 | 5.0027 | 10.2727 | 32.9099 | 6.7817 | 4.9472 | 9.9621 | 33.0687 | 6.6669 | 4.8634 | 9.4845 | 33.2383 | 6.5716 | 4.7939 | 9.0521 | 33.4548 | 6.2655 | 4.5706 | 8.0972 | 33.6446 | 5.8459 | 4.2645 | 7.1869 | 33.7872 | 6.798 | 4.9591 | 6.5742 | 33.8789 | 9.2296 | 6.7329 | 6.1173 | 32.2626 | 9.1849 | 6.7002 | 11.8821 | 32.3314 | 8.6136 | 6.2835 | 11.5685 | 32.3247 | 8.1196 | 5.9232 | 11.6672 | 32.3668 | 7.6072 | 5.5493 | 11.4244 | 32.4274 | 7.1845 | 5.241 | 11.3706 | 32.5077 | 6.6909 | 4.8809 | 11.0491 | 32.5937 | 6.548 | 4.7767 | 10.7739 | 32.6825 | 6.3865 | 4.6589 | 10.5667 | 32.7736 | 6.1914 | 4.5165 | 10.221 | 32.8688 | 5.9393 | 4.3327 | 9.8846 | 33.1818 | 5.7809 | 4.2171 | 8.7001 | 33.4164 | 5.5495 | 4.0483 | 7.8515 | 33.576 | 8.5228 | 6.2173 | 7.4339 | 33.655 | 8.2789 | 6.0393 | 7.357 | 32.2541 | 9.1618 | 6.6834 | 11.8707 | 32.3142 | 8.7131 | 6.3561 | 11.5263 | 32.3018 | 8.0082 | 5.8418 | 11.6003 | 32.3451 | 7.8605 | 5.7342 | 11.323 | 32.4116 | 7.5097 | 5.4783 | 11.238 | 32.5056 | 7.1146 | 5.19 | 10.8659 | 32.6147 | 7.0612 | 5.151 | 10.5062 | 32.7335 | 6.8524 | 4.9987 | 10.2091 | 32.858 | 6.7369 | 4.9145 | 9.8146 | 32.9932 | 6.7661 | 4.9357 | 9.4731 | 33.4358 | 5.9432 | 4.3355 | 7.3898 | 30.9715 | 5.0239 | 3.6649 | 2.3333 | 34.1187 | 6.4665 | 4.7172 | -1.5359 | 34.1824 | 5.8665 | 4.2795 | -4.225 | 32.2346 | 9.172 | 6.6909 | 11.9243 | 32.2781 | 8.9153 | 6.5036 | 11.6278 | 32.2507 | 8.9972 | 6.5634 | 11.7468 | 32.273 | 9.0318 | 6.5886 | 11.5323 | 32.3192 | 8.9805 | 6.5512 | 11.4908 | 32.3909 | 8.7714 | 6.3986 | 11.182 | 32.4758 | 8.507 | 6.2058 | 10.8992 | 32.5686 | 8.1803 | 5.9674 | 10.681 | 32.6755 | 8.3358 | 6.0808 | 10.2609 | 32.8242 | 8.1845 | 5.9705 | 9.098 | 33.3679 | 7.5756 | 5.5263 | 3.6658 | 33.739 | 6.3616 | 4.6407 | -0.98234 | 33.8092 | 5.873 | 4.2843 | -3.6194 | 33.6549 | 5.8426 | 4.2621 | -2.9364
ASKAM & DALTON | ULVERSTON | HARKER / HUTTON | 321558 | 477806 | 15.4322 | 9.7311 | 6.9939 | 8.4708 | 15.5097 | 9.6121 | 6.9084 | 8.0149 | 15.6 | 9.521 | 6.843 | 7.8699 | 15.7475 | 9.3314 | 6.7066 | 7.3969 | 15.9107 | 9.1837 | 6.6005 | 7.155 | 16.0968 | 8.9385 | 6.4243 | 6.6204 | 16.3092 | 8.6874 | 6.2438 | 6.0304 | 16.5409 | 8.4696 | 6.0872 | 5.5948 | 16.7825 | 8.2288 | 5.9142 | 5.042 | 17.1579 | 7.9167 | 5.6899 | 4.1427 | 18.5112 | 6.778 | 4.8715 | 1.2411 | 19.1108 | 6.0134 | 4.322 | -0.25193 | 19.3955 | 5.8504 | 4.2048 | -0.67445 | 19.3989 | 5.5883 | 4.0164 | 0.054664 | 15.4241 | 9.7668 | 7.0196 | 8.6271 | 15.49 | 9.6901 | 6.9644 | 8.3372 | 15.5945 | 9.603 | 6.9018 | 8.1051 | 15.6777 | 9.4681 | 6.8049 | 7.7396 | 15.7789 | 9.3782 | 6.7403 | 7.5985 | 15.8992 | 9.2187 | 6.6257 | 7.1648 | 16.0375 | 9.0546 | 6.5077 | 6.6719 | 16.188 | 8.9233 | 6.4133 | 6.323 | 16.3506 | 8.7691 | 6.3025 | 5.8329 | 16.5218 | 8.5981 | 6.1796 | 5.2495 | 17.0046 | 8.1362 | 5.8476 | 3.9054 | 17.6225 | 7.6251 | 5.4803 | 2.5248 | 18.0757 | 7.4143 | 5.3288 | 1.5107 | 18.1293 | 7.3168 | 5.2587 | 0.98848 | 15.4322 | 9.7705 | 7.0222 | 8.4805 | 15.5097 | 9.6885 | 6.9633 | 8.0626 | 15.6001 | 9.5735 | 6.8807 | 7.9248 | 15.7476 | 9.3919 | 6.7502 | 7.4855 | 15.9103 | 9.2525 | 6.6499 | 7.2716 | 16.0956 | 9.0032 | 6.4708 | 6.7685 | 16.3072 | 8.7503 | 6.289 | 6.2101 | 16.5384 | 8.5269 | 6.1285 | 5.8022 | 16.7772 | 8.2734 | 5.9462 | 5.2845 | 17.1409 | 7.9981 | 5.7484 | 4.4786 | 18.4577 | 7.2255 | 5.1931 | 1.8819 | 19.0144 | 6.4532 | 4.638 | 0.56038 | 19.2788 | 6.0664 | 4.36 | 0.20255 | 19.2664 | 5.5234 | 3.9698 | 0.96619 | 15.432 | 9.7288 | 6.9923 | 8.4722 | 15.5431 | 9.5874 | 6.8906 | 7.9653 | 15.6906 | 9.4604 | 6.7994 | 7.766 | 15.9041 | 9.2429 | 6.6431 | 7.2591 | 16.185 | 9.0561 | 6.5088 | 6.9369 | 16.5433 | 8.7584 | 6.2948 | 6.2788 | 16.998 | 8.4363 | 6.0633 | 5.4989 | 17.5058 | 8.1427 | 5.8523 | 4.8653 | 17.7784 | 7.8461 | 5.6391 | 4.2263 | 18.0758 | 7.5236 | 5.4074 | 3.4812 | 19.2638 | 6.0253 | 4.3305 | 0.091594 | 20.6143 | 4.0089 | 2.8813 | -6.2062 | 17.0142 | 2.8013 | 2.0133 | -10.3485 | 9.93 | 1.6349 | 1.175 | -13.1775 | 15.41 | 9.7402 | 7.0005 | 8.5206 | 15.5164 | 9.6096 | 6.9066 | 8.0152 | 15.6675 | 9.4715 | 6.8073 | 7.8384 | 15.8907 | 9.2402 | 6.6411 | 7.3683 | 16.1919 | 9.0368 | 6.4949 | 7.0607 | 16.6137 | 8.7253 | 6.2711 | 6.4058 | 17.0376 | 8.4196 | 6.0514 | 5.7511 | 17.4836 | 8.1561 | 5.862 | 5.2773 | 17.7408 | 7.8739 | 5.6591 | 4.7051 | 18.2108 | 7.351 | 5.2833 | 3.0109 | 19.7105 | 5.3774 | 3.8649 | -4.3976 | 20.2427 | 3.4438 | 2.4751 | -9.6847 | 14.5593 | 2.3971 | 1.7228 | -12.249 | 12.9638 | 2.1344 | 1.534 | -10.7984
ASKERTON CASTLE | - | HARKER / HUTTON | 354779 | 568913 | 3.1393 | 3.1393 | 3.1393 | 1.6199 | 3.1551 | 3.1551 | 3.1551 | 1.5713 | 3.1685 | 3.1685 | 3.1685 | 1.572 | 3.1846 | 3.1846 | 3.1846 | 1.5254 | 3.2048 | 3.2048 | 3.2048 | 1.5163 | 3.2286 | 3.2286 | 3.2286 | 1.4774 | 3.258 | 3.258 | 3.258 | 1.4353 | 3.2903 | 3.2903 | 3.2903 | 1.3879 | 3.3253 | 3.3253 | 3.3253 | 1.3356 | 3.3606 | 3.3606 | 3.3606 | 1.2873 | 3.4663 | 3.4663 | 3.4663 | 1.1068 | 3.5369 | 3.5369 | 3.5369 | 1.0564 | 3.5389 | 3.5389 | 3.5389 | 1.0405 | 3.5232 | 3.5232 | 3.5232 | 1.0262 | 3.1411 | 3.1411 | 3.1411 | 1.6678 | 3.1485 | 3.1485 | 3.1485 | 1.6585 | 3.1606 | 3.1606 | 3.1606 | 1.6303 | 3.1725 | 3.1725 | 3.1725 | 1.5888 | 3.1858 | 3.1858 | 3.1858 | 1.5574 | 3.2009 | 3.2009 | 3.2009 | 1.5153 | 3.2186 | 3.2186 | 3.2186 | 1.4685 | 3.2374 | 3.2374 | 3.2374 | 1.431 | 3.2572 | 3.2572 | 3.2572 | 1.3742 | 3.2777 | 3.2777 | 3.2777 | 1.3073 | 3.3392 | 3.3392 | 3.3392 | 1.2093 | 3.38 | 3.38 | 3.38 | 1.1725 | 3.4028 | 3.4028 | 3.4028 | 1.1704 | 3.4149 | 3.4149 | 3.4149 | 1.2038 | 3.1393 | 3.1393 | 3.1393 | 1.6205 | 3.1551 | 3.1551 | 3.1551 | 1.5727 | 3.1685 | 3.1685 | 3.1685 | 1.5916 | 3.1846 | 3.1846 | 3.1846 | 1.5286 | 3.2047 | 3.2047 | 3.2047 | 1.5218 | 3.2283 | 3.2283 | 3.2283 | 1.4871 | 3.2575 | 3.2575 | 3.2575 | 1.4625 | 3.2897 | 3.2897 | 3.2897 | 1.4186 | 3.3241 | 3.3241 | 3.3241 | 1.3694 | 3.3591 | 3.3591 | 3.3591 | 1.3269 | 3.4603 | 3.4603 | 3.4603 | 1.1617 | 3.519 | 3.519 | 3.519 | 1.1204 | 3.5198 | 3.5198 | 3.5198 | 1.1034 | 3.5058 | 3.5058 | 3.5058 | 1.0786 | 3.139 | 3.139 | 3.139 | 1.6234 | 3.1568 | 3.1568 | 3.1568 | 1.5775 | 3.1749 | 3.1749 | 3.1749 | 1.5806 | 3.1982 | 3.1982 | 3.1982 | 1.5305 | 3.2293 | 3.2293 | 3.2293 | 1.5185 | 3.2569 | 3.2569 | 3.2569 | 1.4754 | 3.2859 | 3.2859 | 3.2859 | 1.4434 | 3.3155 | 3.3155 | 3.3155 | 1.3908 | 3.3451 | 3.3451 | 3.3451 | 1.3417 | 3.3744 | 3.3744 | 3.3744 | 1.3068 | 3.4623 | 3.4623 | 3.4623 | 1.0752 | 3.4832 | 3.4832 | 3.4832 | 0.8764 | 3.463 | 3.463 | 3.463 | 0.79689 | 3.4229 | 3.4229 | 3.4229 | 0.77064 | 3.1463 | 3.1463 | 3.1463 | 1.6214 | 3.1681 | 3.1681 | 3.1681 | 1.5717 | 3.1897 | 3.1897 | 3.1897 | 1.5701 | 3.2149 | 3.2149 | 3.2149 | 1.5219 | 3.237 | 3.237 | 3.237 | 1.5096 | 3.2585 | 3.2585 | 3.2585 | 1.4676 | 3.2841 | 3.2841 | 3.2841 | 1.4365 | 3.3086 | 3.3086 | 3.3086 | 1.387 | 3.332 | 3.332 | 3.332 | 1.3429 | 3.3572 | 3.3572 | 3.3572 | 1.3145 | 3.4343 | 3.4343 | 3.4343 | 1.1132 | 3.4372 | 3.4372 | 3.4372 | 0.99441 | 3.4058 | 3.4058 | 3.4058 | 0.99196 | 3.3594 | 3.3594 | 3.3594 | 1.044
ASPATRIA | STAINBURN & SIDDICK | HARKER / HUTTON | 314417 | 542840 | 14.4119 | 14.4119 | 12.808 | 5.7575 | 14.4895 | 14.4895 | 12.3051 | 5.237 | 14.5631 | 14.5631 | 11.8128 | 4.8923 | 14.6647 | 14.6647 | 11.3145 | 4.6077 | 14.7913 | 14.7913 | 10.8474 | 4.5567 | 14.9373 | 14.3789 | 10.3344 | 4.2295 | 15.1087 | 14.2524 | 10.2435 | 3.902 | 15.2837 | 14.1702 | 10.1844 | 3.8098 | 15.3945 | 14.0348 | 10.0871 | 3.4098 | 15.5225 | 13.8913 | 9.9839 | 2.9686 | 16.0951 | 13.4298 | 9.6522 | 1.2303 | 16.6128 | 13.3351 | 9.5842 | 0.1128 | 16.9511 | 16.7295 | 12.0239 | -0.55762 | 17.1095 | 17.1095 | 12.44 | -0.36135 | 14.3724 | 14.3724 | 12.8378 | 5.9522 | 14.418 | 14.418 | 12.3741 | 5.6213 | 14.5065 | 14.5065 | 11.9012 | 5.2992 | 14.603 | 14.603 | 11.4294 | 5.0528 | 14.7105 | 14.7105 | 10.9865 | 5.0173 | 14.8295 | 14.614 | 10.5034 | 4.7107 | 14.967 | 14.5203 | 10.436 | 4.3972 | 15.1128 | 14.4688 | 10.399 | 4.3023 | 15.2586 | 14.3689 | 10.3272 | 3.9312 | 15.3412 | 14.2897 | 10.2703 | 3.6675 | 15.655 | 14.0775 | 10.1178 | 2.8183 | 16.0499 | 13.7814 | 9.905 | 1.6141 | 16.268 | 15.6766 | 11.267 | 0.46929 | 16.4056 | 16.4056 | 12.7026 | -0.208 | 14.4128 | 14.4128 | 12.8369 | 5.7627 | 14.4907 | 14.4907 | 12.3702 | 5.2611 | 14.5646 | 14.5646 | 11.886 | 4.9369 | 14.6665 | 14.6665 | 11.3963 | 4.6722 | 14.7926 | 14.7926 | 10.9351 | 4.6334 | 14.9372 | 14.5065 | 10.4261 | 4.3218 | 15.107 | 14.3759 | 10.3322 | 4.0088 | 15.2833 | 14.2862 | 10.2678 | 3.9252 | 15.392 | 14.1431 | 10.1649 | 3.5508 | 15.5135 | 14.0009 | 10.0627 | 3.163 | 16.035 | 13.701 | 9.8472 | 1.645 | 16.4413 | 13.5935 | 9.77 | 0.73132 | 16.7107 | 16.709 | 12.0091 | 0.20085 | 16.863 | 16.863 | 12.2237 | 0.41285 | 14.4085 | 14.4085 | 12.8073 | 5.76 | 14.484 | 14.484 | 12.2977 | 5.2139 | 14.5577 | 14.5577 | 11.7926 | 4.8424 | 14.6647 | 14.6647 | 11.2811 | 4.5274 | 14.8031 | 14.8031 | 10.7963 | 4.4164 | 14.9706 | 14.2755 | 10.2601 | 4.0015 | 15.1754 | 14.1065 | 10.1386 | 3.5461 | 15.3998 | 13.9824 | 10.0494 | 3.3399 | 15.6361 | 13.8146 | 9.9288 | 2.8806 | 15.8882 | 13.6688 | 9.824 | 2.5488 | 16.706 | 13.0856 | 9.4049 | 0.85313 | 17.3742 | 12.6068 | 9.0607 | -1.3286 | 17.7009 | 15.7078 | 11.2895 | -2.6287 | 17.7766 | 16.0098 | 11.5066 | -3.3489 | 14.4134 | 14.4134 | 12.8105 | 5.7771 | 14.5123 | 14.5123 | 12.7255 | 5.229 | 14.6021 | 14.6021 | 12.6357 | 4.8605 | 14.711 | 14.711 | 12.5393 | 4.5533 | 14.85 | 14.85 | 12.4657 | 4.4148 | 15.0119 | 15.0119 | 12.346 | 4.0031 | 15.2175 | 15.2175 | 12.227 | 3.5883 | 15.4353 | 15.4353 | 12.1502 | 3.4329 | 15.6401 | 15.6401 | 12.0426 | 3.006 | 15.8551 | 15.8551 | 11.9101 | 2.4195 | 16.744 | 16.1575 | 11.6127 | -0.35287 | 17.2577 | 15.5038 | 11.1429 | -2.1919 | 17.3519 | 16.3882 | 11.7785 | -3.0248 | 17.2375 | 16.2198 | 11.6575 | -2.5492
ATHERTON TOWN CENTRE | ATHERTON | KEARSLEY | 367546 | 403338 | 32.0004 | 5.2686 | 3.7867 | 20.362 | 29.9122 | 4.9248 | 3.5396 | 19.3556 | 28.3246 | 4.6634 | 3.3517 | 19.2109 | 26.1743 | 4.3094 | 3.0973 | 17.6512 | 24.282 | 3.9978 | 2.8733 | 16.9703 | 22.0057 | 3.6231 | 2.604 | 14.5626 | 19.4742 | 3.2063 | 2.3044 | 12.3241 | 17.3772 | 2.861 | 2.0563 | 10.7249 | 14.7888 | 2.4349 | 1.75 | 8.8308 | 12.0736 | 1.9878 | 1.4287 | 7.0169 | 5.1553 | 0.84878 | 0.61003 | 3.4317 | 1.1053 | 0.18198 | 0.13079 | 1.1053 | 2.6844 | 0.44197 | 0.31765 | 1.0744 | 2.6844 | 0.44197 | 0.31765 | 1.34 | 32.3382 | 5.3242 | 3.8266 | 20.6357 | 31.3728 | 5.1653 | 3.7124 | 19.8553 | 30.8311 | 5.0761 | 3.6483 | 19.5701 | 29.4081 | 4.8418 | 3.4799 | 18.4597 | 28.8482 | 4.7496 | 3.4137 | 18.2523 | 27.149 | 4.4699 | 3.2126 | 17.0017 | 25.6934 | 4.2302 | 3.0403 | 15.8985 | 24.2259 | 3.9886 | 2.8667 | 15.0542 | 22.4424 | 3.695 | 2.6556 | 13.7996 | 21.3209 | 3.5103 | 2.5229 | 12.6064 | 18.6581 | 3.0719 | 2.2078 | 10.179 | 15.3563 | 2.5283 | 1.8171 | 8.3866 | 13.836 | 2.278 | 1.6372 | 7.182 | 13.6057 | 2.2401 | 1.61 | 6.6757 | 32.3557 | 5.3271 | 3.8287 | 20.3871 | 31.1899 | 5.1352 | 3.6908 | 19.4201 | 31.3811 | 5.1667 | 3.7134 | 19.3042 | 29.8723 | 4.9183 | 3.5348 | 17.779 | 28.7054 | 4.7261 | 3.3968 | 17.1249 | 25.9548 | 4.2733 | 3.0713 | 14.7581 | 23.6197 | 3.8888 | 2.795 | 12.5557 | 22.3654 | 3.6823 | 2.6465 | 10.942 | 21.1943 | 3.4895 | 2.508 | 9.1483 | 19.6916 | 3.2421 | 2.3301 | 7.4414 | 14.9739 | 2.4653 | 1.7719 | 4.218 | 10.4173 | 1.7151 | 1.2327 | 2.7668 | 8.5814 | 1.4129 | 1.0155 | 2.459 | 4.8936 | 0.8057 | 0.57907 | 3.013 | 31.985 | 5.2661 | 3.7848 | 20.3831 | 29.7599 | 4.8997 | 3.5215 | 19.3993 | 27.9925 | 4.6088 | 3.3124 | 19.2858 | 25.8692 | 4.2592 | 3.0611 | 17.764 | 24.7872 | 4.081 | 2.9331 | 17.1582 | 21.979 | 3.6187 | 2.6008 | 14.8325 | 19.2297 | 3.166 | 2.2755 | 12.652 | 16.9025 | 2.7829 | 2.0001 | 11.1881 | 13.926 | 2.2928 | 1.6479 | 9.4035 | 10.6114 | 1.7471 | 1.2557 | 7.8948 | 1.97 | 0.32435 | 0.23312 | 1.97 | 2.6844 | 0.44197 | 0.31765 | -7.2654 | 2.6844 | 0.44197 | 0.31765 | -15.5989 | 2.6844 | 0.44197 | 0.31765 | -20.7696 | 32.0058 | 5.2695 | 3.7873 | 20.3805 | 28.7909 | 4.7402 | 3.4069 | 19.3266 | 28.6906 | 4.7237 | 3.395 | 19.1999 | 27.6458 | 4.5517 | 3.2714 | 17.7277 | 26.109 | 4.2987 | 3.0895 | 17.1828 | 21.4986 | 3.5396 | 2.544 | 14.9572 | 19.4028 | 3.1945 | 2.296 | 12.8687 | 17.9046 | 2.9478 | 2.1187 | 11.4624 | 15.5847 | 2.5659 | 1.8442 | 9.5433 | 11.3594 | 1.8702 | 1.3442 | 6.2532 | 2.6844 | 0.44197 | 0.31765 | -5.386 | 2.6844 | 0.44197 | 0.31765 | -14.6392 | 2.6844 | 0.44197 | 0.31765 | -20.1216 | 2.6844 | 0.44197 | 0.31765 | -18.1989
ATHLETIC ST | BURNLEY | ROCHDALE | 385381 | 432208 | 22.5898 | 13.7911 | 10.0604 | 10.3933 | 22.6394 | 13.2768 | 9.6853 | 9.4943 | 22.7188 | 12.7651 | 9.312 | 9.0509 | 22.8234 | 12.2418 | 8.9302 | 8.8235 | 22.8961 | 12.1238 | 8.8441 | 8.4484 | 22.9847 | 11.7972 | 8.6059 | 8.1449 | 23.0846 | 11.6476 | 8.4968 | 7.631 | 23.1935 | 11.5525 | 8.4274 | 7.2016 | 23.3091 | 11.4496 | 8.3523 | 6.8893 | 23.4382 | 11.308 | 8.249 | 6.3786 | 23.9634 | 10.7019 | 7.8069 | 4.6842 | 24.3837 | 10.8192 | 7.8924 | 3.8877 | 24.6517 | 11.9452 | 8.7138 | 3.7821 | 24.8542 | 12.0185 | 8.7673 | 4.0709 | 22.5974 | 13.8297 | 10.0886 | 10.7862 | 22.651 | 13.5611 | 9.8927 | 10.3965 | 22.7309 | 13.291 | 9.6956 | 9.9432 | 22.7991 | 13.062 | 9.5286 | 9.746 | 22.869 | 12.8288 | 9.3584 | 9.4287 | 22.9479 | 12.6045 | 9.1948 | 9.1762 | 23.0355 | 12.5161 | 9.1303 | 8.7284 | 23.1295 | 12.4395 | 9.0744 | 8.3571 | 23.2291 | 12.3747 | 9.0272 | 8.0863 | 23.3337 | 12.2928 | 8.9674 | 7.699 | 23.5998 | 12.0907 | 8.82 | 6.5882 | 23.8269 | 12.0692 | 8.8043 | 5.7904 | 23.9906 | 12.6411 | 9.2215 | 5.3209 | 24.0954 | 13.1287 | 9.5772 | 5.0547 | 22.5899 | 13.8295 | 10.0884 | 10.4045 | 22.6395 | 13.5705 | 9.8995 | 9.5002 | 22.719 | 13.243 | 9.6606 | 9.0944 | 22.8238 | 12.9379 | 9.438 | 8.8802 | 22.8964 | 12.623 | 9.2083 | 8.5228 | 22.9845 | 12.2741 | 8.9538 | 8.2355 | 23.0841 | 12.1646 | 8.8739 | 7.7402 | 23.1929 | 12.0639 | 8.8004 | 7.3272 | 23.307 | 11.9752 | 8.7357 | 7.036 | 23.4298 | 11.8805 | 8.6666 | 6.5776 | 23.9136 | 11.6702 | 8.5133 | 5.0632 | 24.268 | 11.7271 | 8.5548 | 4.4111 | 24.502 | 12.9157 | 9.4218 | 4.3588 | 24.6605 | 13.0466 | 9.5173 | 4.658 | 22.5917 | 13.7919 | 10.061 | 10.3995 | 22.6554 | 13.26 | 9.673 | 9.508 | 22.7697 | 12.7227 | 9.281 | 9.0632 | 22.8469 | 12.2847 | 8.9615 | 8.8437 | 22.9427 | 12.1071 | 8.8319 | 8.4875 | 23.0677 | 11.7523 | 8.5732 | 8.1972 | 23.2202 | 11.614 | 8.4722 | 7.6799 | 23.3957 | 11.4734 | 8.3697 | 7.2492 | 23.5901 | 11.3645 | 8.2902 | 6.994 | 23.808 | 11.2263 | 8.1894 | 6.6145 | 24.5941 | 10.5398 | 7.6886 | 4.5484 | 25.2769 | 9.912 | 7.2307 | 0.45663 | 25.6546 | 10.3355 | 7.5396 | -2.4979 | 25.8459 | 9.9565 | 7.2631 | -4.3887 | 22.5867 | 13.7947 | 10.063 | 10.4053 | 22.6651 | 13.409 | 9.7817 | 9.4964 | 22.776 | 12.864 | 9.3841 | 9.0363 | 22.8373 | 12.9048 | 9.4139 | 8.839 | 22.9267 | 12.5189 | 9.1324 | 8.5027 | 23.0411 | 12.3694 | 9.0233 | 8.2569 | 23.186 | 12.2083 | 8.9058 | 7.794 | 23.3481 | 12.16 | 8.8705 | 7.4331 | 23.5306 | 12.1446 | 8.8593 | 7.1337 | 23.7617 | 11.9714 | 8.733 | 6.0668 | 24.5744 | 11.8276 | 8.6281 | 1.3104 | 25.0804 | 10.8327 | 7.9023 | -2.2443 | 25.2402 | 10.3093 | 7.5205 | -4.0835 | 25.1624 | 10.3131 | 7.5233 | -3.2013
AVENHAM | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 354028 | 429192 | 23.8146 | 15.2543 | 11.1278 | 10.4317 | 23.865 | 15.0462 | 10.976 | 10.2549 | 23.876 | 14.872 | 10.8489 | 10.1388 | 23.9132 | 14.725 | 10.7417 | 9.9009 | 23.9631 | 14.5957 | 10.6474 | 9.8176 | 24.0257 | 14.383 | 10.4922 | 9.7121 | 24.0929 | 14.2534 | 10.3976 | 9.4451 | 24.163 | 14.1807 | 10.3446 | 9.2589 | 24.2362 | 14.1108 | 10.2937 | 9.1337 | 24.3139 | 13.9692 | 10.1903 | 8.8333 | 24.4959 | 13.4761 | 9.8306 | 8.2024 | 24.5853 | 13.1437 | 9.5882 | 7.9666 | 24.6166 | 13.3622 | 9.7475 | 7.8018 | 24.6056 | 13.0793 | 9.5411 | 7.9802 | 23.7911 | 15.3139 | 11.1713 | 10.6401 | 23.829 | 14.9754 | 10.9243 | 10.6239 | 23.8932 | 14.7399 | 10.7526 | 10.3762 | 23.9825 | 14.9006 | 10.8698 | 10.042 | 24.0836 | 14.8666 | 10.8449 | 9.8764 | 24.1793 | 14.8691 | 10.8468 | 9.658 | 24.2654 | 14.7699 | 10.7744 | 9.2181 | 24.3579 | 14.6946 | 10.7195 | 8.8579 | 24.4578 | 14.6066 | 10.6553 | 8.4495 | 24.5652 | 14.5209 | 10.5928 | 8.0478 | 24.6633 | 14.4403 | 10.534 | 7.5689 | 24.7269 | 14.4249 | 10.5228 | 7.4118 | 24.7509 | 14.605 | 10.6542 | 7.2187 | 24.7398 | 14.7306 | 10.7458 | 7.3157 | 23.8146 | 15.3096 | 11.1682 | 10.4377 | 23.865 | 14.9332 | 10.8935 | 10.279 | 23.876 | 14.8099 | 10.8036 | 10.192 | 23.9132 | 14.9573 | 10.9112 | 9.9731 | 23.963 | 14.9553 | 10.9097 | 9.8997 | 24.0253 | 14.8598 | 10.84 | 9.8057 | 24.0923 | 14.7523 | 10.7616 | 9.5612 | 24.1623 | 14.6461 | 10.6841 | 9.39 | 24.2349 | 14.5308 | 10.6 | 9.2807 | 24.3098 | 14.3957 | 10.5015 | 9.0129 | 24.4829 | 14.0806 | 10.2716 | 8.4374 | 24.5643 | 13.9668 | 10.1886 | 8.2377 | 24.5916 | 14.4752 | 10.5595 | 8.0926 | 24.5796 | 14.4062 | 10.5091 | 8.2694 | 23.8099 | 15.2557 | 11.1288 | 10.4447 | 23.8567 | 15.0355 | 10.9682 | 10.2805 | 23.8648 | 14.9303 | 10.8914 | 10.1771 | 23.9052 | 14.7285 | 10.7442 | 9.9478 | 23.9627 | 14.555 | 10.6177 | 9.866 | 24.0375 | 14.366 | 10.4798 | 9.7597 | 24.1227 | 14.2433 | 10.3903 | 9.4844 | 24.2158 | 14.1488 | 10.3214 | 9.288 | 24.3135 | 14.0625 | 10.2584 | 9.1619 | 24.3888 | 13.9345 | 10.165 | 8.8766 | 24.5794 | 13.2626 | 9.6749 | 8.0891 | 24.7377 | 12.7263 | 9.2837 | 6.684 | 24.7472 | 12.6597 | 9.2351 | 5.5316 | 24.6974 | 12.2078 | 8.9055 | 4.996 | 23.7976 | 15.2584 | 11.1308 | 10.4552 | 23.8328 | 15.2248 | 11.1063 | 10.2918 | 23.8278 | 15.0625 | 10.9879 | 10.202 | 23.8515 | 15.0337 | 10.9669 | 9.9974 | 23.8911 | 14.9276 | 10.8895 | 9.9407 | 23.9445 | 14.8274 | 10.8164 | 9.8686 | 24.0077 | 14.6281 | 10.671 | 9.6332 | 24.0746 | 14.5465 | 10.6115 | 9.4835 | 24.146 | 14.4226 | 10.5211 | 9.3967 | 24.2302 | 14.1648 | 10.333 | 8.8814 | 24.4536 | 13.2008 | 9.6298 | 7.0656 | 24.5412 | 12.221 | 8.915 | 5.8225 | 24.4889 | 12.1093 | 8.8336 | 5.0527 | 24.3678 | 11.9808 | 8.7398 | 5.6264
BAGULEY | SALE | CARRINGTON | 380562 | 389035 | 32.6549 | 9.7002 | 6.9717 | 6.5421 | 32.8338 | 8.8575 | 6.3661 | 5.7789 | 32.988 | 8.0827 | 5.8092 | 5.5733 | 33.1462 | 7.3803 | 5.3044 | 5.4827 | 33.3045 | 6.6442 | 4.7753 | 5.2019 | 33.5137 | 5.8208 | 4.1835 | 4.4672 | 33.7498 | 5.7255 | 4.115 | 3.871 | 34.0083 | 5.6481 | 4.0594 | 3.3656 | 33.0602 | 5.4431 | 3.9121 | 2.3063 | 32.0977 | 5.2846 | 3.7982 | 1.6076 | 28.0442 | 4.6173 | 3.3185 | -1.1973 | 27.2252 | 4.4824 | 3.2216 | -3.1242 | 38.733 | 8.0507 | 5.7862 | -3.8182 | 39.501 | 10.2963 | 7.4002 | -4.2304 | 32.5482 | 9.7189 | 6.9851 | 6.7341 | 32.633 | 8.8795 | 6.3818 | 6.1327 | 32.821 | 8.0585 | 5.7918 | 5.8059 | 32.9875 | 7.3359 | 5.2725 | 5.7101 | 33.1605 | 6.56 | 4.7148 | 5.4667 | 33.3562 | 5.6883 | 4.0883 | 4.7879 | 33.575 | 5.5709 | 4.0039 | 4.2393 | 33.2673 | 5.4772 | 3.9366 | 3.8805 | 32.0219 | 5.2722 | 3.7892 | 2.9247 | 31.3084 | 5.1547 | 3.7048 | 2.3184 | 28.8036 | 4.7423 | 3.4084 | 0.27808 | 28.0059 | 4.611 | 3.314 | -1.4891 | 37.1042 | 7.1813 | 5.1613 | -2.4998 | 37.6708 | 9.4909 | 6.8213 | -3.3962 | 32.6612 | 9.7169 | 6.9837 | 6.5679 | 32.8425 | 8.8585 | 6.3667 | 5.8382 | 32.9986 | 8.0418 | 5.7798 | 5.6619 | 33.1551 | 7.2744 | 5.2283 | 5.5863 | 33.314 | 6.4303 | 4.6216 | 5.3285 | 33.3905 | 5.4975 | 3.9511 | 4.622 | 32.5082 | 5.3522 | 3.8468 | 4.0514 | 31.8922 | 5.2508 | 3.7739 | 3.5128 | 30.4793 | 5.0182 | 3.6067 | 2.4919 | 29.5667 | 4.8679 | 3.4987 | 1.861 | 26.6483 | 4.3874 | 3.1533 | -0.6451 | 26.6225 | 4.3832 | 3.1503 | -2.1892 | 38.0007 | 7.987 | 5.7404 | -2.6885 | 38.4545 | 9.9678 | 7.164 | -2.8762 | 32.6517 | 9.704 | 6.9745 | 6.5504 | 32.8222 | 8.8711 | 6.3758 | 5.8008 | 32.9747 | 8.1248 | 5.8395 | 5.6095 | 33.1685 | 7.3986 | 5.3175 | 5.5181 | 33.3756 | 6.6433 | 4.7747 | 5.2621 | 33.672 | 5.8001 | 4.1686 | 4.5437 | 34.0381 | 5.6832 | 4.0847 | 3.928 | 33.7265 | 5.5528 | 3.9909 | 3.4884 | 32.6004 | 5.3674 | 3.8577 | 2.5142 | 31.6254 | 5.2069 | 3.7423 | 1.9507 | 25.666 | 4.2257 | 3.0371 | -1.5755 | 18.4985 | 3.0456 | 2.189 | -8.3469 | 34.2898 | 5.6455 | 4.0576 | -13.2438 | 41.2101 | 7.2009 | 5.1755 | -16.9727 | 32.6716 | 9.7145 | 6.982 | 6.5788 | 32.9086 | 9.6566 | 6.9404 | 5.8096 | 33.056 | 9.6383 | 6.9272 | 5.6168 | 33.1991 | 9.6492 | 6.9351 | 5.5659 | 33.4127 | 9.5987 | 6.8988 | 5.357 | 33.7283 | 9.474 | 6.8092 | 4.7069 | 34.1401 | 9.3404 | 6.7131 | 4.1503 | 34.621 | 9.243 | 6.6431 | 3.706 | 35.1676 | 9.0638 | 6.5143 | 2.7073 | 35.8121 | 8.7562 | 6.2933 | 1.2166 | 38.1437 | 7.9615 | 5.7221 | -6.1094 | 39.339 | 6.4769 | 4.6551 | -12.2194 | 40.4091 | 7.8935 | 5.6732 | -15.5545 | 40.3766 | 7.8005 | 5.6064 | -15.147
BAMBER BRIDGE | RIBBLE | PENWORTHAM EAST / ROCHDALE | 356431 | 426698 | 31.1333 | 12.9203 | 9.2861 | 12.4228 | 31.216 | 12.8036 | 9.2022 | 12.1514 | 31.2362 | 12.7545 | 9.1669 | 11.9046 | 31.2871 | 12.6557 | 9.0959 | 11.5156 | 31.3624 | 12.5951 | 9.0524 | 11.5054 | 31.4603 | 12.4292 | 8.9331 | 11.1079 | 31.5731 | 12.2845 | 8.8291 | 10.7077 | 31.6954 | 12.1089 | 8.7029 | 10.3368 | 31.8286 | 11.96 | 8.5959 | 10.0401 | 31.9875 | 11.7841 | 8.4695 | 9.4532 | 33.0927 | 10.8659 | 7.8095 | 7.6547 | 34.6374 | 10.161 | 7.3029 | 6.4014 | 35.9133 | 9.8018 | 7.0448 | 5.4977 | 37.209 | 9.5091 | 6.8344 | 5.0535 | 31.0635 | 12.9247 | 9.2892 | 12.6417 | 31.0971 | 12.8606 | 9.2432 | 12.5181 | 31.166 | 12.8046 | 9.2029 | 12.2108 | 31.2314 | 12.5522 | 9.0215 | 11.7854 | 31.3084 | 12.541 | 9.0135 | 11.7534 | 31.3972 | 12.5139 | 8.994 | 11.3674 | 31.4986 | 12.4176 | 8.9248 | 10.9669 | 31.6065 | 12.3212 | 8.8555 | 10.5802 | 31.7223 | 12.2185 | 8.7817 | 10.246 | 31.8421 | 12.0778 | 8.6805 | 9.7067 | 32.4932 | 11.5908 | 8.3305 | 8.3533 | 33.2937 | 11.2901 | 8.1144 | 7.3812 | 34.1897 | 11.0013 | 7.9069 | 6.4107 | 34.9721 | 10.673 | 7.6709 | 5.8989 | 31.1338 | 12.9232 | 9.2881 | 12.4303 | 31.2174 | 12.8445 | 9.2316 | 12.1696 | 31.2391 | 12.7655 | 9.1748 | 11.9353 | 31.2918 | 12.5523 | 9.0216 | 11.5592 | 31.3692 | 12.5173 | 8.9965 | 11.5583 | 31.4688 | 12.3429 | 8.8711 | 11.175 | 31.5833 | 12.1461 | 8.7296 | 10.7887 | 31.7073 | 12.0353 | 8.65 | 10.4311 | 31.8409 | 11.9288 | 8.5735 | 10.1521 | 31.9956 | 11.7527 | 8.4469 | 9.61 | 32.9306 | 11.0686 | 7.9552 | 8.023 | 33.9166 | 10.2389 | 7.3589 | 7.1413 | 34.9117 | 9.9626 | 7.1603 | 6.4331 | 35.7666 | 9.7467 | 7.0052 | 6.2589 | 31.1294 | 12.9197 | 9.2856 | 12.4329 | 31.2134 | 12.7957 | 9.1965 | 12.1718 | 31.244 | 12.7366 | 9.154 | 11.9363 | 31.3148 | 12.6268 | 9.0751 | 11.5531 | 31.4168 | 12.5356 | 9.0096 | 11.5611 | 31.5769 | 12.3948 | 8.9084 | 11.1683 | 31.7914 | 12.1961 | 8.7656 | 10.7508 | 32.0488 | 12.0298 | 8.6461 | 10.3533 | 32.3391 | 11.8531 | 8.5191 | 10.0568 | 32.6672 | 11.624 | 8.3544 | 9.5204 | 35.0865 | 10.2713 | 7.3822 | 6.6501 | 37.4012 | 8.6596 | 6.2238 | 1.2436 | 38.8636 | 7.6185 | 5.4755 | -3.3289 | 39.5144 | 6.7993 | 4.8868 | -6.238 | 31.1359 | 12.925 | 9.2894 | 12.4525 | 31.2183 | 12.7851 | 9.1889 | 12.1912 | 31.2602 | 12.7487 | 9.1628 | 11.9721 | 31.3417 | 12.6519 | 9.0932 | 11.6259 | 31.4588 | 12.5847 | 9.0448 | 11.6655 | 31.6571 | 12.3616 | 8.8846 | 11.3061 | 31.9375 | 12.1749 | 8.7503 | 10.9086 | 32.2807 | 11.9877 | 8.6158 | 10.526 | 32.7153 | 11.7697 | 8.4591 | 10.0925 | 33.3645 | 11.3624 | 8.1664 | 8.6998 | 35.9131 | 9.5886 | 6.8915 | 2.598 | 37.9416 | 7.8837 | 5.6662 | -2.326 | 38.8404 | 7.2934 | 5.2419 | -5.4872 | 38.9401 | 7.1274 | 5.1226 | -5.1201
BARBARA ST | BOLTON | KEARSLEY | 370695 | 407609 | 26.2916 | 9.4379 | 6.8848 | 10.5594 | 26.343 | 9.317 | 6.7966 | 10.326 | 26.3576 | 9.1991 | 6.7106 | 10.2698 | 26.4035 | 9.0814 | 6.6248 | 9.9809 | 26.47 | 8.9538 | 6.5317 | 9.8482 | 26.5557 | 8.8157 | 6.4309 | 9.5384 | 26.6535 | 8.6832 | 6.3343 | 9.1959 | 26.7604 | 8.5516 | 6.2383 | 8.8461 | 26.8666 | 8.4325 | 6.1514 | 8.4825 | 26.9816 | 8.2632 | 6.0279 | 8.0526 | 27.5484 | 7.3747 | 5.3798 | 6.4852 | 28.1726 | 7.0003 | 5.1066 | 5.5765 | 28.6177 | 6.8217 | 4.9763 | 5.1286 | 29.0337 | 6.8462 | 4.9942 | 5.1038 | 26.2539 | 9.3934 | 6.8524 | 10.5987 | 26.2798 | 9.2312 | 6.734 | 10.39 | 26.333 | 9.1047 | 6.6418 | 10.2652 | 26.4047 | 9.0598 | 6.609 | 9.9736 | 26.4875 | 8.9514 | 6.5299 | 9.8548 | 26.5751 | 8.8367 | 6.4463 | 9.5574 | 26.6551 | 8.7236 | 6.3637 | 9.2225 | 26.7404 | 8.6712 | 6.3255 | 8.8778 | 26.8309 | 8.5831 | 6.2612 | 8.517 | 26.9256 | 8.484 | 6.189 | 8.1576 | 27.2235 | 8.2127 | 5.9911 | 7.1612 | 27.541 | 7.9431 | 5.7944 | 6.4105 | 27.8562 | 7.5818 | 5.5308 | 5.8105 | 28.1217 | 7.3553 | 5.3656 | 5.4729 | 26.2918 | 9.3891 | 6.8492 | 10.5719 | 26.3434 | 9.2258 | 6.7301 | 10.3513 | 26.3585 | 9.1407 | 6.668 | 10.34 | 26.405 | 9.0159 | 6.577 | 10.0663 | 26.4719 | 8.8919 | 6.4865 | 9.9477 | 26.5578 | 8.7513 | 6.3839 | 9.6198 | 26.6558 | 8.6348 | 6.2989 | 9.3293 | 26.763 | 8.5243 | 6.2184 | 8.9875 | 26.8687 | 8.4124 | 6.1367 | 8.6326 | 26.9791 | 8.2849 | 6.0437 | 8.2473 | 27.4783 | 7.7047 | 5.6205 | 6.8545 | 27.9185 | 7.3638 | 5.3718 | 6.1353 | 28.2943 | 7.0029 | 5.1085 | 5.7707 | 28.5579 | 7.0123 | 5.1154 | 5.8305 | 26.2871 | 9.4358 | 6.8833 | 10.554 | 26.3367 | 9.3014 | 6.7853 | 10.3115 | 26.3577 | 9.2028 | 6.7133 | 10.2556 | 26.4194 | 9.0069 | 6.5704 | 9.9602 | 26.5123 | 8.9036 | 6.4951 | 9.8277 | 26.6425 | 8.7653 | 6.3942 | 9.4554 | 26.8054 | 8.5983 | 6.2723 | 9.1366 | 26.9947 | 8.4522 | 6.1658 | 8.7436 | 27.1775 | 8.302 | 6.0562 | 8.4124 | 27.383 | 8.1244 | 5.9267 | 8.0213 | 28.3253 | 6.9124 | 5.0425 | 5.6283 | 29.3324 | 5.5904 | 4.0781 | 0.10572 | 28.9094 | 4.6894 | 3.4208 | -4.3661 | 25.5673 | 4.1473 | 3.0254 | -7.212 | 26.2758 | 9.444 | 6.8893 | 10.5944 | 26.3236 | 9.35 | 6.8207 | 10.3713 | 26.3455 | 9.2132 | 6.7209 | 10.3122 | 26.4019 | 9.1218 | 6.6542 | 10.0585 | 26.4896 | 9.0192 | 6.5794 | 9.9652 | 26.6173 | 8.7887 | 6.4112 | 9.6701 | 26.7877 | 8.6167 | 6.2858 | 9.3836 | 26.9844 | 8.3989 | 6.1269 | 9.0536 | 27.2012 | 8.1738 | 5.9627 | 8.6316 | 27.4564 | 7.7272 | 5.6369 | 7.2991 | 28.5402 | 6.0577 | 4.419 | 1.1972 | 29.3901 | 5.0268 | 3.667 | -3.7604 | 26.0329 | 4.2228 | 3.0805 | -6.7583 | 26.8767 | 4.3597 | 3.1803 | -5.9754
BARROW | BARROW & SANDGATE | HARKER / HUTTON | 319709 | 470489 | 23.072 | 13.3687 | 9.6083 | 8.6076 | 23.1599 | 13.1349 | 9.4403 | 8.5285 | 23.33 | 12.8878 | 9.2627 | 8.3749 | 23.5313 | 12.7001 | 9.1278 | 8.0914 | 23.7764 | 12.4751 | 8.9661 | 7.8803 | 23.9526 | 12.012 | 8.6332 | 7.5488 | 24.059 | 11.7312 | 8.4315 | 7.0939 | 24.1753 | 11.4919 | 8.2594 | 6.6696 | 24.3035 | 11.245 | 8.082 | 6.2646 | 24.4484 | 10.9494 | 7.8696 | 5.7106 | 25.0512 | 10.2926 | 7.3975 | 3.9348 | 25.5071 | 9.9818 | 7.1741 | 3.0875 | 25.7624 | 10.2417 | 7.3609 | 3.0017 | 25.8979 | 10.6049 | 7.6219 | 3.407 | 23.0656 | 13.4222 | 9.6468 | 8.664 | 23.145 | 13.4064 | 9.6354 | 8.6376 | 23.2937 | 13.351 | 9.5956 | 8.4195 | 23.4367 | 13.2338 | 9.5114 | 8.1582 | 23.596 | 13.1661 | 9.4628 | 8.0249 | 23.7738 | 13.0511 | 9.3801 | 7.7707 | 23.9698 | 12.9349 | 9.2965 | 7.3972 | 24.0857 | 12.8154 | 9.2107 | 7.0564 | 24.1935 | 12.7174 | 9.1402 | 6.7302 | 24.3053 | 12.6068 | 9.0608 | 6.3317 | 24.5602 | 12.2825 | 8.8277 | 5.2763 | 24.7707 | 12.0226 | 8.6409 | 4.6073 | 24.8927 | 12.1782 | 8.7527 | 4.2659 | 24.9448 | 12.4398 | 8.9407 | 4.1977 | 23.0732 | 13.4235 | 9.6477 | 8.6145 | 23.1615 | 13.2275 | 9.5069 | 8.536 | 23.3319 | 12.9676 | 9.32 | 8.4003 | 23.5334 | 12.6394 | 9.0842 | 8.1279 | 23.7769 | 12.358 | 8.8819 | 7.9369 | 23.9522 | 11.8302 | 8.5026 | 7.6195 | 24.0576 | 11.5493 | 8.3007 | 7.1791 | 24.1728 | 11.2883 | 8.1131 | 6.7677 | 24.2983 | 11.0311 | 7.9283 | 6.3841 | 24.4344 | 10.805 | 7.7657 | 5.8871 | 24.9931 | 10.4262 | 7.4935 | 4.2986 | 25.39 | 10.162 | 7.3036 | 3.6021 | 25.6027 | 10.3506 | 7.4392 | 3.5823 | 25.7087 | 10.6365 | 7.6447 | 3.9897 | 23.0735 | 13.3703 | 9.6095 | 8.6117 | 23.1657 | 13.1205 | 9.4299 | 8.5422 | 23.349 | 12.9526 | 9.3093 | 8.3844 | 23.5716 | 12.7228 | 9.1441 | 8.1107 | 23.8498 | 12.4593 | 8.9547 | 7.9711 | 24.0686 | 11.9653 | 8.5997 | 7.6836 | 24.2477 | 11.7102 | 8.4163 | 7.2614 | 24.4541 | 11.4488 | 8.2285 | 6.8795 | 24.6816 | 11.1741 | 8.0311 | 6.5847 | 24.9352 | 10.9309 | 7.8563 | 6.2212 | 25.7894 | 10.0357 | 7.2129 | 3.6034 | 26.5368 | 8.8477 | 6.359 | -1.6808 | 26.9152 | 8.3516 | 6.0025 | -5.8622 | 27.0817 | 8.2135 | 5.9032 | -8.3052 | 23.0902 | 13.3787 | 9.6155 | 8.6484 | 23.2436 | 13.1743 | 9.4686 | 8.5593 | 23.4601 | 12.965 | 9.3182 | 8.4357 | 23.6885 | 12.7725 | 9.1798 | 8.2087 | 23.8996 | 12.4911 | 8.9776 | 8.0473 | 24.032 | 12.0157 | 8.6359 | 7.8242 | 24.1996 | 11.6576 | 8.3785 | 7.4742 | 24.3873 | 11.411 | 8.2013 | 7.1797 | 24.5998 | 11.1572 | 8.0189 | 6.7571 | 24.8643 | 10.7284 | 7.7107 | 5.3569 | 25.7521 | 9.2052 | 6.616 | -0.92992 | 26.2963 | 8.1323 | 5.8448 | -5.7449 | 26.4484 | 8.3045 | 5.9686 | -8.2952 | 26.3038 | 8.435 | 6.0624 | -6.8613
BARTON DOCK RD | BARTON | CARRINGTON | 378864 | 395534 | 22.8174 | 11.8815 | 8.6674 | 7.9774 | 22.9204 | 11.5632 | 8.4352 | 7.633 | 22.9249 | 11.3548 | 8.2831 | 7.6071 | 22.9591 | 11.1718 | 8.1497 | 7.7381 | 23.0102 | 10.917 | 7.9638 | 7.6716 | 23.0833 | 10.7204 | 7.8204 | 7.4332 | 23.1619 | 10.6462 | 7.7663 | 7.323 | 23.2447 | 10.5802 | 7.7181 | 7.2404 | 23.3307 | 10.4801 | 7.6451 | 6.8927 | 23.4237 | 10.3869 | 7.5771 | 6.7368 | 25.9715 | 9.476 | 6.9126 | 3.9763 | 27.3016 | 9.6365 | 7.0297 | 2.5428 | 28.1373 | 9.7772 | 7.1323 | 1.3572 | 28.6905 | 9.6818 | 7.0627 | 0.3841 | 22.708 | 11.772 | 8.5875 | 8.2716 | 22.7186 | 11.504 | 8.392 | 8.1735 | 22.7624 | 11.3367 | 8.27 | 8.04 | 22.8223 | 10.9364 | 7.978 | 8.0917 | 22.8875 | 10.7898 | 7.871 | 7.9997 | 22.9608 | 10.6808 | 7.7915 | 7.7307 | 23.0414 | 10.6514 | 7.77 | 7.5977 | 23.1261 | 10.6405 | 7.7621 | 7.532 | 23.2146 | 10.5704 | 7.7109 | 7.119 | 23.3049 | 10.5383 | 7.6875 | 6.9904 | 23.8379 | 10.4103 | 7.5942 | 6.3299 | 24.5193 | 10.3468 | 7.5478 | 5.5207 | 25.3172 | 10.4563 | 7.6277 | 4.501 | 26.0379 | 10.5126 | 7.6688 | 3.891 | 22.8178 | 11.769 | 8.5853 | 7.9817 | 22.9218 | 11.5052 | 8.3929 | 7.6346 | 22.9277 | 11.3151 | 8.2542 | 7.6212 | 22.9637 | 10.8623 | 7.9239 | 7.7432 | 23.0169 | 10.7831 | 7.8661 | 7.6516 | 23.0918 | 10.6645 | 7.7796 | 7.4351 | 23.1722 | 10.6296 | 7.7541 | 7.3171 | 23.2567 | 10.5959 | 7.7295 | 7.2363 | 23.3435 | 10.5017 | 7.6608 | 6.8943 | 23.4345 | 10.4687 | 7.6367 | 6.7501 | 25.8282 | 10.2912 | 7.5073 | 4.1637 | 26.6268 | 10.3549 | 7.5537 | 3.2528 | 27.4221 | 10.7576 | 7.8475 | 2.3341 | 27.7251 | 10.8298 | 7.9002 | 1.8523 | 22.8114 | 11.8836 | 8.6689 | 7.9967 | 22.909 | 11.5644 | 8.4361 | 7.6724 | 22.9095 | 11.3535 | 8.2822 | 7.6645 | 22.9416 | 11.1381 | 8.1251 | 7.8098 | 22.9929 | 10.9257 | 7.9702 | 7.7563 | 23.0887 | 10.729 | 7.8266 | 7.5121 | 23.213 | 10.628 | 7.753 | 7.3619 | 23.3634 | 10.5631 | 7.7056 | 7.2271 | 23.5374 | 10.4423 | 7.6175 | 6.8137 | 23.7347 | 10.3331 | 7.5378 | 6.5866 | 27.1905 | 9.3291 | 6.8054 | 2.6645 | 29.2743 | 8.9481 | 6.5275 | -1.1299 | 30.1232 | 8.8567 | 6.4608 | -3.537 | 30.2537 | 8.7151 | 6.3575 | -4.4939 | 22.8195 | 11.8824 | 8.668 | 7.9879 | 22.9309 | 11.7437 | 8.5669 | 7.6457 | 22.9461 | 11.6385 | 8.4901 | 7.6265 | 22.9937 | 11.5476 | 8.4238 | 7.7579 | 23.0632 | 11.4092 | 8.3229 | 7.6769 | 23.2029 | 11.2585 | 8.213 | 7.4056 | 23.3995 | 11.1419 | 8.1278 | 7.194 | 23.8757 | 11.0238 | 8.0417 | 6.7527 | 25.182 | 10.7245 | 7.8234 | 5.1809 | 26.5788 | 10.3804 | 7.5723 | 3.5967 | 28.5861 | 9.5073 | 6.9355 | -0.040208 | 29.7269 | 9.027 | 6.5851 | -2.7617 | 30.2464 | 8.7385 | 6.3746 | -4.4468 | 30.0305 | 8.6526 | 6.3119 | -4.0962
BEDFORD | ATHERTON | KEARSLEY | 366258 | 399876 | 28.7771 | 10.389 | 7.4668 | 9.7864 | 28.8757 | 10.2265 | 7.35 | 9.2932 | 28.9306 | 10.2274 | 7.3506 | 9.0593 | 29.0207 | 10.1864 | 7.3212 | 8.8112 | 29.1433 | 10.0089 | 7.1936 | 8.2893 | 29.2957 | 9.8133 | 7.053 | 7.7581 | 29.4713 | 9.6155 | 6.9109 | 7.3392 | 29.6641 | 9.3522 | 6.7216 | 6.85 | 29.87 | 9.1284 | 6.5608 | 6.2536 | 30.107 | 9.0635 | 6.5141 | 5.6859 | 31.3066 | 8.2065 | 5.8982 | 2.8267 | 32.5561 | 7.6397 | 5.4908 | 1.0897 | 33.4688 | 7.8745 | 5.6596 | 0.28578 | 34.2176 | 8.4895 | 6.1016 | 0.20935 | 28.7262 | 10.469 | 7.5243 | 10.076 | 28.7812 | 10.3911 | 7.4683 | 9.7949 | 28.8714 | 10.2718 | 7.3825 | 9.3652 | 28.9734 | 10.1585 | 7.3011 | 8.9937 | 29.092 | 10.0028 | 7.1892 | 8.3886 | 29.2265 | 9.8366 | 7.0698 | 7.7981 | 29.3783 | 9.7424 | 7.0021 | 7.2977 | 29.5423 | 9.6127 | 6.9088 | 6.7015 | 29.718 | 9.4291 | 6.7769 | 5.8485 | 29.9026 | 9.1649 | 6.587 | 4.5254 | 30.5123 | 8.7005 | 6.2532 | 3.2129 | 31.1376 | 8.4981 | 6.1078 | 2.4207 | 31.7201 | 9.0458 | 6.5014 | 1.7923 | 32.207 | 9.6058 | 6.9039 | 1.6757 | 28.7783 | 10.4718 | 7.5263 | 9.805 | 28.8778 | 10.4524 | 7.5123 | 9.3337 | 28.933 | 10.3027 | 7.4048 | 9.1222 | 29.024 | 10.026 | 7.2059 | 8.8946 | 29.1473 | 9.7499 | 7.0075 | 8.4008 | 29.2995 | 9.6828 | 6.9592 | 7.8983 | 29.4747 | 9.5703 | 6.8784 | 7.5049 | 29.6669 | 9.4164 | 6.7677 | 7.0432 | 29.87 | 9.1948 | 6.6085 | 6.485 | 30.0955 | 8.8844 | 6.3854 | 5.9772 | 31.1659 | 8.3493 | 6.0008 | 3.2639 | 32.0835 | 7.8719 | 5.6577 | 1.9141 | 32.8137 | 8.3767 | 6.0205 | 1.3113 | 33.3756 | 8.8223 | 6.3407 | 1.4314 | 28.7743 | 10.3899 | 7.4674 | 9.8134 | 28.8764 | 10.2641 | 7.377 | 9.348 | 28.9451 | 10.2698 | 7.3811 | 9.1484 | 29.064 | 10.2003 | 7.3311 | 8.9463 | 29.2325 | 10.0022 | 7.1888 | 8.4802 | 29.4639 | 9.7705 | 7.0222 | 7.9996 | 29.7594 | 9.4923 | 6.8223 | 7.619 | 30.1059 | 9.3159 | 6.6955 | 7.1687 | 30.4897 | 9.2276 | 6.632 | 6.629 | 30.9217 | 9.0643 | 6.5147 | 6.0298 | 32.99 | 7.8751 | 5.66 | 2.4424 | 35.1742 | 6.0909 | 4.3776 | -4.0807 | 33.3149 | 5.485 | 3.9422 | -9.1577 | 32.4325 | 5.3398 | 3.8378 | -12.3952 | 28.7727 | 10.3944 | 7.4707 | 9.8269 | 28.8821 | 10.427 | 7.4941 | 9.339 | 28.9626 | 10.4111 | 7.4827 | 9.1484 | 29.086 | 10.1749 | 7.3129 | 8.9853 | 29.2612 | 9.906 | 7.1196 | 8.5629 | 29.5026 | 9.9022 | 7.1169 | 8.1446 | 29.8212 | 9.7891 | 7.0356 | 7.819 | 30.1908 | 9.6381 | 6.9271 | 7.4392 | 30.6208 | 9.4119 | 6.7645 | 6.8771 | 31.1982 | 9.0289 | 6.4892 | 5.2756 | 33.6451 | 7.0023 | 5.0327 | -2.1799 | 32.4284 | 5.3391 | 3.8373 | -7.9229 | 34.8974 | 5.7456 | 4.1295 | -11.2749 | 34.6197 | 5.6999 | 4.0966 | -10.2532
BELGRAVE | GREENHILL | WHITEGATE | 393008 | 403366 | 16.5103 | 13.6111 | 9.9291 | 11.3444 | 16.5647 | 11.2473 | 8.2047 | 11.112 | 16.591 | 8.8886 | 6.4841 | 11.0942 | 16.6346 | 6.472 | 4.7212 | 10.9523 | 16.6967 | 4.0819 | 2.9777 | 10.7895 | 13.7743 | 2.2343 | 1.6299 | 10.5449 | 13.3346 | 2.163 | 1.5779 | 10.3076 | 12.8441 | 2.0834 | 1.5198 | 9.9877 | 11.956 | 1.9394 | 1.4148 | 9.651 | 11.6533 | 1.8903 | 1.3789 | 9.2836 | 12.303 | 1.9957 | 1.4558 | 7.9772 | 17.9376 | 5.2497 | 3.8296 | 7.2769 | 18.1602 | 11.0787 | 8.0818 | 7.051 | 18.3071 | 12.1049 | 8.8303 | 7.0876 | 16.4651 | 13.5791 | 9.9058 | 11.5157 | 16.4894 | 11.1683 | 8.1472 | 11.4205 | 16.5371 | 8.7586 | 6.3892 | 11.2923 | 16.5947 | 6.2754 | 4.5778 | 11.0566 | 16.6604 | 3.8744 | 2.8263 | 10.9271 | 12.3628 | 2.0054 | 1.4629 | 10.6805 | 11.9505 | 1.9385 | 1.4141 | 10.4398 | 11.504 | 1.8661 | 1.3613 | 10.1511 | 11.0237 | 1.7882 | 1.3044 | 9.8397 | 10.5415 | 1.7099 | 1.2474 | 9.5314 | 10.8459 | 1.7593 | 1.2834 | 8.6172 | 17.4666 | 3.8721 | 2.8246 | 7.9439 | 17.5941 | 7.6681 | 5.5938 | 7.5249 | 17.68 | 8.7749 | 6.4012 | 7.2304 | 16.5104 | 13.5788 | 9.9056 | 11.3522 | 16.5648 | 11.1785 | 8.1545 | 11.1264 | 16.591 | 8.6674 | 6.3227 | 11.1145 | 16.6348 | 6.2123 | 4.5318 | 10.975 | 16.6967 | 3.8161 | 2.7838 | 10.8201 | 10.9172 | 1.7709 | 1.2918 | 10.5851 | 10.7914 | 1.7505 | 1.2769 | 10.3562 | 10.4752 | 1.6992 | 1.2395 | 10.0523 | 10.049 | 1.6301 | 1.1891 | 9.7193 | 9.5589 | 1.5505 | 1.1311 | 9.4204 | 10.6241 | 1.7233 | 1.2572 | 8.245 | 17.8646 | 5.1351 | 3.746 | 7.6382 | 18.0675 | 11.2218 | 8.1861 | 7.4291 | 18.2076 | 12.3243 | 8.9904 | 7.4494 | 16.5062 | 13.6137 | 9.931 | 11.3598 | 16.5645 | 11.2595 | 8.2137 | 11.1456 | 16.5909 | 8.882 | 6.4793 | 11.1499 | 16.6475 | 6.4702 | 4.7199 | 11.0148 | 16.7315 | 4.0747 | 2.9725 | 10.874 | 13.6234 | 2.2099 | 1.6121 | 10.5964 | 13.1037 | 2.1255 | 1.5506 | 10.2976 | 12.2933 | 1.9941 | 1.4547 | 9.956 | 11.9086 | 1.9317 | 1.4091 | 9.6496 | 11.2296 | 1.8216 | 1.3288 | 9.3581 | 10.5958 | 1.7187 | 1.2538 | 7.5022 | 18.6423 | 4.2319 | 3.0871 | 3.4358 | 18.9804 | 9.3857 | 6.8467 | 0.22051 | 19.1757 | 9.9785 | 7.2791 | -2.0502 | 16.4985 | 13.6184 | 9.9344 | 11.3692 | 16.5548 | 13.1157 | 9.5677 | 11.1512 | 16.5825 | 12.6098 | 9.1987 | 11.1638 | 16.6332 | 12.0532 | 8.7926 | 11.0766 | 16.7106 | 11.4347 | 8.3414 | 10.9783 | 16.8097 | 11.3396 | 8.2721 | 10.7542 | 16.9308 | 11.2639 | 8.2169 | 10.5089 | 17.0637 | 11.2204 | 8.1851 | 10.2315 | 17.2132 | 11.1736 | 8.151 | 9.877 | 17.4078 | 10.9761 | 8.0069 | 8.9109 | 18.0736 | 12.0747 | 8.8083 | 4.3744 | 18.4881 | 11.0344 | 8.0495 | 0.73281 | 18.6459 | 10.3829 | 7.5742 | -1.4028 | 18.5908 | 10.2704 | 7.4921 | -0.88853
BENCHILL | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 15.0871 | 15.0871 | 15.0871 | 9.8252 | 15.1056 | 15.1056 | 15.1056 | 9.7769 | 15.122 | 15.122 | 15.122 | 9.7068 | 15.1436 | 15.1436 | 15.1436 | 9.6498 | 15.1758 | 15.1758 | 15.1758 | 9.5444 | 15.2129 | 15.2129 | 15.2129 | 9.4224 | 15.2539 | 15.2539 | 15.2539 | 9.2917 | 15.2964 | 15.2964 | 15.2964 | 9.1558 | 15.3368 | 15.3368 | 15.3368 | 9.0204 | 15.3817 | 15.3817 | 15.3817 | 8.8589 | 15.5646 | 15.5646 | 15.5646 | 8.231 | 15.6938 | 15.6938 | 15.6938 | 7.9259 | 15.7625 | 15.7625 | 15.7625 | 7.8629 | 15.8001 | 15.8001 | 15.8001 | 7.9088 | 15.0827 | 15.0827 | 15.0827 | 9.8504 | 15.0974 | 15.0974 | 15.0974 | 9.8215 | 15.1182 | 15.1182 | 15.1182 | 9.7324 | 15.135 | 15.135 | 15.135 | 9.6797 | 15.1609 | 15.1609 | 15.1609 | 9.5849 | 15.1903 | 15.1903 | 15.1903 | 9.4758 | 15.2222 | 15.2222 | 15.2222 | 9.3582 | 15.2558 | 15.2558 | 15.2558 | 9.2362 | 15.2908 | 15.2908 | 15.2908 | 9.1128 | 15.3271 | 15.3271 | 15.3271 | 8.9826 | 15.4192 | 15.4192 | 15.4192 | 8.5326 | 15.4823 | 15.4823 | 15.4823 | 8.2335 | 15.5193 | 15.5193 | 15.5193 | 8.0784 | 15.541 | 15.541 | 15.541 | 7.9702 | 15.0871 | 15.0871 | 15.0871 | 9.8322 | 15.1056 | 15.1056 | 15.1056 | 9.7875 | 15.122 | 15.122 | 15.122 | 9.7214 | 15.1436 | 15.1436 | 15.1436 | 9.6672 | 15.1757 | 15.1757 | 15.1757 | 9.5658 | 15.2127 | 15.2127 | 15.2127 | 9.4481 | 15.2535 | 15.2535 | 15.2535 | 9.3217 | 15.2959 | 15.2959 | 15.2959 | 9.1899 | 15.3357 | 15.3357 | 15.3357 | 9.0606 | 15.3784 | 15.3784 | 15.3784 | 8.914 | 15.5507 | 15.5507 | 15.5507 | 8.3629 | 15.6708 | 15.6708 | 15.6708 | 8.098 | 15.7399 | 15.7399 | 15.7399 | 8.0407 | 15.7762 | 15.7762 | 15.7762 | 8.0562 | 15.0888 | 15.0888 | 15.0888 | 9.8249 | 15.1117 | 15.1117 | 15.1117 | 9.7757 | 15.1384 | 15.1384 | 15.1384 | 9.7014 | 15.1767 | 15.1767 | 15.1767 | 9.6351 | 15.2104 | 15.2104 | 15.2104 | 9.5262 | 15.2546 | 15.2546 | 15.2546 | 9.3972 | 15.3081 | 15.3081 | 15.3081 | 9.2495 | 15.3694 | 15.3694 | 15.3694 | 9.0914 | 15.4367 | 15.4367 | 15.4367 | 8.9587 | 15.512 | 15.512 | 15.512 | 8.8157 | 15.7595 | 15.7595 | 15.7595 | 8.1035 | 15.9584 | 15.9584 | 15.9584 | 6.7484 | 16.0636 | 16.0636 | 16.0636 | 5.7242 | 16.1272 | 16.1272 | 16.1272 | 4.9091 | 15.0857 | 15.0857 | 15.0857 | 9.8295 | 15.1083 | 15.1083 | 15.1083 | 9.7759 | 15.1356 | 15.1356 | 15.1356 | 9.7038 | 15.1743 | 15.1743 | 15.1743 | 9.6481 | 15.2072 | 15.2072 | 15.2072 | 9.5528 | 15.2472 | 15.2472 | 15.2472 | 9.4432 | 15.2972 | 15.2972 | 15.2972 | 9.3142 | 15.3525 | 15.3525 | 15.3525 | 9.1787 | 15.4128 | 15.4128 | 15.4128 | 9.0516 | 15.4901 | 15.4901 | 15.4901 | 8.7092 | 15.7408 | 15.7408 | 15.7408 | 7.1221 | 15.8815 | 15.8815 | 15.8815 | 5.9073 | 15.9229 | 15.9229 | 15.9229 | 5.2049 | 15.8954 | 15.8954 | 15.8954 | 5.3328
BENTHAM | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 366887 | 470130 | 6.7855 | 6.7855 | 6.7855 | 5.2493 | 6.8146 | 6.8146 | 6.8146 | 5.0464 | 6.8298 | 6.8298 | 6.8298 | 5.0396 | 6.8523 | 6.8523 | 6.8523 | 4.9142 | 6.8796 | 6.8796 | 6.8796 | 4.863 | 6.913 | 6.913 | 6.913 | 4.7075 | 6.9508 | 6.9508 | 6.9508 | 4.5547 | 6.9917 | 6.9917 | 6.9917 | 4.4673 | 7.0348 | 7.0348 | 7.0348 | 4.316 | 7.0843 | 7.0843 | 7.0843 | 4.0972 | 7.2273 | 7.2273 | 7.2273 | 3.3692 | 7.319 | 7.319 | 7.319 | 2.9565 | 7.3652 | 7.3652 | 7.3652 | 2.7722 | 7.381 | 7.381 | 7.381 | 2.8826 | 6.778 | 6.778 | 6.778 | 5.3488 | 6.8041 | 6.8041 | 6.8041 | 5.2253 | 6.8399 | 6.8399 | 6.8399 | 5.1772 | 6.8804 | 6.8804 | 6.8804 | 5.0517 | 6.9258 | 6.9258 | 6.9258 | 4.9944 | 6.977 | 6.977 | 6.977 | 4.8447 | 7.0347 | 7.0347 | 7.0347 | 4.6897 | 7.0984 | 7.0984 | 7.0984 | 4.5779 | 7.1621 | 7.1621 | 7.1621 | 4.4238 | 7.2297 | 7.2297 | 7.2297 | 4.2202 | 7.2935 | 7.2935 | 7.2935 | 3.8354 | 7.3456 | 7.3456 | 7.3456 | 3.3975 | 7.377 | 7.377 | 7.377 | 3.0536 | 7.3912 | 7.3912 | 7.3912 | 2.8649 | 6.7855 | 6.7855 | 6.7855 | 5.2072 | 6.8146 | 6.8146 | 6.8146 | 5.0592 | 6.8298 | 6.8298 | 6.8298 | 5.0607 | 6.8523 | 6.8523 | 6.8523 | 4.9446 | 6.8795 | 6.8795 | 6.8795 | 4.9005 | 6.9128 | 6.9128 | 6.9128 | 4.7535 | 6.9505 | 6.9505 | 6.9505 | 4.6086 | 6.9913 | 6.9913 | 6.9913 | 4.5275 | 7.0339 | 7.0339 | 7.0339 | 4.3874 | 7.0817 | 7.0817 | 7.0817 | 4.1914 | 7.2181 | 7.2181 | 7.2181 | 3.5412 | 7.3038 | 7.3038 | 7.3038 | 3.1832 | 7.347 | 7.347 | 7.347 | 3.0333 | 7.3619 | 7.3619 | 7.3619 | 3.1428 | 6.7841 | 6.7841 | 6.7841 | 5.2577 | 6.8134 | 6.8134 | 6.8134 | 5.0482 | 6.8309 | 6.8309 | 6.8309 | 5.0332 | 6.8574 | 6.8574 | 6.8574 | 4.8997 | 6.8919 | 6.8919 | 6.8919 | 4.8294 | 6.9362 | 6.9362 | 6.9362 | 4.6451 | 6.9901 | 6.9901 | 6.9901 | 4.4483 | 7.0511 | 7.0511 | 7.0511 | 4.3169 | 7.1082 | 7.1082 | 7.1082 | 4.1465 | 7.1683 | 7.1683 | 7.1683 | 3.9627 | 7.3398 | 7.3398 | 7.3398 | 3.2063 | 7.4639 | 7.4639 | 7.4639 | 2.0472 | 7.5134 | 7.5134 | 7.5134 | 1.3208 | 7.5344 | 7.5344 | 7.5344 | 0.81941 | 6.7793 | 6.7793 | 6.7793 | 5.2586 | 6.8057 | 6.8057 | 6.8057 | 5.0423 | 6.8189 | 6.8189 | 6.8189 | 5.031 | 6.8397 | 6.8397 | 6.8397 | 4.9018 | 6.8682 | 6.8682 | 6.8682 | 4.8293 | 6.9044 | 6.9044 | 6.9044 | 4.6543 | 6.95 | 6.95 | 6.95 | 4.4796 | 7 | 7 | 7 | 4.3775 | 7.0511 | 7.0511 | 7.0511 | 4.2281 | 7.1054 | 7.1054 | 7.1054 | 3.8933 | 7.2779 | 7.2779 | 7.2779 | 2.4504 | 7.3617 | 7.3617 | 7.3617 | 1.4726 | 7.371 | 7.371 | 7.371 | 1.0086 | 7.3376 | 7.3376 | 7.3376 | 1.2513
BISPHAM | BISPHAM | PENWORTHAM WEST / STANAH | 331655 | 439667 | 32.7688 | 10.8446 | 7.911 | 9.899 | 32.8077 | 10.3615 | 7.5586 | 9.7759 | 32.8236 | 9.8425 | 7.18 | 9.5751 | 32.8955 | 9.2553 | 6.7516 | 9.2175 | 32.9891 | 8.9618 | 6.5375 | 8.8944 | 33.1089 | 8.6847 | 6.3354 | 8.5027 | 33.2473 | 8.53 | 6.2225 | 8.0127 | 33.4002 | 8.3735 | 6.1084 | 7.5192 | 33.5669 | 8.2053 | 5.9857 | 7.0167 | 33.7349 | 8.0198 | 5.8503 | 6.3879 | 34.308 | 7.4196 | 5.4125 | 4.4632 | 34.7106 | 7.3674 | 5.3744 | 3.5736 | 34.9328 | 8.4662 | 6.176 | 3.4991 | 35.0288 | 8.8225 | 6.4359 | 3.9694 | 32.7496 | 10.7275 | 7.8255 | 9.9241 | 32.7818 | 10.2005 | 7.4411 | 9.8115 | 32.8554 | 9.6818 | 7.0627 | 9.5179 | 32.9669 | 9.3108 | 6.7921 | 9.1664 | 33.0737 | 8.9272 | 6.5122 | 8.8736 | 33.1907 | 8.682 | 6.3334 | 8.501 | 33.3235 | 8.553 | 6.2393 | 8.0198 | 33.4681 | 8.4176 | 6.1405 | 7.5278 | 33.625 | 8.2671 | 6.0307 | 7.0138 | 33.7918 | 8.1597 | 5.9524 | 6.4553 | 34.0857 | 7.9835 | 5.8238 | 5.2087 | 34.2847 | 7.9439 | 5.795 | 4.2549 | 34.3962 | 8.6227 | 6.2901 | 3.7239 | 34.4465 | 9.1831 | 6.6989 | 3.4457 | 32.7688 | 10.724 | 7.823 | 9.9136 | 32.8077 | 10.1817 | 7.4274 | 9.821 | 32.8236 | 9.6961 | 7.0732 | 9.6525 | 32.8955 | 9.256 | 6.7521 | 9.3198 | 32.9886 | 8.8404 | 6.4489 | 9.0214 | 33.1077 | 8.656 | 6.3144 | 8.654 | 33.2453 | 8.5259 | 6.2195 | 8.1882 | 33.3978 | 8.4033 | 6.1301 | 7.7178 | 33.5622 | 8.2724 | 6.0346 | 7.2485 | 33.7232 | 8.1284 | 5.9295 | 6.6911 | 34.2594 | 7.7237 | 5.6343 | 4.9869 | 34.6305 | 7.7704 | 5.6684 | 4.2424 | 34.8358 | 8.9898 | 6.5579 | 4.22 | 34.9259 | 9.1869 | 6.7017 | 4.6746 | 32.7631 | 10.8439 | 7.9105 | 9.9053 | 32.8006 | 10.3569 | 7.5552 | 9.7882 | 32.8295 | 9.79 | 7.1417 | 9.6064 | 32.9164 | 9.3432 | 6.8157 | 9.2705 | 33.0494 | 8.9476 | 6.5272 | 8.9748 | 33.2259 | 8.6468 | 6.3077 | 8.5997 | 33.4431 | 8.4637 | 6.1741 | 8.0897 | 33.6933 | 8.2364 | 6.0083 | 7.5837 | 33.9306 | 8.1693 | 5.9594 | 7.1487 | 34.1909 | 8.0428 | 5.8671 | 6.6866 | 35.0931 | 7.2168 | 5.2646 | 3.9285 | 35.9994 | 6.0885 | 4.4415 | -2.4702 | 36.3015 | 6.1625 | 4.4955 | -7.3135 | 35.4237 | 5.7461 | 4.1917 | -10.584 | 32.7422 | 10.8531 | 7.9172 | 9.9507 | 32.7747 | 10.5182 | 7.6728 | 9.836 | 32.79 | 10.081 | 7.354 | 9.6745 | 32.8556 | 9.5973 | 7.0011 | 9.4011 | 32.9686 | 9.3589 | 6.8272 | 9.1399 | 33.1146 | 9.1449 | 6.6711 | 8.8382 | 33.3017 | 8.9721 | 6.545 | 8.4288 | 33.5102 | 8.785 | 6.4085 | 8.0405 | 33.7489 | 8.6094 | 6.2804 | 7.5555 | 34.0589 | 8.3039 | 6.0576 | 5.9845 | 35.0168 | 7.459 | 5.4412 | -1.1908 | 35.5513 | 5.9253 | 4.3224 | -6.9636 | 34.7456 | 5.6361 | 4.1114 | -10.0988 | 35.3088 | 5.7274 | 4.1781 | -8.8145
BLACKBULL | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353041 | 433005 | 31.0736 | 13.425 | 9.7934 | 12.0131 | 31.1482 | 13.2069 | 9.6343 | 10.8943 | 31.1615 | 13.095 | 9.5526 | 10.6619 | 31.2183 | 12.9271 | 9.4301 | 10.342 | 31.302 | 12.7143 | 9.2749 | 9.9617 | 31.4104 | 12.1643 | 8.8737 | 9.4984 | 31.531 | 12.2862 | 8.9626 | 9.034 | 31.6561 | 12.2354 | 8.9255 | 8.6497 | 31.7855 | 12.0683 | 8.8036 | 8.0959 | 31.9319 | 11.7934 | 8.6031 | 7.4848 | 32.698 | 11.0961 | 8.0945 | 5.5809 | 33.5269 | 11.0695 | 8.075 | 4.6187 | 34.1406 | 11.1985 | 8.1691 | 4.3673 | 34.6863 | 11.2193 | 8.1844 | 4.5199 | 30.9981 | 13.5037 | 9.8507 | 12.5186 | 31.0101 | 13.339 | 9.7306 | 11.8807 | 31.0578 | 13.231 | 9.6518 | 11.7136 | 31.1266 | 12.9902 | 9.4762 | 11.4109 | 31.2073 | 12.8522 | 9.3755 | 11.0868 | 31.2983 | 12.9355 | 9.4363 | 10.6989 | 31.3989 | 12.9292 | 9.4316 | 10.3062 | 31.5045 | 12.8965 | 9.4078 | 9.9866 | 31.6159 | 12.8125 | 9.3465 | 9.4897 | 31.7304 | 12.7245 | 9.2824 | 9.0193 | 32.1431 | 12.3303 | 8.9948 | 7.7355 | 32.5693 | 11.9574 | 8.7227 | 6.8425 | 32.9872 | 12.1037 | 8.8295 | 6.2386 | 33.3302 | 12.3536 | 9.0118 | 5.8864 | 31.0738 | 13.4921 | 9.8423 | 12.0168 | 31.1488 | 13.1643 | 9.6031 | 10.9032 | 31.1626 | 13.1167 | 9.5684 | 10.6735 | 31.2202 | 13.217 | 9.6417 | 10.3578 | 31.3043 | 13.15 | 9.5928 | 9.9839 | 31.413 | 13.0185 | 9.4968 | 9.5286 | 31.5338 | 12.8685 | 9.3874 | 9.0715 | 31.6598 | 12.7003 | 9.2647 | 8.6931 | 31.7883 | 12.4388 | 9.0739 | 8.153 | 31.9283 | 12.3265 | 8.992 | 7.5799 | 32.6018 | 11.9346 | 8.7061 | 5.8216 | 33.1792 | 11.8848 | 8.6698 | 5.0409 | 33.6719 | 12.0112 | 8.762 | 4.8522 | 34.0355 | 12.1243 | 8.8445 | 5.105 | 31.0668 | 13.4268 | 9.7946 | 12.0351 | 31.1383 | 13.2018 | 9.6305 | 10.9448 | 31.1565 | 13.0637 | 9.5298 | 10.7546 | 31.2259 | 12.8437 | 9.3693 | 10.4921 | 31.3305 | 12.611 | 9.1995 | 10.1892 | 31.4814 | 12.3588 | 9.0156 | 9.8104 | 31.6698 | 12.3498 | 9.009 | 9.421 | 31.8874 | 12.2245 | 8.9176 | 9.1176 | 32.1257 | 11.9808 | 8.7398 | 8.6929 | 32.3934 | 11.7296 | 8.5566 | 8.2964 | 33.7563 | 11.2457 | 8.2036 | 6.3355 | 34.9883 | 10.2816 | 7.5003 | 2.2853 | 35.6799 | 9.7471 | 7.1103 | -0.84705 | 35.9588 | 9.3818 | 6.8439 | -2.7233 | 31.0648 | 13.4239 | 9.7925 | 12.0083 | 31.1448 | 13.1727 | 9.6093 | 10.8585 | 31.1691 | 12.9865 | 9.4735 | 10.6642 | 31.2399 | 12.6142 | 9.2019 | 10.4266 | 31.3483 | 12.5616 | 9.1635 | 10.1463 | 31.506 | 12.559 | 9.1616 | 9.8113 | 31.7097 | 12.3818 | 9.0323 | 9.466 | 31.9443 | 12.1783 | 8.8839 | 9.2205 | 32.2218 | 11.8039 | 8.6107 | 8.7814 | 32.6171 | 11.7356 | 8.561 | 7.895 | 34.0413 | 10.8634 | 7.9247 | 3.618 | 35.0283 | 9.9264 | 7.2412 | -0.082303 | 35.3718 | 9.8929 | 7.2167 | -2.0906 | 35.2873 | 9.7799 | 7.1343 | -1.23
BLACKBURN | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 370584 | 429294 | 31.2705 | 10.3352 | 7.5394 | 13.9385 | 31.3451 | 9.6166 | 7.0152 | 13.3166 | 31.3488 | 9.199 | 6.7106 | 13.1927 | 31.3777 | 8.7107 | 6.3543 | 13.1964 | 31.4228 | 8.2636 | 6.0282 | 12.9101 | 31.4853 | 7.9007 | 5.7634 | 12.6268 | 31.5539 | 7.7968 | 5.6877 | 12.4461 | 31.6267 | 7.7724 | 5.6699 | 12.3913 | 31.7026 | 7.6816 | 5.6036 | 12.1269 | 31.7871 | 7.5772 | 5.5275 | 11.9064 | 32.3015 | 7.2745 | 5.3066 | 11.2431 | 33.0004 | 6.9949 | 5.1027 | 10.5212 | 33.5248 | 8.2902 | 6.0476 | 10.2512 | 34.0861 | 8.1497 | 5.9451 | 9.9818 | 31.1849 | 10.417 | 7.599 | 14.4528 | 31.1964 | 9.8047 | 7.1524 | 14.2615 | 31.2394 | 9.2599 | 6.755 | 14.0352 | 31.2943 | 8.7907 | 6.4127 | 13.9284 | 31.3575 | 8.3281 | 6.0752 | 13.5772 | 31.4275 | 7.8844 | 5.7515 | 13.2651 | 31.5057 | 7.8236 | 5.7072 | 13.0349 | 31.5896 | 7.7732 | 5.6705 | 12.9142 | 31.6796 | 7.6776 | 5.6007 | 12.5714 | 31.7744 | 7.5854 | 5.5335 | 12.2781 | 32.0727 | 7.4235 | 5.4153 | 11.8466 | 32.4327 | 7.2814 | 5.3117 | 11.3141 | 32.8141 | 7.7393 | 5.6457 | 11.0427 | 33.1305 | 8.4909 | 6.194 | 10.8725 | 31.2707 | 10.418 | 7.5998 | 13.9445 | 31.3457 | 9.8257 | 7.1677 | 13.3304 | 31.3501 | 9.2587 | 6.7541 | 13.214 | 31.38 | 8.707 | 6.3517 | 13.2243 | 31.426 | 8.1437 | 5.9407 | 12.9481 | 31.4892 | 7.6346 | 5.5693 | 12.6751 | 31.5585 | 7.5125 | 5.4803 | 12.5039 | 31.6321 | 7.404 | 5.4011 | 12.4572 | 31.7079 | 7.2726 | 5.3053 | 12.2063 | 31.7893 | 7.1281 | 5.1998 | 12.0075 | 32.2169 | 6.7394 | 4.9163 | 11.4392 | 32.6477 | 6.9307 | 5.0558 | 10.9494 | 33.0653 | 8.208 | 5.9877 | 10.7867 | 33.3897 | 8.0155 | 5.8472 | 10.7166 | 31.264 | 10.3409 | 7.5436 | 13.9662 | 31.3352 | 9.6334 | 7.0275 | 13.3716 | 31.3405 | 9.2072 | 6.7165 | 13.2735 | 31.3753 | 8.7026 | 6.3484 | 13.3045 | 31.434 | 8.3491 | 6.0906 | 13.0438 | 31.5284 | 7.7791 | 5.6747 | 12.7775 | 31.6485 | 7.8259 | 5.7089 | 12.6019 | 31.7904 | 7.7432 | 5.6486 | 12.5422 | 31.9463 | 7.6332 | 5.5683 | 12.2732 | 32.1225 | 7.5483 | 5.5064 | 12.063 | 33.1895 | 6.9548 | 5.0735 | 11.0604 | 34.531 | 6.2231 | 4.5397 | 8.1647 | 35.1941 | 6.8974 | 5.0316 | 5.6862 | 35.4505 | 6.4369 | 4.6956 | 4.1931 | 31.2602 | 10.3428 | 7.545 | 13.9691 | 31.3335 | 10.264 | 7.4874 | 13.365 | 31.3419 | 10.2431 | 7.4722 | 13.2687 | 31.3788 | 10.2358 | 7.4668 | 13.3128 | 31.4399 | 10.1637 | 7.4143 | 13.0681 | 31.5443 | 10.0324 | 7.3185 | 12.817 | 31.6864 | 9.7584 | 7.1186 | 12.6438 | 31.8567 | 9.5985 | 7.002 | 12.5859 | 32.0586 | 9.3723 | 6.8369 | 12.3023 | 32.3446 | 9.0472 | 6.5998 | 11.8653 | 33.7237 | 8.2312 | 6.0045 | 8.8995 | 34.6935 | 7.1995 | 5.2519 | 6.2048 | 35.0649 | 6.6126 | 4.8238 | 4.4748 | 35.035 | 6.5619 | 4.7868 | 5.1004
BLACKFRIARS | FREDERICK RD | WHITEGATE | 383030 | 399104 | 32.5069 | 11.7222 | 8.5512 | 9.7995 | 32.5917 | 11.483 | 8.3767 | 8.718 | 32.6229 | 11.3633 | 8.2894 | 8.3259 | 32.6671 | 11.2194 | 8.1844 | 7.9333 | 32.7305 | 11.1565 | 8.1385 | 8.0946 | 32.8155 | 10.9606 | 7.9956 | 7.6729 | 32.9 | 10.7989 | 7.8777 | 7.4794 | 32.9827 | 10.8019 | 7.8798 | 7.2958 | 33.0647 | 10.7114 | 7.8138 | 7.0738 | 33.1492 | 10.5157 | 7.671 | 6.6826 | 33.4224 | 10.3624 | 7.5593 | 5.6182 | 33.6075 | 10.1716 | 7.4201 | 4.9022 | 33.6995 | 11.128 | 8.1177 | 4.3874 | 33.7158 | 10.9852 | 8.0135 | 4.3754 | 32.3906 | 11.8383 | 8.6359 | 10.4047 | 32.4174 | 11.6799 | 8.5203 | 9.8912 | 32.4811 | 11.5804 | 8.4478 | 9.534 | 32.5883 | 11.4686 | 8.3662 | 9.0685 | 32.7057 | 11.469 | 8.3665 | 9.1375 | 32.8299 | 11.3572 | 8.2849 | 8.6723 | 32.9405 | 11.2484 | 8.2056 | 8.4047 | 33.0534 | 11.2009 | 8.1709 | 8.136 | 33.1696 | 11.1615 | 8.1422 | 7.8228 | 33.2883 | 11.0923 | 8.0917 | 7.3936 | 33.6487 | 10.9038 | 7.9541 | 6.5814 | 33.8472 | 10.8055 | 7.8824 | 5.7974 | 33.9616 | 11.3107 | 8.251 | 5.0963 | 34.0035 | 11.7699 | 8.586 | 4.7275 | 32.5069 | 11.8308 | 8.6304 | 9.8054 | 32.5917 | 11.6024 | 8.4638 | 8.7349 | 32.6229 | 11.5662 | 8.4374 | 8.3542 | 32.6671 | 11.4728 | 8.3692 | 7.974 | 32.7304 | 11.4505 | 8.353 | 8.1421 | 32.8152 | 11.3329 | 8.2672 | 7.7336 | 32.8996 | 11.2321 | 8.1937 | 7.5508 | 32.9822 | 11.1111 | 8.1054 | 7.3781 | 33.0637 | 11.0551 | 8.0645 | 7.1703 | 33.1465 | 10.9903 | 8.0173 | 6.806 | 33.4111 | 10.8274 | 7.8984 | 5.7994 | 33.5891 | 10.6866 | 7.7957 | 5.1215 | 33.6775 | 11.5768 | 8.4451 | 4.6233 | 33.6929 | 11.4939 | 8.3847 | 4.6024 | 32.4959 | 11.7245 | 8.5528 | 9.8256 | 32.5983 | 11.4793 | 8.374 | 8.7759 | 32.5794 | 11.3521 | 8.2812 | 8.4216 | 32.6143 | 11.2004 | 8.1705 | 8.0571 | 32.6705 | 11.1394 | 8.1261 | 8.2417 | 32.7517 | 10.928 | 7.9718 | 7.8408 | 32.8373 | 10.8521 | 7.9164 | 7.6339 | 32.9237 | 10.802 | 7.8799 | 7.4379 | 33.011 | 10.6643 | 7.7794 | 7.2381 | 33.1 | 10.5904 | 7.7256 | 6.9263 | 33.3221 | 10.3039 | 7.5165 | 5.8818 | 33.4731 | 9.8894 | 7.2142 | 4.019 | 33.4497 | 10.4691 | 7.637 | 2.4296 | 33.3534 | 10.0638 | 7.3414 | 1.2785 | 32.4843 | 11.7272 | 8.5549 | 9.8396 | 32.5827 | 11.4496 | 8.3523 | 8.7982 | 32.5477 | 11.256 | 8.2111 | 8.464 | 32.5684 | 10.9925 | 8.0188 | 8.1276 | 32.6112 | 10.9748 | 8.006 | 8.3118 | 32.6764 | 10.9649 | 7.9987 | 7.9296 | 32.7449 | 10.9377 | 7.9789 | 7.7665 | 32.8119 | 10.9047 | 7.9548 | 7.6193 | 32.8791 | 10.8335 | 7.9029 | 7.455 | 32.9555 | 10.7217 | 7.8213 | 6.9148 | 33.1814 | 11.1379 | 8.1249 | 4.8294 | 33.2823 | 10.4318 | 7.6098 | 2.9137 | 33.2045 | 10.0526 | 7.3332 | 1.6963 | 33.0317 | 9.97 | 7.273 | 2.0005
BLACKLEY | RED BANK | WHITEGATE | 383882 | 403258 | 30.3071 | 13.379 | 9.7598 | 15.5312 | 30.3811 | 13.2968 | 9.6998 | 15.1888 | 30.4032 | 13.2301 | 9.6512 | 14.9643 | 30.4674 | 13.0765 | 9.5391 | 14.6402 | 30.5522 | 12.8587 | 9.3802 | 14.2911 | 30.654 | 12.5483 | 9.1538 | 13.8816 | 30.765 | 12.6977 | 9.2628 | 13.49 | 30.8836 | 12.7661 | 9.3127 | 13.0472 | 31.0092 | 12.7263 | 9.2836 | 12.5836 | 31.1481 | 12.6519 | 9.2294 | 12.0406 | 31.6813 | 12.1592 | 8.87 | 10.0961 | 31.9997 | 11.6685 | 8.512 | 9.0745 | 32.1767 | 11.4598 | 8.3597 | 8.7999 | 32.2612 | 11.1578 | 8.1394 | 8.9988 | 30.2409 | 13.4577 | 9.8172 | 15.6748 | 30.2611 | 13.3708 | 9.7538 | 15.4602 | 30.3157 | 13.3275 | 9.7222 | 15.2034 | 30.3942 | 13.3049 | 9.7058 | 14.9155 | 30.4846 | 13.239 | 9.6577 | 14.629 | 30.5834 | 13.1506 | 9.5932 | 14.2829 | 30.6868 | 13.0751 | 9.5381 | 13.9485 | 30.7966 | 12.9972 | 9.4813 | 13.5625 | 30.9127 | 12.9097 | 9.4174 | 13.157 | 31.0343 | 12.8156 | 9.3488 | 12.7578 | 31.2981 | 12.5671 | 9.1675 | 11.404 | 31.4986 | 12.2779 | 8.9565 | 10.3139 | 31.6193 | 12.1823 | 8.8868 | 9.6417 | 31.6799 | 12.0391 | 8.7824 | 9.2183 | 30.3071 | 13.4615 | 9.82 | 15.5223 | 30.3811 | 13.4116 | 9.7836 | 15.201 | 30.4032 | 13.3506 | 9.7391 | 14.9973 | 30.4674 | 13.3045 | 9.7054 | 14.6865 | 30.5518 | 13.2505 | 9.666 | 14.3544 | 30.6531 | 13.1716 | 9.6085 | 13.962 | 30.7636 | 13.0854 | 9.5456 | 13.5862 | 30.8818 | 12.9539 | 9.4497 | 13.1591 | 31.0057 | 12.8755 | 9.3925 | 12.7196 | 31.1378 | 12.7728 | 9.3176 | 12.2316 | 31.6461 | 12.2185 | 8.9133 | 10.4946 | 31.942 | 11.9152 | 8.692 | 9.6146 | 32.1066 | 11.5322 | 8.4126 | 9.3669 | 32.1866 | 11.4122 | 8.325 | 9.5465 | 30.3005 | 13.3776 | 9.7588 | 15.5395 | 30.371 | 13.2774 | 9.6857 | 15.2039 | 30.4005 | 13.1573 | 9.598 | 14.9903 | 30.4784 | 12.9622 | 9.4558 | 14.6757 | 30.5861 | 12.6477 | 9.2263 | 14.3531 | 30.7273 | 12.6798 | 9.2497 | 13.9564 | 30.8937 | 12.7907 | 9.3306 | 13.5316 | 31.0807 | 12.7493 | 9.3005 | 13.0584 | 31.2854 | 12.7098 | 9.2716 | 12.6299 | 31.4725 | 12.6287 | 9.2124 | 12.2116 | 32.0576 | 11.8301 | 8.6299 | 9.9668 | 32.5188 | 10.7044 | 7.8087 | 6.0178 | 32.7258 | 9.9107 | 7.2297 | 3.2205 | 32.8136 | 9.2552 | 6.7515 | 1.1713 | 30.2974 | 13.3755 | 9.7572 | 15.5288 | 30.3771 | 13.1626 | 9.602 | 15.1473 | 30.4133 | 12.9123 | 9.4194 | 14.9151 | 30.4827 | 13.1703 | 9.6076 | 14.6008 | 30.5885 | 13.2213 | 9.6448 | 14.2563 | 30.7199 | 13.1923 | 9.6236 | 13.8745 | 30.8755 | 13.1105 | 9.564 | 13.5006 | 31.0431 | 13.0023 | 9.485 | 13.0948 | 31.2251 | 12.8935 | 9.4056 | 12.6739 | 31.4143 | 12.6612 | 9.2362 | 11.6712 | 32.0046 | 11.1978 | 8.1687 | 7.0201 | 32.3193 | 10.3701 | 7.5649 | 3.5354 | 32.3652 | 9.8005 | 7.1494 | 1.6581 | 32.2326 | 9.6175 | 7.0158 | 2.2246
BLACKPOOL | BLACKPOOL | PENWORTHAM WEST / STANAH | 330835 | 435308 | 35.5425 | 9.3055 | 6.7882 | 19.8135 | 35.6301 | 9.322 | 6.8003 | 19.5343 | 35.6281 | 9.3241 | 6.8018 | 19.4681 | 35.6532 | 9.2684 | 6.7612 | 19.285 | 35.6937 | 9.1418 | 6.6688 | 19.0952 | 35.7506 | 8.9992 | 6.5648 | 18.9463 | 35.8096 | 8.8339 | 6.4442 | 18.6662 | 35.8702 | 8.6799 | 6.3319 | 18.461 | 35.9325 | 8.5107 | 6.2085 | 18.2062 | 35.997 | 8.4078 | 6.1334 | 18.0147 | 36.0944 | 7.8317 | 5.7131 | 17.4209 | 36.1364 | 7.6301 | 5.566 | 17.1836 | 36.1278 | 7.5973 | 5.5421 | 17.1188 | 36.0844 | 7.5959 | 5.5411 | 17.2423 | 35.4794 | 9.2694 | 6.7619 | 20.0323 | 35.5256 | 9.1916 | 6.7051 | 19.9087 | 35.6087 | 9.0784 | 6.6225 | 19.6269 | 35.7139 | 8.943 | 6.5238 | 19.2498 | 35.8343 | 8.8141 | 6.4297 | 18.8691 | 35.9351 | 8.6648 | 6.3209 | 18.4983 | 36.0478 | 8.4638 | 6.1742 | 17.6653 | 36.1704 | 8.2594 | 6.0251 | 16.8029 | 36.3043 | 8.0237 | 5.8532 | 15.8299 | 36.449 | 7.7674 | 5.6662 | 14.6719 | 36.5339 | 7.6524 | 5.5824 | 14.4676 | 36.5848 | 7.5966 | 5.5416 | 14.3491 | 36.5876 | 7.6038 | 5.5468 | 14.3519 | 36.5404 | 7.6271 | 5.5639 | 14.43 | 35.5425 | 9.2687 | 6.7614 | 19.837 | 35.6301 | 9.2045 | 6.7146 | 19.5819 | 35.6281 | 9.0417 | 6.5958 | 19.5435 | 35.6532 | 8.8164 | 6.4315 | 19.3924 | 35.6936 | 8.6366 | 6.3003 | 19.2351 | 35.7503 | 8.4794 | 6.1856 | 19.1157 | 35.8092 | 8.2493 | 6.0177 | 18.8731 | 35.8697 | 8.0176 | 5.8487 | 18.7027 | 35.9315 | 7.7848 | 5.6789 | 18.4891 | 35.9941 | 7.5071 | 5.4764 | 18.3422 | 36.0829 | 7.1382 | 5.2073 | 17.784 | 36.1181 | 7.0628 | 5.1522 | 17.5644 | 36.1062 | 7.0884 | 5.1709 | 17.5055 | 36.0617 | 6.9643 | 5.0804 | 17.6255 | 35.534 | 9.3111 | 6.7923 | 19.8194 | 35.6141 | 9.3395 | 6.813 | 19.5447 | 35.6071 | 9.4468 | 6.8913 | 19.4833 | 35.6291 | 9.2444 | 6.7437 | 19.3044 | 35.6689 | 9.0912 | 6.6319 | 19.1073 | 35.7286 | 8.993 | 6.5602 | 18.9536 | 35.7938 | 8.846 | 6.453 | 18.6634 | 35.8636 | 8.7129 | 6.3559 | 18.4462 | 35.9374 | 8.5714 | 6.2527 | 18.1839 | 36.0155 | 8.4358 | 6.1538 | 18.0058 | 36.1127 | 7.7852 | 5.6792 | 17.1651 | 36.1514 | 7.1048 | 5.1829 | 15.274 | 36.1059 | 6.5726 | 4.7946 | 13.1665 | 36.015 | 6.2231 | 4.5396 | 11.5966 | 35.5173 | 9.319 | 6.7981 | 19.8512 | 35.5826 | 9.4342 | 6.8821 | 19.6017 | 35.5571 | 9.3976 | 6.8554 | 19.5832 | 35.5568 | 9.2511 | 6.7486 | 19.4588 | 35.5731 | 9.0595 | 6.6088 | 19.3196 | 35.6065 | 8.8441 | 6.4517 | 19.2327 | 35.6445 | 8.6594 | 6.3169 | 19.0156 | 35.6837 | 8.523 | 6.2174 | 18.8799 | 35.7241 | 8.3594 | 6.0981 | 18.7089 | 35.7739 | 8.0934 | 5.904 | 18.2222 | 35.8692 | 7.0269 | 5.1261 | 15.8245 | 35.6368 | 5.7806 | 4.2169 | 13.2537 | 32.756 | 5.3133 | 3.876 | 11.6766 | 32.9758 | 5.349 | 3.902 | 12.1967
BOLLINGTON | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 16.6133 | 15.0371 | 10.8075 | 4.3292 | 16.6821 | 14.9855 | 10.7703 | 3.9825 | 16.7237 | 14.9316 | 10.7316 | 3.761 | 16.7841 | 14.8682 | 10.6861 | 3.5313 | 16.8589 | 14.7574 | 10.6065 | 3.0964 | 16.9466 | 14.6485 | 10.5282 | 2.7573 | 17.0436 | 14.4937 | 10.4169 | 2.3412 | 17.1472 | 14.3893 | 10.3418 | 1.8792 | 17.2564 | 14.2838 | 10.2661 | 1.5582 | 17.3884 | 14.1301 | 10.1556 | 0.94769 | 17.9234 | 13.518 | 9.7156 | -1.1267 | 18.3356 | 12.9225 | 9.2877 | -2.3642 | 18.5934 | 12.3143 | 8.8506 | -2.5048 | 18.7497 | 12.0151 | 8.6355 | -2.3178 | 16.5817 | 15.0522 | 10.8183 | 4.423 | 16.6262 | 15.0153 | 10.7918 | 4.161 | 16.6911 | 14.9661 | 10.7564 | 3.8982 | 16.7579 | 14.9271 | 10.7284 | 3.7207 | 16.8349 | 14.8369 | 10.6636 | 3.3483 | 16.9199 | 14.7821 | 10.6242 | 3.0705 | 17.0139 | 14.7028 | 10.5672 | 2.7137 | 17.1141 | 14.6026 | 10.4952 | 2.3092 | 17.2207 | 14.5079 | 10.4271 | 2.0679 | 17.3222 | 14.455 | 10.3891 | 1.6402 | 17.5759 | 14.1302 | 10.1557 | 0.41381 | 17.8096 | 13.8679 | 9.9671 | -0.63871 | 17.9916 | 13.6787 | 9.8311 | -1.2202 | 18.1218 | 13.4997 | 9.7025 | -1.6859 | 16.6133 | 15.0516 | 10.8179 | 4.3343 | 16.6821 | 15.0063 | 10.7853 | 4.0059 | 16.7239 | 14.9391 | 10.737 | 3.8024 | 16.7844 | 14.8101 | 10.6443 | 3.5881 | 16.859 | 14.7751 | 10.6192 | 3.174 | 16.9464 | 14.6921 | 10.5595 | 2.8534 | 17.0431 | 14.5836 | 10.4815 | 2.4536 | 17.1466 | 14.4387 | 10.3774 | 1.9966 | 17.2546 | 14.3592 | 10.3202 | 1.6586 | 17.3816 | 14.2536 | 10.2443 | 1.1006 | 17.8862 | 13.7371 | 9.8731 | -0.79895 | 18.2521 | 13.4152 | 9.6418 | -1.9041 | 18.4865 | 12.8747 | 9.2533 | -1.9971 | 18.6129 | 12.6352 | 9.0812 | -1.7948 | 16.6108 | 15.0369 | 10.8073 | 4.3381 | 16.684 | 14.9786 | 10.7654 | 3.983 | 16.7376 | 14.9 | 10.709 | 3.7549 | 16.8165 | 14.8172 | 10.6494 | 3.5285 | 16.9187 | 14.691 | 10.5587 | 3.0935 | 17.0476 | 14.5685 | 10.4707 | 2.7386 | 17.2036 | 14.4095 | 10.3564 | 2.2757 | 17.3786 | 14.256 | 10.246 | 1.7623 | 17.5606 | 14.1481 | 10.1685 | 1.5 | 17.7615 | 13.9773 | 10.0458 | 1.0405 | 18.517 | 13.0839 | 9.4037 | -0.99203 | 19.278 | 12.2104 | 8.7759 | -4.0699 | 19.6314 | 11.2878 | 8.1127 | -5.7818 | 19.818 | 10.8518 | 7.7994 | -7.1652 | 16.6085 | 15.0327 | 10.8043 | 4.3149 | 16.6857 | 14.9459 | 10.7419 | 3.9235 | 16.737 | 14.8486 | 10.672 | 3.7071 | 16.8089 | 14.7459 | 10.5981 | 3.5021 | 16.9044 | 14.5966 | 10.4909 | 3.0837 | 17.0209 | 14.4483 | 10.3842 | 2.7736 | 17.1612 | 14.3162 | 10.2893 | 2.3804 | 17.3141 | 14.1476 | 10.1681 | 1.9605 | 17.4803 | 14.0044 | 10.0652 | 1.7486 | 17.7166 | 13.801 | 9.919 | 0.9207 | 18.5867 | 12.5463 | 9.0173 | -2.7157 | 19.0381 | 11.5652 | 8.3122 | -5.2465 | 19.1771 | 11.4372 | 8.2202 | -6.233 | 19.1336 | 11.1661 | 8.0253 | -5.7667
BOLTON BY BOWLAND | PADIHAM | PADIHAM | 378320 | 449559 | 8.1531 | 8.1531 | 8.1531 | 4.2518 | 8.2038 | 8.2038 | 8.2038 | 4.084 | 8.2635 | 8.2635 | 8.2635 | 4.0212 | 8.2957 | 8.2957 | 8.2957 | 3.9638 | 8.3227 | 8.3227 | 8.3227 | 3.8646 | 8.3546 | 8.3546 | 8.3546 | 3.7407 | 8.3912 | 8.3912 | 8.3912 | 3.6007 | 8.4306 | 8.4306 | 8.4306 | 3.4582 | 8.4727 | 8.4727 | 8.4727 | 3.2919 | 8.5192 | 8.5192 | 8.5192 | 3.0958 | 8.6817 | 8.6817 | 8.6817 | 2.4381 | 8.7939 | 8.7939 | 8.7939 | 2.1547 | 8.8556 | 8.8556 | 8.8556 | 2.1181 | 8.8889 | 8.8889 | 8.8889 | 2.2549 | 8.1665 | 8.1665 | 8.1665 | 4.3651 | 8.2226 | 8.2226 | 8.2226 | 4.2979 | 8.2759 | 8.2759 | 8.2759 | 4.2115 | 8.3103 | 8.3103 | 8.3103 | 4.1177 | 8.3483 | 8.3483 | 8.3483 | 4.0028 | 8.3904 | 8.3904 | 8.3904 | 3.8773 | 8.438 | 8.438 | 8.438 | 3.7336 | 8.4897 | 8.4897 | 8.4897 | 3.5839 | 8.546 | 8.546 | 8.546 | 3.4274 | 8.6071 | 8.6071 | 8.6071 | 3.2672 | 8.6809 | 8.6809 | 8.6809 | 2.8567 | 8.7378 | 8.7378 | 8.7378 | 2.4896 | 8.7729 | 8.7729 | 8.7729 | 2.2604 | 8.7915 | 8.7915 | 8.7915 | 2.1305 | 8.1531 | 8.1531 | 8.1531 | 4.2541 | 8.2038 | 8.2038 | 8.2038 | 4.0888 | 8.2635 | 8.2635 | 8.2635 | 4.0285 | 8.2957 | 8.2957 | 8.2957 | 3.9738 | 8.3226 | 8.3226 | 8.3226 | 3.9012 | 8.3543 | 8.3543 | 8.3543 | 3.7826 | 8.3908 | 8.3908 | 8.3908 | 3.6479 | 8.4301 | 8.4301 | 8.4301 | 3.4993 | 8.4717 | 8.4717 | 8.4717 | 3.3407 | 8.5162 | 8.5162 | 8.5162 | 3.1638 | 8.669 | 8.669 | 8.669 | 2.57 | 8.7727 | 8.7727 | 8.7727 | 2.3257 | 8.8301 | 8.8301 | 8.8301 | 2.3052 | 8.8622 | 8.8622 | 8.8622 | 2.434 | 8.1549 | 8.1549 | 8.1549 | 4.2579 | 8.21 | 8.21 | 8.21 | 4.0954 | 8.2735 | 8.2735 | 8.2735 | 4.0379 | 8.3019 | 8.3019 | 8.3019 | 3.9858 | 8.3363 | 8.3363 | 8.3363 | 3.8871 | 8.3789 | 8.3789 | 8.3789 | 3.7694 | 8.431 | 8.431 | 8.431 | 3.6352 | 8.4896 | 8.4896 | 8.4896 | 3.5051 | 8.5545 | 8.5545 | 8.5545 | 3.3848 | 8.6264 | 8.6264 | 8.6264 | 3.2685 | 8.8409 | 8.8409 | 8.8409 | 2.743 | 8.9734 | 8.9734 | 8.9734 | 2.1882 | 9.0248 | 9.0248 | 9.0248 | 1.926 | 9.0434 | 9.0434 | 9.0434 | 1.7947 | 8.1656 | 8.1656 | 8.1656 | 4.2535 | 8.2248 | 8.2248 | 8.2248 | 4.0816 | 8.2726 | 8.2726 | 8.2726 | 4.0235 | 8.2957 | 8.2957 | 8.2957 | 3.9758 | 8.3261 | 8.3261 | 8.3261 | 3.8723 | 8.3627 | 8.3627 | 8.3627 | 3.765 | 8.409 | 8.409 | 8.409 | 3.646 | 8.4592 | 8.4592 | 8.4592 | 3.5364 | 8.5137 | 8.5137 | 8.5137 | 3.43 | 8.575 | 8.575 | 8.575 | 3.2418 | 8.7558 | 8.7558 | 8.7558 | 2.414 | 8.8375 | 8.8375 | 8.8375 | 1.9494 | 8.8429 | 8.8429 | 8.8429 | 1.8107 | 8.8193 | 8.8193 | 8.8193 | 2.0162
BOLTON LE SANDS | LANCASTER | HEYSHAM | 347707 | 467237 | 23.887 | 12.7785 | 9.1841 | 9.0471 | 23.9602 | 12.6872 | 9.1185 | 8.4661 | 24.0213 | 12.4596 | 8.955 | 8.2212 | 24.1009 | 12.2746 | 8.822 | 7.8767 | 24.2018 | 11.5742 | 8.3186 | 7.4724 | 24.3288 | 11.4807 | 8.2514 | 7.1051 | 24.4799 | 10.9826 | 7.8934 | 6.6578 | 24.6485 | 10.8093 | 7.7688 | 6.196 | 24.8283 | 10.6337 | 7.6426 | 5.7101 | 25.0423 | 10.4265 | 7.4937 | 5.101 | 26.2495 | 9.6259 | 6.9184 | 2.3932 | 27.6081 | 9.0724 | 6.5205 | 0.4123 | 28.4879 | 8.8612 | 6.3688 | -0.77732 | 29.1661 | 8.8265 | 6.3438 | -0.26242 | 23.8738 | 12.8235 | 9.2165 | 9.2139 | 23.9324 | 12.7042 | 9.1308 | 8.7993 | 24.0216 | 12.6218 | 9.0715 | 8.5695 | 24.119 | 12.5749 | 9.0378 | 8.3277 | 24.232 | 12.4653 | 8.9591 | 8.0197 | 24.3618 | 12.4301 | 8.9338 | 7.7406 | 24.508 | 12.3208 | 8.8552 | 7.3799 | 24.67 | 12.1647 | 8.743 | 7.0007 | 24.8475 | 12.1115 | 8.7048 | 6.5514 | 25.0392 | 12.038 | 8.6519 | 6.1933 | 25.7843 | 11.7151 | 8.4199 | 4.8649 | 26.5611 | 11.293 | 8.1165 | 3.3837 | 27.1662 | 11.03 | 7.9275 | 2.1765 | 27.629 | 10.8713 | 7.8134 | 1.7406 | 23.8942 | 12.8181 | 9.2126 | 9.0534 | 23.9699 | 12.7046 | 9.131 | 8.4897 | 24.0293 | 12.6456 | 9.0887 | 8.2633 | 24.1101 | 12.6131 | 9.0653 | 7.948 | 24.2113 | 12.4953 | 8.9806 | 7.5735 | 24.336 | 12.3525 | 8.878 | 7.2353 | 24.4825 | 12.2145 | 8.7788 | 6.8189 | 24.6447 | 12.0325 | 8.648 | 6.3886 | 24.8149 | 11.8703 | 8.5314 | 5.9343 | 25.0129 | 11.7138 | 8.4189 | 5.3982 | 26.0886 | 11.0904 | 7.9709 | 2.9988 | 27.0682 | 10.4962 | 7.5439 | 1.3426 | 27.7257 | 10.2229 | 7.3474 | 0.25923 | 28.1542 | 9.946 | 7.1484 | 0.89693 | 23.8961 | 12.7716 | 9.1792 | 9.0471 | 23.9794 | 12.6785 | 9.1123 | 8.4232 | 24.047 | 12.4176 | 8.9248 | 8.1299 | 24.1451 | 12.2065 | 8.773 | 7.7601 | 24.2765 | 11.64 | 8.3659 | 7.2944 | 24.4614 | 11.3552 | 8.1612 | 6.8154 | 24.7016 | 10.8079 | 7.7679 | 6.181 | 24.9854 | 10.5709 | 7.5975 | 5.4968 | 25.3026 | 10.3308 | 7.4249 | 4.8562 | 25.6597 | 10.0618 | 7.2316 | 4.298 | 27.564 | 9.2056 | 6.6162 | 1.2775 | 29.4953 | 7.8642 | 5.6521 | -3.89 | 30.5906 | 6.9848 | 5.0201 | -7.8706 | 30.7675 | 6.47 | 4.6501 | -9.4591 | 23.9046 | 12.7811 | 9.186 | 9.0678 | 23.9818 | 12.7002 | 9.1279 | 8.4557 | 24.0515 | 12.4833 | 8.972 | 8.1824 | 24.1536 | 12.1705 | 8.7472 | 7.8273 | 24.2909 | 11.7414 | 8.4388 | 7.3698 | 24.4966 | 11.2877 | 8.1127 | 6.9334 | 24.7779 | 10.7292 | 7.7113 | 6.3852 | 25.1128 | 10.5677 | 7.5952 | 5.8179 | 25.4914 | 10.4105 | 7.4822 | 5.2723 | 25.9502 | 10.1201 | 7.2735 | 4.2063 | 27.9812 | 8.8635 | 6.3703 | -1.2289 | 29.6212 | 7.5822 | 5.4494 | -5.4961 | 30.4643 | 6.8217 | 4.9029 | -8.3884 | 30.3398 | 6.8927 | 4.954 | -7.1432
BOTANY BAY | LEYLAND | PENWORTHAM WEST / STANAH | 359442 | 418850 | 19.7328 | 19.7328 | 19.4687 | 10.0327 | 19.7972 | 19.7972 | 19.4018 | 9.7423 | 19.8792 | 19.8792 | 19.3551 | 9.4396 | 19.9812 | 19.9812 | 19.261 | 9.0544 | 20.078 | 20.078 | 19.1534 | 8.6984 | 20.1859 | 20.1859 | 19.0388 | 8.2285 | 20.3136 | 20.3136 | 18.9773 | 7.7371 | 20.4557 | 20.4557 | 18.8501 | 7.2012 | 20.6102 | 20.6102 | 18.773 | 6.6905 | 20.7815 | 20.7815 | 18.6553 | 6.0852 | 21.5423 | 21.5423 | 18.1962 | 4.0039 | 22.1484 | 22.1484 | 17.9089 | 2.7006 | 22.5375 | 22.5375 | 17.7478 | 2.2449 | 22.8198 | 22.8198 | 17.6739 | 2.1818 | 19.7377 | 19.7377 | 19.4663 | 10.0919 | 19.8018 | 19.8018 | 19.4113 | 9.8596 | 19.8848 | 19.8848 | 19.3501 | 9.5463 | 19.9597 | 19.9597 | 19.278 | 9.2129 | 20.0592 | 20.0592 | 19.2285 | 8.9307 | 20.1728 | 20.1728 | 19.1798 | 8.5395 | 20.2893 | 20.2893 | 19.0876 | 8.1333 | 20.4158 | 20.4158 | 19.0456 | 7.6858 | 20.551 | 20.551 | 18.9747 | 7.2487 | 20.6846 | 20.6846 | 18.9178 | 6.7756 | 21.1775 | 21.1775 | 18.6341 | 5.2172 | 21.524 | 21.524 | 18.4389 | 4.1464 | 21.7571 | 21.7571 | 18.309 | 3.5949 | 21.9233 | 21.9233 | 18.1363 | 3.2194 | 19.7365 | 19.7365 | 19.466 | 10.0362 | 19.8022 | 19.8022 | 19.3849 | 9.7546 | 19.8851 | 19.8851 | 19.3068 | 9.4612 | 19.9876 | 19.9876 | 19.2478 | 9.0864 | 20.0827 | 20.0827 | 19.1996 | 8.7435 | 20.1885 | 20.1885 | 19.0758 | 8.2898 | 20.3129 | 20.3129 | 19.0149 | 7.8146 | 20.4506 | 20.4506 | 18.9436 | 7.2953 | 20.5982 | 20.5982 | 18.8607 | 6.8076 | 20.7564 | 20.7564 | 18.7658 | 6.2558 | 21.4547 | 21.4547 | 18.3645 | 4.3704 | 21.9478 | 21.9478 | 18.1853 | 3.247 | 22.2399 | 22.2399 | 18.0312 | 2.9339 | 22.4364 | 22.4364 | 17.8574 | 2.9411 | 19.7393 | 19.7393 | 19.4695 | 10.0369 | 19.8165 | 19.8165 | 19.4055 | 9.75 | 19.9256 | 19.9256 | 19.334 | 9.4566 | 20.0264 | 20.0264 | 19.244 | 9.0844 | 20.1425 | 20.1425 | 19.1543 | 8.7709 | 20.2933 | 20.2933 | 19.0379 | 8.3501 | 20.4693 | 20.4693 | 18.923 | 7.912 | 20.67 | 20.67 | 18.7995 | 7.4394 | 20.8962 | 20.8962 | 18.6354 | 7.0383 | 21.1515 | 21.1515 | 18.5885 | 6.6051 | 22.1374 | 22.1374 | 18.1284 | 4.3384 | 23.0954 | 23.0954 | 17.5005 | 1.0533 | 23.7151 | 23.6556 | 17.0017 | -1.5546 | 24.0168 | 23.1671 | 16.6507 | -3.5321 | 19.7416 | 19.7416 | 19.4664 | 10.006 | 19.8335 | 19.8335 | 19.3898 | 9.6604 | 19.9518 | 19.9518 | 19.3475 | 9.3547 | 20.0405 | 20.0405 | 19.2575 | 8.9993 | 20.1551 | 20.1551 | 19.1725 | 8.7197 | 20.2976 | 20.2976 | 19.0475 | 8.3509 | 20.4777 | 20.4777 | 18.9233 | 7.9578 | 20.6848 | 20.6848 | 18.7695 | 7.5479 | 20.9204 | 20.9204 | 18.71 | 7.1497 | 21.1914 | 21.1914 | 18.5544 | 6.3311 | 22.1953 | 22.1953 | 17.9364 | 2.7216 | 22.953 | 22.953 | 17.387 | 0.14102 | 23.3564 | 23.3564 | 17.0913 | -1.1558 | 23.4182 | 23.4182 | 16.9947 | -1.2965
BOW LANE | LEYLAND | PENWORTHAM WEST / STANAH | 354895 | 422392 | 25.9076 | 12.0572 | 8.6658 | 9.2145 | 26.036 | 10.537 | 7.5731 | 8.5984 | 26.094 | 9.0934 | 6.5356 | 8.2187 | 26.1872 | 7.5644 | 5.4367 | 7.735 | 26.3083 | 6.093 | 4.3792 | 7.3431 | 26.4608 | 4.5669 | 3.2823 | 6.7246 | 26.4609 | 4.3566 | 3.1312 | 6.0953 | 25.0676 | 4.1272 | 2.9663 | 5.39 | 23.7412 | 3.9088 | 2.8093 | 4.7425 | 22.2007 | 3.6552 | 2.627 | 3.9339 | 18.0426 | 2.9706 | 2.135 | 1.0519 | 26.8438 | 4.4196 | 3.1765 | -0.86327 | 31.8413 | 7.3276 | 5.2665 | -1.5942 | 33.4152 | 7.8991 | 5.6772 | -2.1466 | 25.8293 | 12.0854 | 8.686 | 9.5364 | 25.8983 | 10.6724 | 7.6705 | 9.1899 | 26.0105 | 9.2335 | 6.6363 | 8.7212 | 26.136 | 7.7707 | 5.5849 | 8.2093 | 26.28 | 6.3045 | 4.5312 | 7.8262 | 26.4425 | 4.8639 | 3.4958 | 7.2371 | 26.6266 | 4.7161 | 3.3896 | 6.6317 | 26.8247 | 4.5526 | 3.272 | 5.9446 | 26.7061 | 4.397 | 3.1602 | 5.2988 | 25.6497 | 4.223 | 3.0352 | 4.562 | 23.6832 | 3.8993 | 2.8025 | 2.4754 | 28.992 | 4.8132 | 3.4593 | 0.85586 | 29.9986 | 6.6385 | 4.7712 | -0.19718 | 30.9037 | 6.9003 | 4.9594 | -0.98616 | 25.9081 | 12.082 | 8.6836 | 9.2257 | 26.0376 | 10.664 | 7.6644 | 8.6271 | 26.0972 | 9.1753 | 6.5945 | 8.2646 | 26.1925 | 7.6495 | 5.4978 | 7.7987 | 26.3157 | 6.2065 | 4.4607 | 7.4265 | 26.4698 | 4.7045 | 3.3812 | 6.8316 | 26.6466 | 4.5267 | 3.2535 | 6.2249 | 26.3417 | 4.337 | 3.1171 | 5.5429 | 25.1871 | 4.1469 | 2.9804 | 4.9278 | 23.922 | 3.9386 | 2.8307 | 4.1918 | 21.1302 | 3.4789 | 2.5004 | 1.6064 | 29.5664 | 5.0477 | 3.6279 | 0.17791 | 30.6885 | 7.8368 | 5.6325 | -0.34814 | 31.6686 | 8.3484 | 6.0002 | -0.52424 | 25.9027 | 12.0583 | 8.6666 | 9.2338 | 26.0335 | 10.5312 | 7.5689 | 8.6421 | 26.1099 | 9.0751 | 6.5225 | 8.2932 | 26.2294 | 7.5438 | 5.4219 | 7.839 | 26.3917 | 6.0581 | 4.3541 | 7.5143 | 26.6286 | 4.5058 | 3.2384 | 6.9645 | 25.9371 | 4.2703 | 3.0692 | 6.3896 | 24.3762 | 4.0134 | 2.8845 | 5.7427 | 23.1391 | 3.8097 | 2.7381 | 5.2148 | 21.7379 | 3.579 | 2.5723 | 4.6017 | 15.2287 | 2.5073 | 1.802 | 0.61557 | 16.0206 | 2.6377 | 1.8957 | -7.008 | 27.3671 | 4.5058 | 3.2384 | -13.1078 | 25.9588 | 4.2739 | 3.0718 | -17.5543 | 25.9075 | 12.0556 | 8.6646 | 9.205 | 26.06 | 11.8066 | 8.4856 | 8.5561 | 26.1459 | 11.6662 | 8.3847 | 8.2123 | 26.2721 | 11.427 | 8.2128 | 7.7967 | 26.4464 | 11.2194 | 8.0636 | 7.5115 | 26.718 | 10.9722 | 7.8859 | 7.0128 | 27.0932 | 10.7505 | 7.7266 | 6.4744 | 27.5412 | 10.5164 | 7.5584 | 5.8708 | 28.0877 | 10.2492 | 7.3663 | 5.1681 | 28.8322 | 9.8132 | 7.053 | 3.3914 | 32.1685 | 7.6826 | 5.5216 | -5.0415 | 34.3594 | 5.7535 | 4.1351 | -11.9578 | 30.0744 | 4.9515 | 3.5588 | -16.0943 | 28.9113 | 4.76 | 3.4211 | -15.8414
BOWATERS | BARROW & SANDGATE | HARKER / HUTTON | 319579 | 472480 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
BOWDON | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 31.6516 | 12.2908 | 8.8336 | 12.1562 | 31.7582 | 12.1413 | 8.7262 | 11.5381 | 31.8103 | 12.044 | 8.6563 | 11.2578 | 31.8876 | 11.9496 | 8.5884 | 10.922 | 31.9836 | 11.9909 | 8.6181 | 10.8158 | 32.102 | 11.942 | 8.583 | 10.3631 | 32.2296 | 11.8768 | 8.5361 | 9.839 | 32.3668 | 11.8303 | 8.5027 | 9.4491 | 32.5121 | 11.7232 | 8.4257 | 8.9243 | 32.6697 | 11.6476 | 8.3713 | 8.435 | 33.2352 | 11.1958 | 8.0466 | 6.837 | 33.5878 | 10.8636 | 7.8079 | 5.9994 | 33.7925 | 10.759 | 7.7327 | 6.0415 | 33.9095 | 10.6819 | 7.6773 | 6.2575 | 31.596 | 12.4811 | 8.9704 | 12.3733 | 31.6615 | 12.4154 | 8.9232 | 11.9249 | 31.7577 | 12.3391 | 8.8684 | 11.5783 | 31.8659 | 12.2423 | 8.7988 | 11.2397 | 31.9848 | 12.2002 | 8.7685 | 11.1452 | 32.1186 | 12.0995 | 8.6962 | 10.7127 | 32.2654 | 11.9985 | 8.6235 | 10.1893 | 32.4249 | 11.9122 | 8.5615 | 9.8328 | 32.5975 | 11.7892 | 8.4731 | 9.2848 | 32.7792 | 11.6736 | 8.3901 | 8.8695 | 33.0371 | 11.4428 | 8.2242 | 7.7334 | 33.2356 | 11.2478 | 8.084 | 6.739 | 33.3671 | 11.2623 | 8.0944 | 6.3325 | 33.4392 | 11.2363 | 8.0757 | 5.9555 | 31.6516 | 12.4826 | 8.9715 | 12.1639 | 31.7582 | 12.4128 | 8.9213 | 11.5749 | 31.8103 | 12.307 | 8.8453 | 11.2997 | 31.8876 | 12.2285 | 8.7889 | 10.9789 | 31.9831 | 12.1703 | 8.7471 | 10.87 | 32.1007 | 12.0375 | 8.6516 | 10.4279 | 32.2277 | 11.8887 | 8.5447 | 9.9343 | 32.3645 | 11.8119 | 8.4894 | 9.545 | 32.5078 | 11.6734 | 8.3899 | 9.0647 | 32.6571 | 11.5578 | 8.3068 | 8.6093 | 33.1851 | 11.1757 | 8.0322 | 7.165 | 33.521 | 10.8603 | 7.8055 | 6.4186 | 33.7112 | 10.8602 | 7.8054 | 6.477 | 33.8228 | 10.7339 | 7.7147 | 6.6663 | 31.6473 | 12.2899 | 8.833 | 12.1808 | 31.7574 | 12.1155 | 8.7076 | 11.5937 | 31.8258 | 11.9998 | 8.6245 | 11.36 | 31.9288 | 12.006 | 8.629 | 11.0722 | 32.0609 | 12.0368 | 8.6511 | 11.0195 | 32.2286 | 11.9791 | 8.6096 | 10.6295 | 32.4201 | 11.9169 | 8.5649 | 10.1529 | 32.6353 | 11.8726 | 8.5331 | 9.8623 | 32.871 | 11.7845 | 8.4698 | 9.4496 | 33.104 | 11.7423 | 8.4394 | 9.1771 | 33.7223 | 11.1389 | 8.0058 | 7.1906 | 34.239 | 10.0854 | 7.2486 | 2.8037 | 34.5139 | 9.2982 | 6.6828 | -0.21501 | 34.6406 | 8.8057 | 6.3288 | -2.2544 | 31.6564 | 12.2698 | 8.8186 | 12.0806 | 31.789 | 12.1449 | 8.7288 | 11.3804 | 31.8521 | 12.1823 | 8.7557 | 11.1902 | 31.9368 | 12.221 | 8.7835 | 10.9823 | 32.0488 | 12.2308 | 8.7905 | 10.9842 | 32.189 | 12.1622 | 8.7412 | 10.6813 | 32.3555 | 12.0526 | 8.6625 | 10.2983 | 32.5358 | 11.9871 | 8.6154 | 10.0791 | 32.7365 | 11.8364 | 8.5071 | 9.6534 | 32.9727 | 11.589 | 8.3292 | 8.619 | 33.5992 | 10.3176 | 7.4155 | 3.7379 | 33.9466 | 9.1309 | 6.5626 | -0.17947 | 34.027 | 8.7221 | 6.2687 | -1.9706 | 33.8959 | 8.6804 | 6.2388 | -1.0105
BRADFORD | STUART ST | STALYBRIDGE | 387613 | 397710 | 27.278 | 4.4248 | 3.2278 | 13.5776 | 21.1825 | 3.436 | 2.5065 | 12.5852 | 15.8696 | 2.5742 | 1.8778 | 12.4891 | 9.7088 | 1.5749 | 1.1488 | 9.7088 | 5.0415 | 0.81777 | 0.59656 | 5.0415 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 8.6653 | 1.4056 | 1.0254 | 6.8425 | 11.6348 | 1.8873 | 1.3767 | 5.6191 | 27.3393 | 4.6419 | 3.3862 | 14.1214 | 23.0303 | 3.7357 | 2.7252 | 13.6167 | 16.6644 | 2.7031 | 1.9719 | 13.4732 | 12.0181 | 1.9494 | 1.4221 | 12.0181 | 7.5904 | 1.2312 | 0.89817 | 7.5904 | 2.4644 | 0.39975 | 0.29161 | 2.4644 | 1.7559 | 0.28483 | 0.20778 | 1.7559 | 1.3152 | 0.21333 | 0.15562 | 1.3152 | 0.67275 | 0.10913 | 0.079607 | 0.67275 | 0.10927 | 0.017724 | 0.012929 | 0.10927 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 1.5655 | 0.25394 | 0.18525 | 1.5655 | 9.3691 | 1.5198 | 1.1086 | 9.2433 | 12.5378 | 2.0338 | 1.4836 | 8.8476 | 27.3942 | 4.6391 | 3.3842 | 13.5848 | 22.0645 | 3.5791 | 2.6109 | 12.6021 | 17.5322 | 2.8439 | 2.0746 | 12.513 | 12.1684 | 1.9738 | 1.4399 | 12.1684 | 7.2558 | 1.177 | 0.85857 | 7.2558 | 1.2914 | 0.20947 | 0.15281 | 1.2914 | 0.46824 | 0.075953 | 0.055407 | 0.46824 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 1.9514 | 0.31654 | 0.23091 | 1.9514 | 13.5876 | 2.204 | 1.6078 | 8.4209 | 17.4831 | 2.8359 | 2.0688 | 8.1831 | 27.2411 | 4.4188 | 3.2234 | 13.586 | 21.1323 | 3.4279 | 2.5006 | 12.6027 | 15.8424 | 2.5698 | 1.8746 | 12.5113 | 8.2889 | 1.3445 | 0.98083 | 8.2889 | 5.2105 | 0.8452 | 0.61656 | 5.2105 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.1424 | 0.51981 | 0.084319 | 0.061509 | -1.2961 | 27.2309 | 4.4171 | 3.2222 | 13.5774 | 25.5808 | 4.1494 | 3.027 | 12.5707 | 24.7589 | 4.0161 | 2.9297 | 12.4712 | 22.7455 | 3.6895 | 2.6915 | 12.2033 | 22.7619 | 3.6922 | 2.6934 | 12.2798 | 20.8375 | 3.3801 | 2.4657 | 11.9018 | 19.564 | 3.1735 | 2.315 | 11.6702 | 18.7282 | 3.0379 | 2.2161 | 11.4184 | 17.7099 | 2.8727 | 2.0956 | 11.0027 | 16.0653 | 2.6059 | 1.901 | 10.1626 | 8.3853 | 1.3602 | 0.99223 | 6.0328 | 0.89745 | 0.14557 | 0.10619 | 0.89745 | 1.8609 | 0.30185 | 0.2202 | -0.5482 | 1.1694 | 0.18969 | 0.13837 | -0.53919
BRADSHAWGATE | BOLTON | KEARSLEY | 371891 | 408910 | 33.8723 | 12.0569 | 8.7953 | 20.3436 | 33.9296 | 11.9369 | 8.7078 | 19.9537 | 33.9487 | 11.9106 | 8.6886 | 19.8671 | 33.9863 | 11.9126 | 8.6901 | 19.7739 | 34.0364 | 11.8787 | 8.6654 | 19.6823 | 34.0987 | 11.7772 | 8.5913 | 19.3844 | 34.1675 | 11.7094 | 8.5418 | 19.1356 | 34.2406 | 11.6424 | 8.4929 | 19.011 | 34.3179 | 11.5412 | 8.4191 | 18.7837 | 34.4011 | 11.4095 | 8.3231 | 18.5636 | 34.707 | 11.0826 | 8.0846 | 17.6719 | 35.0392 | 11.041 | 8.0543 | 17.1381 | 35.2857 | 11.4247 | 8.3342 | 16.8315 | 35.5283 | 11.2729 | 8.2235 | 16.7916 | 33.8497 | 12.1501 | 8.8634 | 20.624 | 33.8959 | 12.1237 | 8.8441 | 20.4699 | 33.9653 | 12.0569 | 8.7953 | 20.2663 | 34.0502 | 11.986 | 8.7436 | 20.0881 | 34.1464 | 11.9218 | 8.6968 | 19.9384 | 34.2542 | 11.8116 | 8.6164 | 19.6107 | 34.3754 | 11.7401 | 8.5643 | 19.3166 | 34.5088 | 11.6869 | 8.5254 | 19.1328 | 34.6558 | 11.6093 | 8.4688 | 18.8341 | 34.8171 | 11.5268 | 8.4087 | 18.4694 | 34.9799 | 11.3472 | 8.2776 | 18.0005 | 35.1491 | 11.038 | 8.0521 | 17.6292 | 35.3135 | 11.5581 | 8.4315 | 17.3147 | 35.4433 | 11.8682 | 8.6577 | 17.2281 | 33.8724 | 12.1536 | 8.8659 | 20.3518 | 33.9298 | 12.141 | 8.8567 | 19.9737 | 33.9492 | 12.0636 | 8.8002 | 19.8985 | 33.9871 | 11.9775 | 8.7374 | 19.8154 | 34.0374 | 11.883 | 8.6685 | 19.734 | 34.0998 | 11.7487 | 8.5705 | 19.4501 | 34.1687 | 11.6368 | 8.4889 | 19.2098 | 34.242 | 11.5355 | 8.415 | 19.1007 | 34.3188 | 11.4101 | 8.3235 | 18.8765 | 34.399 | 11.2517 | 8.208 | 18.6614 | 34.6658 | 11.1153 | 8.1085 | 17.8328 | 34.8956 | 11.1559 | 8.138 | 17.423 | 35.0905 | 11.6192 | 8.476 | 17.1767 | 35.2424 | 11.5154 | 8.4003 | 17.2029 | 33.8683 | 12.056 | 8.7947 | 20.3567 | 33.9229 | 11.9728 | 8.734 | 19.9808 | 33.9429 | 11.9602 | 8.7248 | 19.9074 | 33.9853 | 11.9451 | 8.7138 | 19.8258 | 34.0448 | 11.8983 | 8.6796 | 19.7412 | 34.1255 | 11.7817 | 8.5946 | 19.4482 | 34.2228 | 11.7107 | 8.5428 | 19.191 | 34.3332 | 11.6251 | 8.4804 | 19.0541 | 34.4558 | 11.5056 | 8.3932 | 18.8216 | 34.5916 | 11.3362 | 8.2696 | 18.6208 | 35.1293 | 11.0537 | 8.0635 | 17.402 | 35.6532 | 10.5342 | 7.6845 | 15.3503 | 35.9528 | 10.5364 | 7.6862 | 13.7486 | 36.0675 | 10.175 | 7.4225 | 12.867 | 33.8582 | 12.0558 | 8.7945 | 20.354 | 33.9063 | 12.0723 | 8.8066 | 19.9622 | 33.919 | 12.101 | 8.8275 | 19.8887 | 33.9508 | 12.0802 | 8.8123 | 19.8184 | 33.9995 | 11.988 | 8.7451 | 19.7417 | 34.0703 | 11.8071 | 8.6131 | 19.4664 | 34.1617 | 11.6315 | 8.485 | 19.2291 | 34.2659 | 11.3955 | 8.3129 | 19.1185 | 34.3842 | 11.4658 | 8.3641 | 18.8822 | 34.5232 | 11.3846 | 8.3049 | 18.3443 | 35.0941 | 11.1672 | 8.1463 | 15.9 | 35.522 | 10.3102 | 7.5212 | 14.1033 | 35.6691 | 9.9539 | 7.2612 | 13.0726 | 35.6358 | 9.9234 | 7.239 | 13.5664
BRAMHALL | HAZEL GROVE | BREDBURY | 389440 | 386463 | 23.5396 | 12.7756 | 9.1821 | 8.3793 | 23.5637 | 12.7181 | 9.1407 | 7.9787 | 23.5824 | 12.6441 | 9.0876 | 7.6864 | 23.6286 | 12.5161 | 8.9955 | 7.1891 | 23.69 | 12.4578 | 8.9536 | 7.174 | 23.7647 | 12.2436 | 8.7997 | 6.8243 | 23.8486 | 12.0115 | 8.6329 | 6.4204 | 23.939 | 11.9254 | 8.571 | 6.0393 | 24.0338 | 11.9184 | 8.566 | 5.6941 | 24.138 | 11.8697 | 8.531 | 5.3119 | 24.5334 | 11.4948 | 8.2615 | 3.9712 | 24.7976 | 11.0755 | 7.9602 | 3.4708 | 24.9575 | 10.9195 | 7.848 | 3.371 | 25.0524 | 10.7859 | 7.752 | 3.6834 | 23.5348 | 12.7988 | 9.1988 | 8.6401 | 23.5539 | 12.728 | 9.1479 | 8.4206 | 23.5898 | 12.6441 | 9.0876 | 8.1466 | 23.6422 | 12.5155 | 8.9951 | 7.6376 | 23.7022 | 12.4698 | 8.9623 | 7.6388 | 23.7703 | 12.3805 | 8.8981 | 7.3184 | 23.8456 | 12.2761 | 8.8231 | 6.9351 | 23.9267 | 12.1732 | 8.7491 | 6.567 | 24.0142 | 12.0648 | 8.6712 | 6.2186 | 24.1067 | 11.9457 | 8.5856 | 5.8625 | 24.283 | 11.629 | 8.358 | 4.8735 | 24.4153 | 11.5876 | 8.3283 | 4.3005 | 24.5058 | 11.5585 | 8.3073 | 3.9459 | 24.5658 | 11.5474 | 8.2994 | 3.902 | 23.5396 | 12.7968 | 9.1973 | 8.417 | 23.5637 | 12.7326 | 9.1511 | 7.9892 | 23.5824 | 12.6356 | 9.0814 | 7.7369 | 23.6286 | 12.4795 | 8.9693 | 7.2262 | 23.6897 | 12.424 | 8.9294 | 7.2402 | 23.7639 | 12.2995 | 8.8399 | 6.901 | 23.8473 | 12.1361 | 8.7224 | 6.5078 | 23.9375 | 11.9636 | 8.5985 | 6.1364 | 24.0309 | 11.8249 | 8.4988 | 5.8067 | 24.1293 | 11.8061 | 8.4853 | 5.4618 | 24.4993 | 11.5859 | 8.327 | 4.2222 | 24.7428 | 11.3437 | 8.153 | 3.7727 | 24.8919 | 11.1239 | 7.995 | 3.7181 | 24.9835 | 11.0199 | 7.9202 | 4.043 | 23.5373 | 12.7807 | 9.1858 | 8.4038 | 23.5606 | 12.7275 | 9.1475 | 8.028 | 23.5838 | 12.6445 | 9.0879 | 7.7909 | 23.6415 | 12.5148 | 8.9947 | 7.3277 | 23.7211 | 12.4431 | 8.9431 | 7.3992 | 23.8213 | 12.2194 | 8.7823 | 7.1303 | 23.9389 | 11.9904 | 8.6178 | 6.8115 | 24.0724 | 12.0142 | 8.6349 | 6.5271 | 24.221 | 11.9941 | 8.6204 | 6.3152 | 24.3874 | 11.9352 | 8.5781 | 6.1039 | 24.9021 | 11.2173 | 8.0621 | 4.3273 | 25.3624 | 10.0485 | 7.2221 | 0.62508 | 25.6233 | 9.1396 | 6.5688 | -2.3703 | 25.7727 | 8.4923 | 6.1036 | -4.1583 | 23.5308 | 12.7775 | 9.1834 | 8.3766 | 23.5556 | 12.7305 | 9.1497 | 7.9522 | 23.5761 | 12.6304 | 9.0777 | 7.7003 | 23.6232 | 12.4701 | 8.9625 | 7.2903 | 23.6912 | 12.3324 | 8.8635 | 7.394 | 23.7744 | 12.2792 | 8.8253 | 7.1912 | 23.8761 | 12.2401 | 8.7972 | 6.9342 | 23.9878 | 12.1991 | 8.7677 | 6.7262 | 24.1178 | 12.1352 | 8.7218 | 6.5015 | 24.2908 | 11.9334 | 8.5768 | 5.608 | 24.8349 | 10.7526 | 7.7281 | 1.411 | 25.1644 | 9.6835 | 6.9597 | -1.9173 | 25.2671 | 9.0598 | 6.5115 | -3.9929 | 25.1897 | 8.9673 | 6.445 | -3.0399
BRIDGEWATER | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 31.455 | 13.1718 | 9.6086 | 14.5013 | 31.5507 | 13.0008 | 9.4839 | 13.9311 | 31.5572 | 12.9521 | 9.4484 | 14.0098 | 31.6029 | 12.8779 | 9.3943 | 13.9546 | 31.6649 | 12.9827 | 9.4707 | 13.8554 | 31.7452 | 12.9212 | 9.4259 | 13.6646 | 31.8251 | 12.8645 | 9.3845 | 13.4855 | 31.904 | 12.7921 | 9.3317 | 13.3881 | 31.9473 | 12.7324 | 9.2881 | 13.2648 | 31.9929 | 12.6784 | 9.2487 | 13.1464 | 32.1609 | 12.3851 | 9.0348 | 12.7079 | 32.2591 | 12.1223 | 8.8431 | 12.4671 | 32.2935 | 12.7827 | 9.3248 | 12.393 | 32.2698 | 13.4003 | 9.7754 | 12.4333 | 31.372 | 13.4545 | 9.8149 | 14.9282 | 31.4017 | 13.3889 | 9.767 | 14.7662 | 31.4655 | 13.3341 | 9.727 | 14.6827 | 31.5593 | 13.2464 | 9.663 | 14.5597 | 31.6221 | 13.2023 | 9.6309 | 14.3748 | 31.6833 | 13.1407 | 9.586 | 14.1578 | 31.7472 | 13.0858 | 9.5459 | 13.9149 | 31.8111 | 13.0378 | 9.5109 | 13.7454 | 31.8752 | 12.9735 | 9.464 | 13.5639 | 31.9398 | 12.8993 | 9.4098 | 13.3611 | 32.0908 | 12.7979 | 9.3359 | 12.9193 | 32.199 | 12.7258 | 9.2833 | 12.5843 | 32.2438 | 13.1713 | 9.6083 | 12.434 | 32.2313 | 13.663 | 9.9669 | 12.4197 | 31.455 | 13.4536 | 9.8142 | 14.5051 | 31.5507 | 13.389 | 9.7671 | 13.9425 | 31.5572 | 13.313 | 9.7117 | 14.0278 | 31.6029 | 13.2313 | 9.652 | 13.9783 | 31.6647 | 13.1443 | 9.5886 | 13.8846 | 31.7448 | 13.0701 | 9.5345 | 13.6996 | 31.8244 | 12.9961 | 9.4805 | 13.5261 | 31.9033 | 12.9409 | 9.4402 | 13.434 | 31.947 | 12.8946 | 9.4064 | 13.317 | 31.9918 | 12.8407 | 9.3671 | 13.2079 | 32.1568 | 12.6358 | 9.2176 | 12.7848 | 32.2524 | 12.5108 | 9.1264 | 12.5641 | 32.2854 | 12.9395 | 9.4392 | 12.4966 | 32.2612 | 13.6246 | 9.9389 | 12.5366 | 31.4478 | 13.1802 | 9.6147 | 14.5271 | 31.5351 | 13.0484 | 9.5186 | 13.9828 | 31.5319 | 13.0838 | 9.5445 | 14.0857 | 31.5702 | 13.0452 | 9.5163 | 14.0532 | 31.6253 | 13.0005 | 9.4837 | 13.9654 | 31.6987 | 12.9173 | 9.423 | 13.7948 | 31.7713 | 12.8709 | 9.3892 | 13.6114 | 31.8426 | 12.8125 | 9.3466 | 13.5219 | 31.9113 | 12.7421 | 9.2952 | 13.418 | 31.9781 | 12.6882 | 9.2559 | 13.309 | 32.1804 | 12.3689 | 9.0229 | 12.8207 | 32.3141 | 11.9218 | 8.6968 | 11.6397 | 32.2419 | 12.3646 | 9.0198 | 10.7532 | 32.1217 | 12.8366 | 9.3642 | 10.1467 | 31.4404 | 13.1843 | 9.6178 | 14.534 | 31.5213 | 13.1531 | 9.595 | 13.9955 | 31.508 | 13.1604 | 9.6003 | 14.1072 | 31.5304 | 13.1097 | 9.5634 | 14.088 | 31.5688 | 13.0063 | 9.4879 | 14.0186 | 31.6227 | 12.941 | 9.4403 | 13.8594 | 31.6766 | 12.8581 | 9.3798 | 13.7081 | 31.727 | 12.798 | 9.336 | 13.6373 | 31.7743 | 12.7272 | 9.2843 | 13.5418 | 31.8603 | 12.613 | 9.201 | 13.234 | 32.1987 | 11.9442 | 8.7132 | 11.8209 | 32.2064 | 11.7689 | 8.5853 | 10.7053 | 32.1117 | 12.7176 | 9.2773 | 10.1085 | 31.9534 | 12.722 | 9.2805 | 10.4538
BRINKSWAY | ADSWOOD | BREDBURY | 388434 | 389885 | 30.6308 | 13.3967 | 9.7727 | 17.8452 | 30.7047 | 13.246 | 9.6628 | 17.2181 | 30.7501 | 13.1662 | 9.6046 | 17.1856 | 30.8269 | 13.0279 | 9.5037 | 16.9448 | 30.9085 | 12.9205 | 9.4253 | 16.8906 | 30.9976 | 12.8252 | 9.3558 | 16.6809 | 31.1008 | 12.7218 | 9.2804 | 16.3815 | 31.2159 | 12.6548 | 9.2315 | 16.3396 | 31.3435 | 12.5635 | 9.1649 | 16.1075 | 31.4861 | 12.4586 | 9.0884 | 15.8794 | 32.1455 | 11.9619 | 8.726 | 14.9572 | 32.7876 | 11.3282 | 8.2637 | 13.9983 | 33.1488 | 11.2388 | 8.1986 | 13.2235 | 33.3528 | 11.0613 | 8.0691 | 12.8656 | 30.6085 | 13.3837 | 9.7632 | 18.1225 | 30.6653 | 13.1572 | 9.598 | 17.7444 | 30.7513 | 13.099 | 9.5555 | 17.666 | 30.8471 | 13.008 | 9.4892 | 17.3773 | 30.934 | 12.9805 | 9.4691 | 17.2828 | 31.0331 | 12.9173 | 9.423 | 17.0495 | 31.1397 | 12.7273 | 9.2844 | 16.7171 | 31.2558 | 12.7643 | 9.3114 | 16.6254 | 31.3821 | 12.7383 | 9.2924 | 16.3405 | 31.517 | 12.6889 | 9.2564 | 16.0806 | 31.9737 | 12.5415 | 9.1489 | 15.3974 | 32.3752 | 12.3018 | 8.974 | 14.6701 | 32.6119 | 12.1417 | 8.8572 | 14.0638 | 32.757 | 12.0489 | 8.7895 | 13.819 | 30.64 | 13.3747 | 9.7567 | 17.8522 | 30.7169 | 13.2309 | 9.6518 | 17.2399 | 30.7643 | 13.1016 | 9.5574 | 17.2178 | 30.8418 | 12.9684 | 9.4602 | 16.9901 | 30.9153 | 12.9813 | 9.4696 | 16.9463 | 31.0015 | 12.9204 | 9.4252 | 16.7493 | 31.1 | 12.8303 | 9.3595 | 16.4642 | 31.2085 | 12.7822 | 9.3245 | 16.4313 | 31.327 | 12.6964 | 9.2619 | 16.2157 | 31.4582 | 12.6174 | 9.2042 | 16.0156 | 32.0678 | 12.2536 | 8.9388 | 15.2664 | 32.5771 | 11.9305 | 8.7031 | 14.5734 | 32.8559 | 11.5175 | 8.4019 | 14.0571 | 32.9799 | 11.5026 | 8.391 | 14.1081 | 30.6397 | 13.3992 | 9.7745 | 17.856 | 30.7166 | 13.242 | 9.6598 | 17.2388 | 30.7709 | 13.1161 | 9.568 | 17.2145 | 30.8505 | 12.9579 | 9.4526 | 16.9793 | 30.9288 | 12.7973 | 9.3355 | 16.9262 | 31.0414 | 12.8045 | 9.3407 | 16.7086 | 31.1841 | 12.6808 | 9.2504 | 16.3803 | 31.35 | 12.6248 | 9.2096 | 16.3045 | 31.5295 | 12.516 | 9.1303 | 16.0532 | 31.7163 | 12.399 | 9.0449 | 15.8346 | 32.6791 | 11.7081 | 8.5409 | 14.6373 | 33.7073 | 10.5849 | 7.7216 | 10.811 | 34.2962 | 9.7423 | 7.1069 | 7.1043 | 34.5861 | 9.1834 | 6.6992 | 5.0208 | 30.6355 | 13.4021 | 9.7767 | 17.8637 | 30.7181 | 13.2674 | 9.6784 | 17.2437 | 30.7755 | 13.0854 | 9.5456 | 17.2324 | 30.8341 | 13.004 | 9.4862 | 17.0216 | 30.9107 | 12.9801 | 9.4688 | 16.9824 | 31.0283 | 12.8444 | 9.3698 | 16.7908 | 31.1845 | 12.7188 | 9.2782 | 16.498 | 31.3644 | 12.633 | 9.2156 | 16.4606 | 31.5624 | 12.4958 | 9.1155 | 16.1985 | 31.9039 | 12.2785 | 8.957 | 15.5986 | 32.9483 | 11.012 | 8.0331 | 12.3214 | 33.6608 | 10.1693 | 7.4183 | 9.3984 | 34.0791 | 9.6041 | 7.0061 | 7.1798 | 34.134 | 9.3269 | 6.8038 | 6.3398
BROADHEATH | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5627 | 2.6844 | 0.44197 | 0.31765 | -3.3983 | 2.6844 | 0.44197 | 0.31765 | -7.5595 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -2.0375 | 2.6844 | 0.44197 | 0.31765 | -6.2792 | 2.6844 | 0.44197 | 0.31765 | -5.2739
BROADWAY | LANCASTER | HEYSHAM | 344792 | 464471 | 25.7378 | 8.4996 | 6.2004 | 16.094 | 25.7916 | 8.3329 | 6.0788 | 16.0385 | 25.8301 | 8.1739 | 5.9627 | 15.9101 | 25.8893 | 7.816 | 5.7016 | 15.6558 | 25.9721 | 7.4307 | 5.4206 | 15.2622 | 26.0738 | 6.866 | 5.0086 | 14.9609 | 26.1907 | 6.6331 | 4.8388 | 14.573 | 26.3177 | 6.4686 | 4.7188 | 14.0434 | 26.454 | 6.339 | 4.6242 | 13.6566 | 26.6041 | 6.181 | 4.5089 | 13.1978 | 27.2888 | 5.6029 | 4.0872 | 11.329 | 27.9464 | 5.4538 | 3.9785 | 10.1234 | 28.4419 | 7.8642 | 5.7368 | 9.3907 | 28.9341 | 7.8726 | 5.743 | 9.8211 | 25.7149 | 8.5589 | 6.2436 | 16.1597 | 25.7453 | 8.5554 | 6.241 | 16.116 | 25.8016 | 8.5207 | 6.2157 | 15.9632 | 25.8717 | 8.4303 | 6.1498 | 15.704 | 25.9538 | 8.3258 | 6.0736 | 15.3591 | 26.0461 | 8.2144 | 5.9923 | 15.0883 | 26.1497 | 8.0861 | 5.8987 | 14.727 | 26.2605 | 7.9536 | 5.802 | 14.2278 | 26.3785 | 7.8583 | 5.7325 | 13.9276 | 26.5024 | 7.7154 | 5.6283 | 13.5174 | 26.8635 | 7.2973 | 5.3233 | 12.1466 | 27.2126 | 6.8855 | 5.0229 | 11.0754 | 27.5518 | 7.9472 | 5.7974 | 10.0648 | 27.8408 | 9.5388 | 6.9584 | 10.1043 | 25.7379 | 8.5539 | 6.24 | 16.103 | 25.792 | 8.5226 | 6.2171 | 16.0537 | 25.831 | 8.422 | 6.1437 | 15.952 | 25.8908 | 8.2996 | 6.0544 | 15.7072 | 25.9739 | 8.0782 | 5.893 | 15.3379 | 26.0757 | 7.9047 | 5.7664 | 15.0535 | 26.1927 | 7.7532 | 5.6559 | 14.6828 | 26.3199 | 7.5674 | 5.5203 | 14.1763 | 26.455 | 7.4129 | 5.4076 | 13.8074 | 26.5982 | 7.2147 | 5.263 | 13.3989 | 27.2124 | 6.6758 | 4.8699 | 11.7406 | 27.683 | 6.6241 | 4.8322 | 10.7587 | 28.0837 | 8.9205 | 6.5074 | 10.0983 | 28.411 | 8.6479 | 6.3085 | 10.6348 | 25.7352 | 8.4981 | 6.1992 | 16.0993 | 25.7909 | 8.3466 | 6.0887 | 16.0438 | 25.837 | 8.1118 | 5.9174 | 15.9249 | 25.9168 | 7.8262 | 5.7091 | 15.6753 | 26.0324 | 7.3565 | 5.3665 | 15.3035 | 26.1872 | 6.8691 | 5.0109 | 15.0162 | 26.3807 | 6.5726 | 4.7946 | 14.6241 | 26.6051 | 6.3896 | 4.6611 | 14.0958 | 26.8446 | 6.2567 | 4.5642 | 13.8304 | 27.082 | 6.0934 | 4.4451 | 13.4712 | 28.2002 | 5.2438 | 3.8253 | 10.8535 | 25.8265 | 4.1893 | 3.056 | 5.4267 | 29.952 | 5.7348 | 4.1835 | 0.61909 | 30.2786 | 5.199 | 3.7926 | -1.4153 | 25.7292 | 8.5027 | 6.2026 | 16.1209 | 25.7913 | 8.3739 | 6.1086 | 16.07 | 25.8433 | 8.113 | 5.9183 | 15.9466 | 25.9242 | 7.8199 | 5.7045 | 15.7225 | 26.0411 | 7.2983 | 5.324 | 15.373 | 26.1986 | 6.8985 | 5.0323 | 15.1246 | 26.4045 | 6.5405 | 4.7712 | 14.7759 | 26.6403 | 6.4223 | 4.685 | 14.3002 | 26.8776 | 6.3436 | 4.6276 | 13.9279 | 27.1697 | 6.1372 | 4.477 | 12.7386 | 28.4272 | 7.5565 | 5.5124 | 6.8443 | 29.3251 | 6.2361 | 4.5492 | 1.846 | 29.6913 | 5.3782 | 3.9234 | -1.6633 | 29.6697 | 5.4952 | 4.0087 | -0.20986
BUCKSHAW | LEYLAND | PENWORTHAM WEST / STANAH | 356748 | 421312 | 27.3272 | 14.0348 | 10.0871 | 16.118 | 27.3921 | 13.8809 | 9.9764 | 15.2884 | 27.426 | 13.7506 | 9.8828 | 14.8342 | 27.476 | 13.6339 | 9.799 | 14.6562 | 27.5446 | 13.4682 | 9.6798 | 14.4198 | 27.6289 | 13.1959 | 9.4842 | 14.1508 | 27.724 | 12.9379 | 9.2987 | 13.8708 | 27.8272 | 12.939 | 9.2995 | 13.5925 | 27.9392 | 12.9425 | 9.302 | 13.3004 | 28.0592 | 12.8832 | 9.2594 | 13.0021 | 28.8798 | 12.426 | 8.9308 | 11.7412 | 29.9778 | 12.1187 | 8.71 | 10.671 | 30.9086 | 12.8233 | 9.2164 | 10.0715 | 31.8943 | 12.7599 | 9.1708 | 9.4922 | 27.2865 | 14.1122 | 10.1427 | 16.5579 | 27.3161 | 14.0046 | 10.0654 | 16.1437 | 27.3645 | 13.9158 | 10.0015 | 15.7841 | 27.4156 | 13.8343 | 9.943 | 15.5838 | 27.4767 | 13.7384 | 9.874 | 15.3507 | 27.5449 | 13.6298 | 9.796 | 15.0959 | 27.6206 | 13.5555 | 9.7426 | 14.825 | 27.7006 | 13.4632 | 9.6763 | 14.5503 | 27.7849 | 13.3686 | 9.6083 | 14.2531 | 27.8714 | 13.2792 | 9.544 | 13.964 | 28.3966 | 12.9005 | 9.2719 | 13.0417 | 29.0306 | 12.6441 | 9.0876 | 12.2675 | 29.7008 | 13.1296 | 9.4365 | 11.6611 | 30.3078 | 13.4857 | 9.6924 | 11.1901 | 27.3276 | 14.1115 | 10.1422 | 16.1219 | 27.3933 | 14.008 | 10.0679 | 15.2962 | 27.4283 | 13.8766 | 9.9734 | 14.8458 | 27.4797 | 13.6916 | 9.8404 | 14.6715 | 27.5498 | 13.4519 | 9.6681 | 14.4402 | 27.6354 | 13.0917 | 9.4093 | 14.1773 | 27.7318 | 13.169 | 9.4648 | 13.9033 | 27.8363 | 13.1571 | 9.4563 | 13.6305 | 27.9484 | 13.1046 | 9.4185 | 13.3483 | 28.0653 | 13.0418 | 9.3734 | 13.0742 | 28.7542 | 12.7116 | 9.1361 | 11.9635 | 29.4197 | 12.3317 | 8.863 | 11.2359 | 30.1357 | 13.1951 | 9.4836 | 10.7932 | 30.7859 | 13.1447 | 9.4474 | 10.5027 | 27.3253 | 14.0375 | 10.0891 | 16.1339 | 27.3931 | 13.8802 | 9.976 | 15.3254 | 27.4397 | 13.7437 | 9.8779 | 14.8982 | 27.5121 | 13.5467 | 9.7363 | 14.7498 | 27.6098 | 13.3219 | 9.5747 | 14.5553 | 27.7522 | 13.1498 | 9.451 | 14.3268 | 27.9281 | 13.1561 | 9.4556 | 14.0815 | 28.1257 | 13.0927 | 9.41 | 13.8353 | 28.3494 | 13.0016 | 9.3445 | 13.5836 | 28.5701 | 12.8866 | 9.2619 | 13.337 | 30.186 | 12.1575 | 8.7378 | 11.6729 | 32.0967 | 11.6646 | 8.3835 | 9.7122 | 33.3057 | 12.037 | 8.6513 | 7.9144 | 33.7298 | 11.7254 | 8.4273 | 6.211 | 27.3333 | 14.0329 | 10.0857 | 16.1009 | 27.4192 | 13.7836 | 9.9066 | 15.2397 | 27.4822 | 13.59 | 9.7674 | 14.8021 | 27.57 | 13.354 | 9.5978 | 14.6666 | 27.6852 | 12.9962 | 9.3406 | 14.4865 | 27.8607 | 12.7351 | 9.153 | 14.2692 | 28.0813 | 12.7157 | 9.1391 | 14.0142 | 28.341 | 12.662 | 9.1004 | 13.7547 | 28.6308 | 12.5786 | 9.0405 | 13.4636 | 29.0344 | 12.4213 | 8.9274 | 13.064 | 30.9107 | 12.3974 | 8.9103 | 10.892 | 32.5632 | 11.7007 | 8.4096 | 8.5794 | 33.3195 | 11.5136 | 8.2751 | 7.0037 | 33.3292 | 11.3869 | 8.184 | 6.8928
BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 20.9599 | 12.1425 | 8.8578 | 16.5626 | 21.0152 | 10.7597 | 7.8491 | 16.4327 | 21.0596 | 9.2415 | 6.7416 | 16.1648 | 21.1225 | 7.6129 | 5.5535 | 16.09 | 21.2079 | 6.0573 | 4.4187 | 15.9179 | 21.3043 | 4.3177 | 3.1497 | 15.5259 | 21.4115 | 4.2472 | 3.0983 | 15.0896 | 21.5286 | 4.1909 | 3.0572 | 14.8029 | 21.6591 | 4.0903 | 2.9838 | 14.3545 | 21.8257 | 3.9908 | 2.9112 | 13.919 | 22.5966 | 3.9042 | 2.8481 | 12.5375 | 23.1713 | 6.0695 | 4.4276 | 11.8211 | 23.4034 | 10.5118 | 7.6682 | 11.7009 | 23.579 | 11.3081 | 8.2491 | 11.8539 | 20.9347 | 12.1112 | 8.835 | 16.6794 | 20.9685 | 10.5238 | 7.677 | 16.6399 | 21.0243 | 8.9695 | 6.5431 | 16.3173 | 21.0762 | 7.4326 | 5.422 | 16.2324 | 21.1446 | 5.9126 | 4.3132 | 16.0753 | 21.2213 | 4.352 | 3.1747 | 15.7427 | 21.303 | 4.2664 | 3.1123 | 15.3558 | 21.3872 | 4.2001 | 3.0639 | 15.0812 | 21.4751 | 4.128 | 3.0113 | 14.7783 | 21.5656 | 4.0493 | 2.9539 | 14.4512 | 21.9207 | 4.0498 | 2.9543 | 13.5072 | 22.2845 | 5.381 | 3.9254 | 12.7478 | 22.5733 | 8.2327 | 6.0057 | 12.3139 | 22.8042 | 9.3601 | 6.828 | 12.0284 | 20.96 | 12.1082 | 8.8328 | 16.5675 | 21.0153 | 10.5173 | 7.6723 | 16.443 | 21.0599 | 8.8968 | 6.4901 | 16.1825 | 21.1229 | 7.2903 | 5.3181 | 16.113 | 21.2082 | 5.7314 | 4.181 | 15.9483 | 21.3042 | 4.1009 | 2.9915 | 15.5707 | 21.4112 | 4.0242 | 2.9356 | 15.1466 | 21.5281 | 3.9559 | 2.8858 | 14.8696 | 21.6573 | 3.87 | 2.8231 | 14.4394 | 21.8178 | 3.7905 | 2.7651 | 14.0446 | 22.5471 | 3.8528 | 2.8106 | 12.8128 | 23.0635 | 6.1425 | 4.4809 | 12.2157 | 23.262 | 10.9369 | 7.9783 | 12.138 | 23.3894 | 11.7076 | 8.5405 | 12.311 | 20.9588 | 12.1444 | 8.8591 | 16.5726 | 21.0194 | 10.7794 | 7.8634 | 16.4539 | 21.083 | 9.2448 | 6.7439 | 16.2015 | 21.1747 | 7.617 | 5.5565 | 16.1434 | 21.2929 | 6.0396 | 4.4058 | 16.0051 | 21.4485 | 4.336 | 3.1631 | 15.6791 | 21.6486 | 4.2508 | 3.1009 | 15.2798 | 21.8786 | 4.1657 | 3.0388 | 15.0072 | 22.1213 | 4.0656 | 2.9658 | 14.7042 | 22.3915 | 3.9485 | 2.8804 | 14.4232 | 22.9174 | 3.7174 | 2.7118 | 12.5154 | 23.9359 | 5.1542 | 3.7599 | 8.3016 | 24.3026 | 8.8985 | 6.4914 | 5.0506 | 24.4737 | 9.2393 | 6.74 | 2.9063 | 20.9524 | 12.1498 | 8.8631 | 16.5919 | 21.0186 | 12.2835 | 8.9606 | 16.4666 | 21.0904 | 12.2101 | 8.9071 | 16.2178 | 21.1802 | 12.0282 | 8.7744 | 16.1815 | 21.3129 | 11.7811 | 8.5942 | 16.0333 | 21.4751 | 11.6213 | 8.4776 | 15.7211 | 21.6735 | 11.5197 | 8.4035 | 15.3683 | 21.8968 | 11.4503 | 8.3528 | 15.172 | 22.2193 | 11.3387 | 8.2714 | 14.725 | 22.6643 | 11.1331 | 8.1215 | 13.6837 | 23.3919 | 11.0394 | 8.0531 | 9.002 | 23.8657 | 10.0228 | 7.3115 | 5.2146 | 24.0294 | 9.5426 | 6.9612 | 3.1516 | 23.937 | 9.5355 | 6.956 | 3.9018
BURNLEY CENTRE | BURNLEY | ROCHDALE | 384308 | 432288 | 29.8312 | 11.8699 | 8.6589 | 15.0799 | 29.8886 | 11.4681 | 8.3658 | 14.7892 | 29.9211 | 10.9862 | 8.0143 | 14.7439 | 29.9692 | 10.3552 | 7.5539 | 14.6784 | 30.0304 | 10.228 | 7.4612 | 14.4924 | 30.1054 | 9.8952 | 7.2184 | 14.1623 | 30.1871 | 9.7724 | 7.1288 | 13.9219 | 30.2745 | 9.6684 | 7.0529 | 13.7965 | 30.364 | 9.5568 | 6.9716 | 13.4904 | 30.4466 | 9.4381 | 6.885 | 13.2802 | 30.6962 | 8.9184 | 6.5059 | 12.6576 | 30.8582 | 8.8868 | 6.4828 | 12.1988 | 30.94 | 10.422 | 7.6027 | 11.9885 | 30.9748 | 10.7676 | 7.8548 | 11.9375 | 29.8304 | 11.8977 | 8.6792 | 15.2148 | 29.8956 | 11.6523 | 8.5002 | 15.0471 | 29.9826 | 11.3963 | 8.3134 | 14.8476 | 30.0666 | 11.146 | 8.1309 | 14.6393 | 30.1473 | 10.8819 | 7.9382 | 14.3187 | 30.2378 | 10.6103 | 7.74 | 13.8555 | 30.3383 | 10.5122 | 7.6685 | 13.45 | 30.4472 | 10.4427 | 7.6178 | 13.1861 | 30.5617 | 10.3202 | 7.5284 | 12.6225 | 30.6848 | 10.152 | 7.4058 | 11.7614 | 30.8486 | 10.0726 | 7.3478 | 11.4756 | 30.9589 | 10.1637 | 7.4143 | 11.3027 | 31.0117 | 11.0508 | 8.0614 | 11.2155 | 31.0275 | 11.8309 | 8.6305 | 11.2414 | 29.8314 | 11.8978 | 8.6793 | 15.0918 | 29.8888 | 11.6818 | 8.5217 | 14.934 | 29.9213 | 11.3721 | 8.2958 | 14.7846 | 29.9695 | 11.0467 | 8.0584 | 14.734 | 30.0304 | 10.6998 | 7.8053 | 14.6374 | 30.105 | 10.3147 | 7.5244 | 14.3599 | 30.1863 | 10.19 | 7.4335 | 14.0647 | 30.2734 | 10.0921 | 7.362 | 13.9223 | 30.3616 | 9.9447 | 7.2545 | 13.8154 | 30.4406 | 9.7428 | 7.1072 | 13.5153 | 30.6747 | 9.4285 | 6.8779 | 12.8999 | 30.8188 | 9.6435 | 7.0348 | 12.4874 | 30.8864 | 11.2717 | 8.2225 | 12.2973 | 30.915 | 11.7249 | 8.5532 | 12.2433 | 29.8303 | 11.8732 | 8.6613 | 15.0838 | 29.8873 | 11.4548 | 8.3561 | 14.8101 | 29.921 | 10.9345 | 7.9766 | 14.7513 | 29.9724 | 10.2713 | 7.4927 | 14.6834 | 30.0395 | 10.2237 | 7.458 | 14.5422 | 30.1225 | 9.8662 | 7.1972 | 14.2242 | 30.2157 | 9.731 | 7.0986 | 13.9366 | 30.3177 | 9.6261 | 7.0221 | 13.7625 | 30.4215 | 9.5087 | 6.9364 | 13.5891 | 30.5343 | 9.3638 | 6.8307 | 13.3102 | 30.8477 | 8.6579 | 6.3158 | 12.1303 | 31.15 | 8.0576 | 5.8779 | 8.6143 | 31.3276 | 8.9669 | 6.5412 | 5.69 | 31.4054 | 8.8401 | 6.4487 | 3.8213 | 29.8107 | 11.8839 | 8.6691 | 15.1182 | 29.8514 | 11.6441 | 8.4942 | 14.8723 | 29.868 | 11.0675 | 8.0736 | 14.8384 | 29.8964 | 11.1004 | 8.0976 | 14.8131 | 29.9391 | 10.6438 | 7.7645 | 14.7439 | 29.9945 | 10.4552 | 7.6269 | 14.4901 | 30.0605 | 10.3363 | 7.5402 | 14.2277 | 30.1297 | 10.2233 | 7.4578 | 14.1119 | 30.2114 | 10.0868 | 7.3582 | 13.9592 | 30.3247 | 9.9433 | 7.2535 | 13.1354 | 30.68 | 9.8443 | 7.1813 | 9.3307 | 30.8988 | 8.7323 | 6.3701 | 6.0907 | 30.9785 | 8.6527 | 6.312 | 4.1496 | 30.9189 | 8.6134 | 6.2834 | 4.767
BURNLEY NORTH | BURNLEY | ROCHDALE | 384418 | 434168 | 17.4841 | 17.4841 | 17.2155 | 9.124 | 17.5808 | 17.5808 | 17.0913 | 8.9155 | 17.7465 | 17.7465 | 16.9504 | 8.7903 | 17.9404 | 17.9404 | 16.8456 | 8.5627 | 18.1735 | 18.1735 | 16.8014 | 8.4014 | 18.3471 | 18.3471 | 16.7414 | 8.2097 | 18.4592 | 18.4592 | 16.6848 | 7.9006 | 18.5845 | 18.5845 | 16.6371 | 7.6541 | 18.7213 | 18.7213 | 16.5881 | 7.3264 | 18.8711 | 18.8711 | 16.5175 | 6.8822 | 19.516 | 19.516 | 16.2918 | 5.2677 | 20.0713 | 20.0713 | 16.2515 | 4.1977 | 20.4078 | 20.4078 | 17.4043 | 3.4849 | 20.5883 | 20.5883 | 17.3883 | 2.8275 | 17.5005 | 17.5005 | 17.2318 | 9.3073 | 17.6049 | 17.6049 | 17.1957 | 9.2497 | 17.7704 | 17.7704 | 17.1342 | 9.0699 | 17.9406 | 17.9406 | 17.0617 | 8.8158 | 18.1319 | 18.1319 | 17.0008 | 8.6497 | 18.3132 | 18.3132 | 16.9411 | 8.4704 | 18.405 | 18.405 | 16.9009 | 8.1726 | 18.5055 | 18.5055 | 16.8683 | 7.9405 | 18.6135 | 18.6135 | 16.8345 | 7.6908 | 18.7273 | 18.7273 | 16.7916 | 7.3944 | 19.2021 | 19.2021 | 16.6492 | 6.2468 | 19.5641 | 19.5641 | 16.5765 | 5.4049 | 19.7455 | 19.7455 | 17.2703 | 5.0416 | 19.8284 | 19.8284 | 17.9707 | 4.9008 | 17.4945 | 17.4945 | 17.2341 | 9.1292 | 17.5947 | 17.5947 | 17.2339 | 8.9251 | 17.7625 | 17.7625 | 17.1677 | 8.8052 | 17.9572 | 17.9572 | 17.077 | 8.5845 | 18.1887 | 18.1887 | 16.9916 | 8.4295 | 18.3502 | 18.3502 | 16.9073 | 8.2449 | 18.4577 | 18.4577 | 16.8553 | 7.9447 | 18.5768 | 18.5768 | 16.8208 | 7.6618 | 18.7047 | 18.7047 | 16.7767 | 7.3521 | 18.8401 | 18.8401 | 16.7265 | 6.947 | 19.4348 | 19.4348 | 16.5788 | 5.4818 | 19.8681 | 19.8681 | 16.6172 | 4.6379 | 20.0781 | 20.0781 | 17.8848 | 4.4416 | 20.1799 | 20.1799 | 17.93 | 4.4835 | 17.4973 | 17.4973 | 17.2177 | 9.1357 | 17.5973 | 17.5973 | 17.0792 | 8.9389 | 17.7617 | 17.7617 | 16.9576 | 8.8253 | 17.9501 | 17.9501 | 16.849 | 8.6095 | 18.1722 | 18.1722 | 16.8064 | 8.4626 | 18.3832 | 18.3832 | 16.7319 | 8.2861 | 18.525 | 18.525 | 16.6753 | 7.9928 | 18.6907 | 18.6907 | 16.632 | 7.7716 | 18.8648 | 18.8648 | 16.5798 | 7.5546 | 19.0577 | 19.0577 | 16.5261 | 7.2641 | 19.9229 | 19.9229 | 16.1912 | 5.153 | 20.8052 | 20.8052 | 15.714 | 0.62319 | 21.3327 | 21.3327 | 16.4627 | -2.9886 | 21.5799 | 21.5799 | 16.249 | -5.0008 | 17.5139 | 17.5139 | 17.2181 | 9.1283 | 17.66 | 17.66 | 17.0757 | 8.9035 | 17.8523 | 17.8523 | 17.0082 | 8.7812 | 18.0459 | 18.0459 | 17.0489 | 8.5764 | 18.2685 | 18.2685 | 17.0022 | 8.4485 | 18.39 | 18.39 | 16.9335 | 8.3032 | 18.5458 | 18.5458 | 16.8681 | 8.0364 | 18.7135 | 18.7135 | 16.8288 | 7.8529 | 18.9006 | 18.9006 | 16.7972 | 7.5215 | 19.1431 | 19.1431 | 16.7213 | 6.668 | 20.0475 | 20.0475 | 17.3774 | 3.0798 | 20.7001 | 20.7001 | 16.84 | -0.27326 | 21.0453 | 21.0453 | 16.5807 | -2.8688 | 21.0721 | 21.0721 | 16.4082 | -3.5651
BURROW BECK | LANCASTER | HEYSHAM | 347903 | 458401 | 4.031 | 3.0133 | 2.1657 | 4.031 | 4.1649 | 2.4277 | 1.7449 | 4.1649 | 4.3776 | 1.9019 | 1.3669 | 4.3776 | 4.603 | 1.3469 | 0.96805 | 4.603 | 4.8612 | 0.86667 | 0.6229 | 4.6334 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.2353 | 2.6844 | 0.44197 | 0.31765 | 1.4749 | 2.6844 | 0.44197 | 0.31765 | -0.72084 | 2.6844 | 0.44197 | 0.31765 | -2.3897 | 2.6844 | 0.44197 | 0.31765 | -2.2226 | 1.2018 | 0.19787 | 0.14221 | -0.92463 | 4.061 | 3.1892 | 2.2921 | 4.061 | 4.2224 | 3.058 | 2.1979 | 4.2224 | 4.4421 | 2.8617 | 2.0568 | 4.4421 | 4.6493 | 2.7421 | 1.9708 | 4.6493 | 4.881 | 2.6577 | 1.9101 | 4.881 | 5.1413 | 2.4647 | 1.7714 | 5.1413 | 5.4362 | 2.3435 | 1.6844 | 4.7563 | 5.7472 | 2.2181 | 1.5942 | 4.1857 | 6.0774 | 2.0101 | 1.4447 | 3.5774 | 6.4226 | 1.9561 | 1.4059 | 2.9138 | 7.1122 | 1.6881 | 1.2133 | 1.4387 | 7.4769 | 1.3852 | 0.99555 | -0.38848 | 7.6233 | 2.2854 | 1.6426 | -0.97743 | 7.6846 | 3.5827 | 2.5749 | -0.44445 | 4.031 | 3.1904 | 2.293 | 4.031 | 4.1649 | 2.6535 | 1.9071 | 4.1649 | 4.3776 | 2.0676 | 1.486 | 4.3776 | 4.603 | 1.5747 | 1.1317 | 4.603 | 4.8597 | 0.92701 | 0.66626 | 4.6843 | 3.0559 | 0.50312 | 0.36161 | 3.0559 | 2.1585 | 0.35538 | 0.25542 | 2.1585 | 1.5046 | 0.24772 | 0.17804 | 1.5046 | 0.65415 | 0.1077 | 0.077407 | 0.65415 | 2.6844 | 0.44197 | 0.31765 | 1.6484 | 2.6844 | 0.44197 | 0.31765 | -0.40196 | 2.6844 | 0.44197 | 0.31765 | -1.9783 | 2.6844 | 0.44197 | 0.31765 | -1.8105 | 6.0749 | 1.0002 | 0.71886 | -0.55735 | 4.0306 | 3.0167 | 2.1682 | 4.0306 | 4.1653 | 2.4313 | 1.7474 | 4.1653 | 4.3747 | 1.974 | 1.4187 | 4.3747 | 4.5945 | 1.4092 | 1.0129 | 4.5945 | 4.8438 | 0.87965 | 0.63222 | 4.8438 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5118 | 2.6844 | 0.44197 | 0.31765 | 0.62683 | 2.6844 | 0.44197 | 0.31765 | -3.1113 | 2.6844 | 0.44197 | 0.31765 | -5.4715 | 2.6844 | 0.44197 | 0.31765 | -6.1988 | 4.0974 | 2.9918 | 2.1503 | 4.0974 | 4.2924 | 2.3576 | 1.6945 | 4.2924 | 4.5005 | 1.9618 | 1.41 | 4.5005 | 4.6981 | 1.4161 | 1.0178 | 4.6981 | 4.796 | 0.78963 | 0.56752 | 4.7257 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.2041 | 2.6844 | 0.44197 | 0.31765 | -1.8567 | 2.6844 | 0.44197 | 0.31765 | -5.4578 | 2.6844 | 0.44197 | 0.31765 | -6.8181 | 2.6844 | 0.44197 | 0.31765 | -5.0754
BURSCOUGH BRIDGE | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 344595 | 412486 | 11.6319 | 11.6319 | 11.6319 | 8.5198 | 11.6959 | 11.6959 | 11.6959 | 7.2641 | 11.7302 | 11.7302 | 10.5658 | 6.5305 | 11.7863 | 11.7863 | 8.8056 | 6.1099 | 11.8592 | 9.8304 | 7.0653 | 5.8231 | 11.9518 | 7.4356 | 5.3441 | 5.3706 | 12.0594 | 7.2856 | 5.2363 | 4.9167 | 12.177 | 7.1274 | 5.1226 | 4.4156 | 12.3005 | 6.9816 | 5.0178 | 3.9575 | 12.4506 | 6.8007 | 4.8878 | 3.2925 | 13.3302 | 6.0813 | 4.3708 | 0.96736 | 14.3438 | 5.7308 | 4.1188 | -0.48016 | 15.1154 | 10.992 | 7.9002 | -0.97609 | 15.916 | 15.916 | 11.6385 | -1.036 | 11.5872 | 11.5872 | 11.5872 | 9.1337 | 11.6185 | 11.6185 | 11.6185 | 8.4719 | 11.6771 | 11.6771 | 10.7803 | 7.9421 | 11.741 | 11.741 | 9.0642 | 7.6105 | 11.8159 | 10.2506 | 7.3673 | 7.4076 | 11.9024 | 7.9483 | 5.7126 | 7.0559 | 12.002 | 7.8435 | 5.6373 | 6.6992 | 12.1104 | 7.7318 | 5.557 | 6.2967 | 12.2269 | 7.6229 | 5.4787 | 5.901 | 12.3512 | 7.5049 | 5.3939 | 5.4487 | 12.8381 | 7.1403 | 5.1319 | 4.1471 | 13.3798 | 6.9499 | 4.995 | 3.0035 | 13.9231 | 11.2377 | 8.0768 | 2.1768 | 14.4013 | 14.4013 | 11.0723 | 1.5621 | 11.6325 | 11.6325 | 11.6325 | 8.5246 | 11.6972 | 11.6972 | 11.6972 | 7.2788 | 11.7325 | 11.7325 | 10.6122 | 6.557 | 11.7902 | 11.7902 | 8.8411 | 6.1537 | 11.8644 | 9.9108 | 7.1231 | 5.8835 | 11.9579 | 7.5352 | 5.4157 | 5.45 | 12.0661 | 7.4149 | 5.3293 | 5.0147 | 12.1842 | 7.2885 | 5.2384 | 4.5322 | 12.3068 | 7.1635 | 5.1485 | 4.0958 | 12.4511 | 6.9936 | 5.0264 | 3.4913 | 13.2049 | 6.4816 | 4.6584 | 1.44 | 13.8611 | 6.1451 | 4.4166 | 0.36038 | 14.4627 | 11.3181 | 8.1345 | 0.019744 | 14.9362 | 14.9362 | 11.6415 | 0.16077 | 11.629 | 11.629 | 11.629 | 8.5319 | 11.6988 | 11.6988 | 11.6988 | 7.2654 | 11.7455 | 11.7455 | 10.5332 | 6.5261 | 11.8208 | 11.8208 | 8.7644 | 6.1192 | 11.9272 | 9.7579 | 7.0132 | 5.8314 | 12.0764 | 7.3395 | 5.275 | 5.3521 | 12.2476 | 7.1632 | 5.1483 | 4.8334 | 12.45 | 6.9816 | 5.0178 | 4.2547 | 12.6768 | 6.8141 | 4.8975 | 3.7792 | 12.9342 | 6.6287 | 4.7642 | 3.229 | 14.4415 | 5.711 | 4.1046 | 0.70992 | 16.1416 | 4.8431 | 3.4808 | -2.8021 | 17.2252 | 9.664 | 6.9457 | -4.7664 | 17.7292 | 14.411 | 10.3575 | -6.2355 | 11.6289 | 11.6289 | 11.6289 | 8.4987 | 11.7081 | 11.7081 | 11.7081 | 7.1702 | 11.7643 | 11.7643 | 11.7643 | 6.4222 | 11.8522 | 11.8522 | 11.8522 | 6.0256 | 11.9712 | 11.9712 | 11.9712 | 5.7487 | 12.132 | 12.132 | 12.132 | 5.303 | 12.3423 | 12.3423 | 12.3423 | 4.8301 | 12.5929 | 12.5929 | 12.5929 | 4.3192 | 12.874 | 12.874 | 12.8338 | 3.9084 | 13.2452 | 13.2452 | 12.6569 | 3.0333 | 15.0662 | 15.0662 | 11.8822 | -1.0138 | 16.5214 | 15.5456 | 11.1729 | -3.842 | 17.1413 | 15.2873 | 10.9873 | -4.9957 | 17.1021 | 15.0449 | 10.8131 | -4.5534
BURY TOWN CENTRE | BURY | KEARSLEY | 380863 | 410807 | 31.865 | 7.2566 | 5.2936 | 13.384 | 31.9742 | 7.1525 | 5.2176 | 12.7997 | 31.9988 | 7.0949 | 5.1756 | 12.84 | 32.0591 | 6.9314 | 5.0564 | 12.427 | 32.1456 | 6.8458 | 4.9939 | 12.3298 | 32.2575 | 6.734 | 4.9124 | 11.9761 | 32.38 | 6.6159 | 4.8262 | 11.6324 | 32.5106 | 6.5013 | 4.7426 | 11.3677 | 32.6482 | 6.3333 | 4.6201 | 10.8026 | 32.796 | 6.1898 | 4.5154 | 10.3668 | 33.3817 | 5.5021 | 4.0137 | 8.8049 | 33.8239 | 5.6444 | 4.1175 | 7.9403 | 34.0943 | 6.0926 | 4.4444 | 7.493 | 34.2725 | 6.1771 | 4.5061 | 7.5094 | 31.7707 | 7.2677 | 5.3017 | 13.7011 | 31.805 | 7.1157 | 5.1908 | 13.2617 | 31.8786 | 7.0198 | 5.1209 | 13.1802 | 31.97 | 6.8675 | 5.0097 | 12.6977 | 32.0725 | 6.8231 | 4.9774 | 12.6625 | 32.185 | 6.6993 | 4.887 | 12.2092 | 32.3082 | 6.589 | 4.8066 | 11.8427 | 32.439 | 6.4937 | 4.7371 | 11.5753 | 32.578 | 6.3293 | 4.6172 | 10.9503 | 32.7227 | 6.0933 | 4.445 | 9.9591 | 33.007 | 6.0629 | 4.4228 | 9.3931 | 33.2332 | 6.1337 | 4.4744 | 9.0224 | 33.3818 | 6.6426 | 4.8457 | 8.539 | 33.4601 | 6.6862 | 4.8775 | 8.3533 | 31.865 | 7.2655 | 5.3001 | 13.3248 | 31.9742 | 7.0988 | 5.1785 | 12.8058 | 31.9989 | 6.9644 | 5.0805 | 12.8582 | 32.0593 | 6.7655 | 4.9354 | 12.4744 | 32.1455 | 6.6467 | 4.8487 | 12.3778 | 32.2568 | 6.6224 | 4.8309 | 12.0163 | 32.3789 | 6.563 | 4.7876 | 11.6958 | 32.5091 | 6.5074 | 4.747 | 11.3882 | 32.645 | 6.3827 | 4.6561 | 10.8441 | 32.7853 | 6.1921 | 4.517 | 10.4483 | 33.3305 | 5.9446 | 4.3365 | 9.0231 | 33.7235 | 6.162 | 4.4951 | 8.2639 | 33.9675 | 6.6195 | 4.8288 | 7.8623 | 34.1212 | 6.7884 | 4.9521 | 7.8947 | 31.8569 | 7.2613 | 5.297 | 13.3985 | 31.962 | 7.161 | 5.2238 | 12.8276 | 31.9928 | 7.0815 | 5.1659 | 12.8754 | 32.0689 | 6.9217 | 5.0493 | 12.4634 | 32.1829 | 6.8433 | 4.9921 | 12.3647 | 32.336 | 6.7166 | 4.8997 | 12.0098 | 32.5163 | 6.5885 | 4.8062 | 11.6533 | 32.7197 | 6.4616 | 4.7136 | 11.2972 | 32.9436 | 6.2799 | 4.5811 | 10.7049 | 33.1903 | 6.1278 | 4.4701 | 10.2693 | 33.2049 | 5.3862 | 3.9291 | 8.0817 | 29.3481 | 4.7605 | 3.4727 | 4.1907 | 28.1726 | 4.5699 | 3.3337 | 0.85726 | 25.822 | 4.1886 | 3.0555 | -1.2158 | 31.8529 | 7.2662 | 5.3006 | 13.3851 | 31.9638 | 7.1882 | 5.2437 | 12.802 | 31.9947 | 7.1022 | 5.181 | 12.8555 | 32.0623 | 6.9579 | 5.0757 | 12.4863 | 32.1663 | 6.8565 | 5.0017 | 12.407 | 32.3033 | 6.6888 | 4.8794 | 12.0672 | 32.4706 | 6.5342 | 4.7666 | 11.7416 | 32.6528 | 6.3922 | 4.663 | 11.4358 | 32.8554 | 6.1813 | 4.5092 | 10.8214 | 33.1023 | 5.8522 | 4.2691 | 9.7891 | 33.8919 | 5.888 | 4.2952 | 5.295 | 29.1055 | 4.7212 | 3.4441 | 1.7274 | 25.546 | 4.1438 | 3.0229 | -0.46606 | 25.6674 | 4.1635 | 3.0372 | 0.23795
CRAGGS ROW & BUSHELL ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353809 | 430094 | 31.903 | 12.5883 | 9.183 | 9.7266 | 31.9925 | 12.4363 | 9.0721 | 9.3896 | 32.0083 | 12.243 | 8.9311 | 9.1546 | 32.0584 | 12.226 | 8.9187 | 8.8259 | 32.1301 | 12.1496 | 8.863 | 8.5531 | 32.2242 | 12.0067 | 8.7587 | 8.236 | 32.3256 | 11.8415 | 8.6382 | 7.792 | 32.4309 | 11.6934 | 8.5302 | 7.3913 | 32.5419 | 11.5304 | 8.4112 | 7.0055 | 32.6646 | 11.3449 | 8.2759 | 6.4806 | 33.0952 | 10.5414 | 7.6898 | 4.7609 | 33.3704 | 10.1743 | 7.422 | 3.9149 | 33.5028 | 10.0833 | 7.3557 | 3.633 | 33.5371 | 10.014 | 7.3051 | 3.9664 | 31.8196 | 12.6673 | 9.2406 | 9.9784 | 31.8487 | 12.6006 | 9.1919 | 9.8474 | 31.9158 | 12.4897 | 9.111 | 9.5084 | 32.0043 | 12.4081 | 9.0515 | 9.1319 | 32.1068 | 12.3293 | 8.9941 | 8.8375 | 32.2209 | 12.2275 | 8.9198 | 8.509 | 32.3468 | 12.1135 | 8.8367 | 8.0418 | 32.4804 | 12.0056 | 8.7579 | 7.6074 | 32.6232 | 11.8829 | 8.6684 | 7.1395 | 32.7739 | 11.7515 | 8.5725 | 6.6085 | 33.0044 | 11.4013 | 8.3171 | 5.4609 | 33.1742 | 11.103 | 8.0995 | 4.5728 | 33.2625 | 10.8868 | 7.9418 | 3.9811 | 33.2838 | 10.8095 | 7.8854 | 3.8028 | 31.903 | 12.6657 | 9.2394 | 9.7387 | 31.9925 | 12.5592 | 9.1618 | 9.4209 | 32.0083 | 12.4878 | 9.1097 | 9.2071 | 32.0584 | 12.3611 | 9.0172 | 8.8975 | 32.1299 | 12.2243 | 8.9175 | 8.6452 | 32.2235 | 12.0856 | 8.8163 | 8.3485 | 32.3245 | 11.945 | 8.7137 | 7.9262 | 32.4296 | 11.7923 | 8.6023 | 7.5461 | 32.5393 | 11.6252 | 8.4804 | 7.1882 | 32.6567 | 11.445 | 8.349 | 6.7196 | 33.0634 | 10.9216 | 7.9672 | 5.1768 | 33.3187 | 10.4094 | 7.5935 | 4.4531 | 33.4408 | 10.4896 | 7.652 | 4.2253 | 33.472 | 10.2971 | 7.5116 | 4.5515 | 31.8951 | 12.5885 | 9.1831 | 9.7407 | 31.9793 | 12.4278 | 9.0659 | 9.4188 | 31.9948 | 12.2424 | 8.9306 | 9.2048 | 32.0511 | 12.2225 | 8.9161 | 8.8959 | 32.1368 | 12.129 | 8.848 | 8.6501 | 32.2552 | 11.9726 | 8.7338 | 8.3581 | 32.3951 | 11.7924 | 8.6024 | 7.9093 | 32.5482 | 11.6416 | 8.4924 | 7.5079 | 32.7117 | 11.4713 | 8.3682 | 7.1741 | 32.8891 | 11.2652 | 8.2178 | 6.7766 | 33.4713 | 10.2233 | 7.4578 | 4.6302 | 34.0614 | 9.3072 | 6.7895 | 0.41136 | 34.3172 | 8.4362 | 6.1541 | -2.758 | 34.3518 | 7.9879 | 5.827 | -4.5825 | 31.8827 | 12.5919 | 9.1857 | 9.7523 | 31.9608 | 12.4552 | 9.0859 | 9.4204 | 31.9682 | 12.2843 | 8.9612 | 9.2246 | 32.0143 | 12.2411 | 8.9297 | 8.9561 | 32.0913 | 12.1426 | 8.8579 | 8.7292 | 32.1928 | 11.9779 | 8.7377 | 8.4835 | 32.3136 | 11.7885 | 8.5995 | 8.1048 | 32.4417 | 11.624 | 8.4795 | 7.786 | 32.5874 | 11.4414 | 8.3464 | 7.4457 | 32.8012 | 11.0573 | 8.0661 | 6.3428 | 33.5428 | 9.5655 | 6.9779 | 1.3758 | 33.8329 | 8.5366 | 6.2274 | -2.3617 | 33.8353 | 7.8896 | 5.7554 | -4.4112 | 33.6523 | 8.0095 | 5.8428 | -3.3323
CAMPBELL ST | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 20.2375 | 9.8832 | 7.1033 | 10.168 | 20.3168 | 9.723 | 6.9881 | 9.4815 | 20.3933 | 9.6505 | 6.936 | 9.4547 | 20.4552 | 9.5188 | 6.8414 | 9.212 | 20.5345 | 9.4238 | 6.7731 | 9.1517 | 20.6355 | 9.2419 | 6.6423 | 8.7783 | 20.758 | 9.1076 | 6.5458 | 8.4929 | 20.8985 | 8.9665 | 6.4444 | 8.2561 | 21.0553 | 8.8093 | 6.3314 | 7.9048 | 21.2303 | 8.6285 | 6.2015 | 7.4281 | 22.1753 | 7.991 | 5.7433 | 5.3032 | 23.1013 | 7.517 | 5.4026 | 3.4672 | 23.6489 | 8.3756 | 6.0197 | 2.217 | 23.9973 | 9.2067 | 6.6171 | 1.4501 | 20.2497 | 9.9244 | 7.1329 | 10.5326 | 20.3327 | 9.8367 | 7.0698 | 10.1625 | 20.4098 | 9.7942 | 7.0393 | 10.0501 | 20.4811 | 9.7037 | 6.9742 | 9.7638 | 20.564 | 9.6492 | 6.935 | 9.6842 | 20.6628 | 9.5621 | 6.8724 | 9.3258 | 20.7792 | 9.4742 | 6.8093 | 9.043 | 20.9107 | 9.3945 | 6.752 | 8.802 | 21.052 | 9.2983 | 6.6829 | 8.445 | 21.2026 | 9.1913 | 6.606 | 8.0317 | 21.8909 | 8.7458 | 6.2858 | 6.3756 | 22.4209 | 8.2754 | 5.9477 | 4.9929 | 22.6445 | 9.0703 | 6.519 | 4.368 | 22.7932 | 9.9024 | 7.117 | 4.1861 | 20.2376 | 9.9185 | 7.1287 | 10.1787 | 20.3169 | 9.7814 | 7.0301 | 9.5054 | 20.4025 | 9.6834 | 6.9596 | 9.4886 | 20.465 | 9.4951 | 6.8243 | 9.2564 | 20.544 | 9.4176 | 6.7686 | 9.2062 | 20.6413 | 9.2611 | 6.6562 | 8.8477 | 20.7572 | 9.1467 | 6.5739 | 8.5764 | 20.8887 | 9.037 | 6.4951 | 8.3535 | 21.0331 | 8.8954 | 6.3933 | 8.0235 | 21.1894 | 8.7347 | 6.2778 | 7.6149 | 22.0372 | 8.3706 | 6.0161 | 5.6965 | 22.777 | 8.027 | 5.7692 | 4.3412 | 23.1199 | 8.8036 | 6.3273 | 3.8758 | 23.3242 | 9.971 | 7.1663 | 3.8687 | 20.2426 | 9.8845 | 7.1042 | 10.1879 | 20.3288 | 9.7185 | 6.9849 | 9.5255 | 20.4111 | 9.6229 | 6.9161 | 9.5224 | 20.4834 | 9.5061 | 6.8322 | 9.3047 | 20.5775 | 9.3864 | 6.7462 | 9.2752 | 20.7083 | 9.2019 | 6.6136 | 8.9355 | 20.8764 | 9.0413 | 6.4982 | 8.6676 | 21.0775 | 8.866 | 6.3722 | 8.4416 | 21.3073 | 8.6917 | 6.2469 | 8.0832 | 21.5675 | 8.4509 | 6.0738 | 7.6314 | 22.9603 | 7.8144 | 5.6164 | 4.9374 | 24.3742 | 6.5656 | 4.7188 | 0.42624 | 25.2254 | 6.6917 | 4.8095 | -4.9014 | 25.6644 | 7.0157 | 5.0423 | -8.0734 | 20.2691 | 9.8843 | 7.104 | 10.1805 | 20.3668 | 9.683 | 6.9594 | 9.4844 | 20.4261 | 9.5461 | 6.861 | 9.4681 | 20.5028 | 9.329 | 6.7049 | 9.2556 | 20.6017 | 9.0909 | 6.5338 | 9.236 | 20.7492 | 8.8593 | 6.3674 | 8.9153 | 20.9505 | 8.8244 | 6.3423 | 8.6621 | 21.1936 | 8.7638 | 6.2987 | 8.2753 | 21.4807 | 8.6569 | 6.2219 | 7.7625 | 21.8367 | 8.4657 | 6.0844 | 6.9652 | 23.2718 | 7.0401 | 5.0599 | 2.3229 | 24.4203 | 6.222 | 4.4719 | -2.2233 | 25.0317 | 7.7436 | 5.5655 | -5.3799 | 25.1747 | 7.4338 | 5.3428 | -6.5304
CANNON ST | RED BANK | WHITEGATE | 384064 | 398635 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
CAPONTREE | CARLISLE | HARKER / HUTTON | 352906 | 559671 | 22.4483 | 21.7482 | 15.6309 | 19.732 | 22.5189 | 21.6575 | 15.5657 | 19.3506 | 22.5932 | 21.5881 | 15.5158 | 19.1928 | 22.6308 | 21.4843 | 15.4412 | 18.953 | 22.6802 | 21.4012 | 15.3815 | 18.7998 | 22.7433 | 21.2616 | 15.2811 | 18.5026 | 22.8168 | 21.132 | 15.188 | 18.2028 | 22.8977 | 21.0268 | 15.1124 | 18.0081 | 22.9842 | 20.8972 | 15.0192 | 17.6897 | 23.0858 | 20.7484 | 14.9123 | 17.2525 | 23.6833 | 20.4062 | 14.6664 | 15.5773 | 24.4547 | 20.6746 | 14.8592 | 14.3821 | 25.0739 | 25.0739 | 19.0217 | 13.7143 | 25.7099 | 25.7099 | 18.9235 | 13.6095 | 22.4804 | 21.7757 | 15.6506 | 19.8497 | 22.5387 | 21.7074 | 15.6016 | 19.5807 | 22.5926 | 21.6437 | 15.5557 | 19.412 | 22.6551 | 21.565 | 15.4992 | 19.2149 | 22.7269 | 21.5037 | 15.4551 | 19.0923 | 22.8095 | 21.4005 | 15.381 | 18.8244 | 22.9041 | 21.3095 | 15.3156 | 18.5488 | 23.009 | 21.2376 | 15.2639 | 18.3675 | 23.1036 | 21.1462 | 15.1982 | 18.0583 | 23.2029 | 21.0573 | 15.1343 | 17.7526 | 23.5308 | 20.8258 | 14.9679 | 16.8842 | 23.9682 | 20.6129 | 14.8149 | 15.8718 | 24.4494 | 23.8226 | 17.1218 | 14.9838 | 24.8589 | 24.8589 | 19.4782 | 14.3945 | 22.4485 | 21.7753 | 15.6504 | 19.7374 | 22.5196 | 21.7048 | 15.5996 | 19.3756 | 22.5948 | 21.6275 | 15.5441 | 19.2356 | 22.6334 | 21.5315 | 15.4751 | 19.0141 | 22.6839 | 21.4541 | 15.4195 | 18.8757 | 22.7479 | 21.3068 | 15.3136 | 18.5954 | 22.8223 | 21.1711 | 15.2161 | 18.3115 | 22.904 | 21.0475 | 15.1272 | 18.129 | 22.9905 | 20.7686 | 14.9268 | 17.8339 | 23.0892 | 20.7885 | 14.9411 | 17.4442 | 23.5916 | 20.6284 | 14.8261 | 15.9851 | 24.0641 | 20.9459 | 15.0542 | 15.0773 | 24.5462 | 24.5462 | 19.1244 | 14.569 | 24.9401 | 24.9401 | 18.8791 | 14.6254 | 22.4482 | 21.7479 | 15.6306 | 19.7364 | 22.5238 | 21.6491 | 15.5597 | 19.3311 | 22.5982 | 21.5613 | 15.4965 | 19.1438 | 22.6471 | 21.4393 | 15.4088 | 18.8754 | 22.7154 | 21.3335 | 15.3328 | 18.6718 | 22.818 | 21.1635 | 15.2106 | 18.2905 | 22.9539 | 20.993 | 15.0881 | 17.8633 | 23.1165 | 20.844 | 14.981 | 17.5338 | 23.3009 | 20.6793 | 14.8626 | 17.1258 | 23.5007 | 20.5127 | 14.7429 | 16.7181 | 24.6416 | 19.9884 | 14.3661 | 14.7031 | 25.8454 | 19.8189 | 14.2442 | 11.839 | 26.5981 | 25.3284 | 18.204 | 10.0808 | 26.7788 | 24.8868 | 17.8866 | 8.7919 | 22.4628 | 21.7483 | 15.6309 | 19.7347 | 22.5636 | 21.6596 | 15.5672 | 19.3175 | 22.6012 | 21.5536 | 15.491 | 19.1325 | 22.6526 | 21.4278 | 15.4005 | 18.8663 | 22.7253 | 21.3148 | 15.3194 | 18.6515 | 22.8437 | 21.149 | 15.2002 | 18.2769 | 23.01 | 20.9787 | 15.0778 | 17.8776 | 23.2115 | 20.9501 | 15.0572 | 17.5865 | 23.437 | 20.9432 | 15.0523 | 17.2004 | 23.6894 | 20.9573 | 15.0624 | 16.4926 | 24.9853 | 24.9853 | 19.0014 | 13.1406 | 26.0561 | 25.5824 | 18.3866 | 10.7312 | 26.5123 | 25.1768 | 18.095 | 9.6121 | 26.4668 | 25.0343 | 17.9926 | 9.8032
CARLETON | EGREMONT | HARKER / HUTTON | 308796 | 498305 | 8.0269 | 8.0269 | 8.0269 | 5.4549 | 8.0619 | 8.0619 | 8.0619 | 5.349 | 8.1075 | 8.1075 | 8.1075 | 5.2566 | 8.1635 | 8.1635 | 8.1635 | 5.1428 | 8.2193 | 8.2193 | 8.2193 | 5.0447 | 8.2516 | 8.2516 | 8.2516 | 4.9099 | 8.2895 | 8.2895 | 8.2895 | 4.7603 | 8.3313 | 8.3313 | 8.3313 | 4.626 | 8.3769 | 8.3769 | 8.3769 | 4.4755 | 8.4286 | 8.4286 | 8.4286 | 4.2599 | 8.629 | 8.629 | 8.629 | 3.5516 | 8.781 | 8.781 | 8.781 | 3.2394 | 8.8679 | 8.8679 | 8.8679 | 3.174 | 8.8943 | 8.8943 | 8.8943 | 3.2303 | 8.0156 | 8.0156 | 8.0156 | 5.5149 | 8.0399 | 8.0399 | 8.0399 | 5.4613 | 8.084 | 8.084 | 8.084 | 5.3591 | 8.1201 | 8.1201 | 8.1201 | 5.2607 | 8.1588 | 8.1588 | 8.1588 | 5.1789 | 8.2027 | 8.2027 | 8.2027 | 5.0606 | 8.254 | 8.254 | 8.254 | 4.927 | 8.3091 | 8.3091 | 8.3091 | 4.8045 | 8.3592 | 8.3592 | 8.3592 | 4.6745 | 8.397 | 8.397 | 8.397 | 4.5232 | 8.4923 | 8.4923 | 8.4923 | 4.1442 | 8.5851 | 8.5851 | 8.5851 | 3.7342 | 8.6403 | 8.6403 | 8.6403 | 3.4203 | 8.6635 | 8.6635 | 8.6635 | 3.2625 | 8.0278 | 8.0278 | 8.0278 | 5.4572 | 8.0631 | 8.0631 | 8.0631 | 5.3555 | 8.1089 | 8.1089 | 8.1089 | 5.2681 | 8.165 | 8.165 | 8.165 | 5.1597 | 8.2197 | 8.2197 | 8.2197 | 5.0659 | 8.2516 | 8.2516 | 8.2516 | 4.9363 | 8.289 | 8.289 | 8.289 | 4.7918 | 8.33 | 8.33 | 8.33 | 4.6618 | 8.3744 | 8.3744 | 8.3744 | 4.5195 | 8.4229 | 8.4229 | 8.4229 | 4.3257 | 8.6085 | 8.6085 | 8.6085 | 3.6769 | 8.7392 | 8.7392 | 8.7392 | 3.4107 | 8.8065 | 8.8065 | 8.8065 | 3.3584 | 8.8346 | 8.8346 | 8.8346 | 3.5264 | 8.0277 | 8.0277 | 8.0277 | 5.4573 | 8.0657 | 8.0657 | 8.0657 | 5.3458 | 8.1207 | 8.1207 | 8.1207 | 5.2496 | 8.1931 | 8.1931 | 8.1931 | 5.1365 | 8.2373 | 8.2373 | 8.2373 | 5.0319 | 8.2835 | 8.2835 | 8.2835 | 4.8886 | 8.3414 | 8.3414 | 8.3414 | 4.7252 | 8.4077 | 8.4077 | 8.4077 | 4.5859 | 8.4817 | 8.4817 | 8.4817 | 4.4549 | 8.5645 | 8.5645 | 8.5645 | 4.315 | 8.8384 | 8.8384 | 8.8384 | 3.5996 | 8.9954 | 8.9954 | 8.9954 | 2.8632 | 9.0614 | 9.0614 | 9.0614 | 2.5024 | 9.0773 | 9.0773 | 9.0773 | 2.3237 | 8.038 | 8.038 | 8.038 | 5.4427 | 8.096 | 8.096 | 8.096 | 5.3064 | 8.1646 | 8.1646 | 8.1646 | 5.2007 | 8.2022 | 8.2022 | 8.2022 | 5.0838 | 8.2372 | 8.2372 | 8.2372 | 4.965 | 8.2806 | 8.2806 | 8.2806 | 4.8207 | 8.3359 | 8.3359 | 8.3359 | 4.6679 | 8.3972 | 8.3972 | 8.3972 | 4.5468 | 8.464 | 8.464 | 8.464 | 4.4353 | 8.5381 | 8.5381 | 8.5381 | 4.2622 | 8.7642 | 8.7642 | 8.7642 | 3.5821 | 8.8729 | 8.8729 | 8.8729 | 3.1474 | 8.8908 | 8.8908 | 8.8908 | 2.9829 | 8.8466 | 8.8466 | 8.8466 | 2.9788
CARLISLE NORTH | - | HARKER / HUTTON | 338547 | 560280 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.4602 | 0.44197 | 0.31765 | 1.4602 | 2.1267 | 0.44197 | 0.31765 | 2.1267 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.16778 | 0.063684 | 0.052036 | 0.16778 | 0.75746 | 0.2875 | 0.23492 | 0.75746 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 2.5005 | 0.44197 | 0.31765 | 2.5005 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.33323 | 0.12648 | 0.10335 | 0.33323 | 0.9663 | 0.36677 | 0.29969 | 0.9663 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.5049 | 0.44197 | 0.31765 | 2.5049 | 1.1551 | 0.43843 | 0.31765 | 1.1551 | 0.29377 | 0.1115 | 0.091109 | 0.29377
CARR ST | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 30.5557 | 13.6703 | 9.8251 | 12.2535 | 30.6366 | 13.5821 | 9.7618 | 11.799 | 30.6778 | 13.4848 | 9.6918 | 11.4551 | 30.7485 | 13.3972 | 9.6288 | 11.0748 | 30.8429 | 13.2714 | 9.5384 | 10.6399 | 30.9568 | 13.0782 | 9.3996 | 10.0958 | 31.0823 | 12.8155 | 9.2107 | 9.5103 | 31.2167 | 12.6772 | 9.1114 | 8.9588 | 31.3596 | 12.4357 | 8.9378 | 8.391 | 31.515 | 12.1931 | 8.7634 | 7.7523 | 32.3377 | 11.6707 | 8.388 | 5.335 | 33.2372 | 11.3059 | 8.1257 | 3.8286 | 33.9221 | 10.8336 | 7.7863 | 3.2236 | 34.6198 | 10.5247 | 7.5643 | 2.896 | 30.5088 | 13.7043 | 9.8496 | 12.4849 | 30.5495 | 13.6517 | 9.8117 | 12.2373 | 30.6188 | 13.5881 | 9.766 | 11.8155 | 30.7029 | 13.499 | 9.702 | 11.4263 | 30.7996 | 13.3938 | 9.6264 | 11.0183 | 30.9054 | 13.2542 | 9.5261 | 10.5179 | 31.0205 | 13.1381 | 9.4426 | 9.9708 | 31.1422 | 13.0088 | 9.3497 | 9.4547 | 31.2706 | 12.8735 | 9.2524 | 8.9115 | 31.4038 | 12.6753 | 9.11 | 8.3428 | 31.9037 | 12.2133 | 8.7779 | 6.3098 | 32.3946 | 11.5438 | 8.2967 | 4.8266 | 32.8697 | 11.6403 | 8.3661 | 3.9295 | 33.2837 | 11.5317 | 8.2881 | 3.2788 | 30.5559 | 13.7029 | 9.8486 | 12.2652 | 30.6372 | 13.6416 | 9.8045 | 11.8343 | 30.679 | 13.4836 | 9.6909 | 11.5135 | 30.7504 | 13.3746 | 9.6126 | 11.1497 | 30.8455 | 13.2028 | 9.4891 | 10.7417 | 30.9598 | 12.9829 | 9.3311 | 10.2263 | 31.0856 | 12.7888 | 9.1916 | 9.6699 | 31.2205 | 12.589 | 9.048 | 9.1464 | 31.3625 | 12.3277 | 8.8602 | 8.6144 | 31.512 | 12.0035 | 8.6272 | 8.0383 | 32.2452 | 11.9071 | 8.5579 | 5.8975 | 32.8986 | 11.5945 | 8.3332 | 4.6751 | 33.4589 | 11.186 | 8.0396 | 4.1903 | 33.9345 | 10.8187 | 7.7756 | 3.9563 | 30.5513 | 13.6724 | 9.8266 | 12.2725 | 30.6319 | 13.5904 | 9.7677 | 11.8395 | 30.6838 | 13.4803 | 9.6886 | 11.5148 | 30.7747 | 13.3864 | 9.6211 | 11.1385 | 30.8973 | 13.2351 | 9.5123 | 10.7566 | 31.0605 | 13.026 | 9.362 | 10.2699 | 31.2586 | 12.7788 | 9.1844 | 9.7385 | 31.487 | 12.5539 | 9.0227 | 9.2419 | 31.7394 | 12.2609 | 8.8121 | 8.7821 | 32.02 | 11.8157 | 8.4922 | 8.2938 | 33.5195 | 11.4684 | 8.2426 | 5.1228 | 35.2539 | 9.9702 | 7.1658 | -0.68565 | 36.242 | 8.633 | 6.2047 | -5.1739 | 36.7519 | 7.7694 | 5.584 | -8.1894 | 30.5487 | 13.6741 | 9.8279 | 12.2752 | 30.6385 | 13.5877 | 9.7658 | 11.808 | 30.6972 | 13.4359 | 9.6567 | 11.4726 | 30.7896 | 13.3168 | 9.571 | 11.1157 | 30.9132 | 13.0782 | 9.3996 | 10.7788 | 31.0831 | 12.5828 | 9.0435 | 10.3515 | 31.3011 | 12.2937 | 8.8357 | 9.8643 | 31.5526 | 12.4303 | 8.9339 | 9.4203 | 31.8529 | 12.4086 | 8.9183 | 8.8466 | 32.2715 | 12.2112 | 8.7764 | 7.453 | 34.0361 | 10.7068 | 7.6952 | 0.83827 | 35.3461 | 9.3271 | 6.7036 | -4.4369 | 35.9145 | 8.4426 | 6.0678 | -7.4644 | 35.9588 | 8.3106 | 5.973 | -6.8966
CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 30.4542 | 8.5962 | 6.2708 | 10.8792 | 30.5528 | 7.7252 | 5.6354 | 10.3884 | 30.6028 | 7.1315 | 5.2024 | 9.9844 | 30.6674 | 6.576 | 4.7971 | 9.9127 | 30.7586 | 6.0135 | 4.3868 | 9.7114 | 30.8656 | 5.5392 | 4.0407 | 9.2805 | 30.9828 | 5.4124 | 3.9483 | 8.7529 | 31.1038 | 5.3286 | 3.8871 | 8.4859 | 31.2327 | 5.2404 | 3.8228 | 8.2319 | 31.3873 | 5.0967 | 3.718 | 7.7289 | 29.005 | 4.7049 | 3.4322 | 6.3174 | 29.1894 | 4.7348 | 3.454 | 5.4441 | 33.5063 | 5.435 | 3.9648 | 5.1066 | 33.597 | 5.4498 | 3.9755 | 5.0034 | 30.3951 | 8.7294 | 6.368 | 11.3216 | 30.4416 | 8.1711 | 5.9607 | 11.213 | 30.513 | 7.651 | 5.5813 | 10.7267 | 30.575 | 7.2498 | 5.2886 | 10.5941 | 30.6569 | 6.9311 | 5.0561 | 10.3618 | 30.7466 | 6.516 | 4.7533 | 9.9611 | 30.8448 | 6.3786 | 4.6531 | 9.4471 | 30.9458 | 6.2811 | 4.582 | 9.1727 | 31.0509 | 6.1771 | 4.5061 | 8.8779 | 31.1583 | 6.1332 | 4.4741 | 8.4248 | 31.6687 | 5.9539 | 4.3433 | 7.2566 | 32.2085 | 5.9913 | 4.3706 | 6.3738 | 32.7208 | 6.4355 | 4.6946 | 5.8027 | 33.1726 | 6.5254 | 4.7602 | 5.5157 | 30.4544 | 8.7268 | 6.3661 | 10.888 | 30.5534 | 8.0392 | 5.8645 | 10.4044 | 30.604 | 7.2856 | 5.3147 | 10.01 | 30.6694 | 6.8197 | 4.9748 | 9.9447 | 30.7614 | 6.3422 | 4.6265 | 9.785 | 30.8689 | 5.8063 | 4.2356 | 9.331 | 30.9866 | 5.6843 | 4.1466 | 8.8144 | 31.1081 | 5.5979 | 4.0836 | 8.5558 | 31.2366 | 5.5281 | 4.0327 | 8.3353 | 31.3866 | 5.418 | 3.9524 | 7.8477 | 31.4456 | 5.1008 | 3.7209 | 6.6732 | 32.464 | 5.266 | 3.8415 | 6.013 | 33.49 | 6.0947 | 4.446 | 5.7381 | 33.9371 | 6.119 | 4.4637 | 5.6543 | 30.4537 | 8.5975 | 6.2717 | 10.9043 | 30.5588 | 8.0097 | 5.843 | 10.437 | 30.6286 | 7.328 | 5.3457 | 10.0551 | 30.7262 | 6.5102 | 4.7491 | 9.9995 | 30.8569 | 6.218 | 4.536 | 9.8579 | 31.0313 | 5.6756 | 4.1403 | 9.4131 | 31.2506 | 5.5204 | 4.027 | 8.8908 | 31.499 | 5.3582 | 3.9087 | 8.6166 | 31.7562 | 5.3273 | 3.8862 | 8.4074 | 32.017 | 5.1935 | 3.7886 | 7.9483 | 28.1987 | 4.5741 | 3.3368 | 6.0075 | 23.9774 | 3.8894 | 2.8372 | 1.6716 | 23.744 | 3.8515 | 2.8096 | -1.7102 | 20.4688 | 3.3202 | 2.4221 | -3.9488 | 30.4671 | 8.5919 | 6.2676 | 10.8479 | 30.5854 | 8.1572 | 5.9506 | 10.3495 | 30.663 | 7.7968 | 5.6877 | 9.9762 | 30.7711 | 7.5144 | 5.4817 | 9.9374 | 30.9128 | 7.1657 | 5.2273 | 9.8133 | 31.105 | 6.8806 | 5.0193 | 9.3909 | 31.3514 | 6.7151 | 4.8986 | 8.8834 | 31.6294 | 6.5969 | 4.8123 | 8.6293 | 31.9987 | 6.4046 | 4.6721 | 8.323 | 32.7324 | 6.2256 | 4.5415 | 7.0972 | 32.4296 | 5.2604 | 3.8374 | 2.2627 | 25.7949 | 4.1842 | 3.0523 | -1.6887 | 22.2607 | 3.6109 | 2.6341 | -3.9182 | 22.0657 | 3.5793 | 2.611 | -3.2321
CATTERALL WATERWORKS | RIBBLE | PENWORTHAM EAST / ROCHDALE | 349381 | 442178 | 10.4811 | 10.4811 | 10.4811 | -0.50838 | 10.5557 | 10.5557 | 10.5557 | -0.7661 | 10.571 | 10.571 | 10.571 | -0.71071 | 10.6044 | 10.6044 | 10.6044 | -0.78655 | 10.6506 | 10.6506 | 10.6506 | -0.89652 | 10.7117 | 10.7117 | 10.7117 | -1.0308 | 10.7809 | 10.7809 | 10.7809 | -1.1503 | 10.8529 | 10.8529 | 10.8529 | -1.207 | 10.9187 | 10.9187 | 10.9187 | -1.3615 | 10.9683 | 10.9683 | 10.9683 | -1.525 | 11.2358 | 11.2358 | 11.2358 | -1.9799 | 11.5594 | 11.5594 | 11.5594 | -2.2925 | 11.7849 | 11.7849 | 11.7849 | -2.3849 | 11.9889 | 11.9889 | 11.9889 | -2.4461 | 10.4076 | 10.4076 | 10.4076 | -0.32985 | 10.4211 | 10.4211 | 10.4211 | -0.43759 | 10.4596 | 10.4596 | 10.4596 | -0.44725 | 10.5058 | 10.5058 | 10.5058 | -0.54598 | 10.5559 | 10.5559 | 10.5559 | -0.66584 | 10.6084 | 10.6084 | 10.6084 | -0.79126 | 10.6674 | 10.6674 | 10.6674 | -0.90792 | 10.7284 | 10.7284 | 10.7284 | -0.96723 | 10.791 | 10.791 | 10.791 | -1.1325 | 10.8542 | 10.8542 | 10.8542 | -1.2778 | 11.0947 | 11.0947 | 11.0947 | -1.5704 | 11.292 | 11.292 | 11.292 | -1.8572 | 11.4582 | 11.4582 | 11.4582 | -2.0319 | 11.573 | 11.573 | 11.573 | -2.1293 | 10.4821 | 10.4821 | 10.4821 | -0.50715 | 10.5571 | 10.5571 | 10.5571 | -0.76298 | 10.5728 | 10.5728 | 10.5728 | -0.70635 | 10.6066 | 10.6066 | 10.6066 | -0.78054 | 10.6528 | 10.6528 | 10.6528 | -0.88845 | 10.7134 | 10.7134 | 10.7134 | -1.0204 | 10.7816 | 10.7816 | 10.7816 | -1.1376 | 10.8522 | 10.8522 | 10.8522 | -1.1923 | 10.9168 | 10.9168 | 10.9168 | -1.3431 | 10.966 | 10.966 | 10.966 | -1.4995 | 11.1961 | 11.1961 | 11.1961 | -1.9241 | 11.403 | 11.403 | 11.403 | -2.175 | 11.5656 | 11.5656 | 11.5656 | -2.2395 | 11.6777 | 11.6777 | 11.6777 | -2.2183 | 10.4761 | 10.4761 | 10.4761 | -0.49348 | 10.5465 | 10.5465 | 10.5465 | -0.74156 | 10.5615 | 10.5615 | 10.5615 | -0.6775 | 10.5994 | 10.5994 | 10.5994 | -0.74035 | 10.6544 | 10.6544 | 10.6544 | -0.84253 | 10.7345 | 10.7345 | 10.7345 | -0.97648 | 10.8343 | 10.8343 | 10.8343 | -1.1047 | 10.9091 | 10.9091 | 10.9091 | -1.175 | 10.982 | 10.982 | 10.982 | -1.335 | 11.0618 | 11.0618 | 11.0618 | -1.4739 | 11.5219 | 11.5219 | 11.5219 | -1.9419 | 12.0172 | 12.0172 | 12.0172 | -2.8429 | 12.3013 | 12.3013 | 12.3013 | -3.5211 | 12.2888 | 12.2888 | 12.2888 | -3.871 | 10.4857 | 10.4857 | 10.4857 | -0.49636 | 10.5677 | 10.5677 | 10.5677 | -0.74708 | 10.5861 | 10.5861 | 10.5861 | -0.68049 | 10.6241 | 10.6241 | 10.6241 | -0.74181 | 10.6818 | 10.6818 | 10.6818 | -0.84292 | 10.7677 | 10.7677 | 10.7677 | -0.97267 | 10.873 | 10.873 | 10.873 | -1.0954 | 10.9567 | 10.9567 | 10.9567 | -1.1572 | 11.049 | 11.049 | 11.049 | -1.304 | 11.1562 | 11.1562 | 11.1562 | -1.5488 | 11.6673 | 11.6673 | 11.6673 | -2.5204 | 12.0888 | 12.0888 | 12.0888 | -3.2933 | 12.2067 | 12.2067 | 12.2067 | -3.7218 | 12.0796 | 12.0796 | 12.0796 | -3.4531
CECIL ST | BLACKPOOL | PENWORTHAM WEST / STANAH | 331301 | 437023 | 31.9593 | 15.9839 | 11.66 | 13.6696 | 32.0029 | 15.8312 | 11.5486 | 13.2849 | 31.9997 | 15.6637 | 11.4264 | 13.1425 | 32.0273 | 15.626 | 11.399 | 12.9082 | 32.0724 | 15.6716 | 11.4322 | 12.6984 | 32.1359 | 15.6825 | 11.4402 | 12.4605 | 32.2061 | 15.6295 | 11.4015 | 12.1001 | 32.2818 | 15.5741 | 11.3611 | 11.7793 | 32.3627 | 15.5016 | 11.3082 | 11.4736 | 32.4531 | 15.3928 | 11.2289 | 11.0472 | 32.7546 | 15.1155 | 11.0265 | 10.5251 | 32.9486 | 14.9404 | 10.8988 | 10.3262 | 33.0342 | 14.8792 | 10.8541 | 10.5195 | 33.051 | 14.6864 | 10.7135 | 10.8245 | 31.8986 | 16.0201 | 11.6865 | 13.8738 | 31.9071 | 16.0203 | 11.6866 | 13.6829 | 31.9492 | 15.9564 | 11.64 | 13.2 | 32.0093 | 15.8881 | 11.5901 | 12.6661 | 32.0819 | 15.8129 | 11.5353 | 12.1752 | 32.1651 | 15.7129 | 11.4624 | 11.6397 | 32.2591 | 15.5869 | 11.3704 | 10.9183 | 32.3617 | 15.4564 | 11.2752 | 10.1753 | 32.4639 | 15.3081 | 11.167 | 9.3728 | 32.5637 | 15.1143 | 11.0257 | 8.3575 | 32.712 | 15.0641 | 10.989 | 7.9853 | 32.8148 | 15.0814 | 11.0016 | 7.7837 | 32.8473 | 15.242 | 11.1188 | 7.7965 | 32.8345 | 15.2967 | 11.1587 | 7.8796 | 31.9593 | 16.023 | 11.6885 | 13.6876 | 32.0029 | 16.1363 | 11.7712 | 13.3231 | 31.9997 | 16.1732 | 11.7981 | 13.2015 | 32.0273 | 16.1234 | 11.7618 | 13.1021 | 32.0722 | 16.0491 | 11.7076 | 12.897 | 32.1353 | 15.9771 | 11.655 | 12.6477 | 32.2051 | 15.809 | 11.5325 | 12.3966 | 32.2806 | 15.64 | 11.4091 | 12.1767 | 32.3604 | 15.4492 | 11.27 | 11.8899 | 32.4462 | 15.2507 | 11.1251 | 11.6127 | 32.7266 | 14.9905 | 10.9354 | 10.934 | 32.9029 | 14.778 | 10.7803 | 10.6881 | 32.9792 | 14.93 | 10.8913 | 10.8789 | 32.9929 | 14.7822 | 10.7834 | 11.1709 | 31.9522 | 15.9844 | 11.6604 | 13.6875 | 31.9965 | 15.8271 | 11.5457 | 13.3237 | 31.9882 | 16.0665 | 11.7203 | 13.2092 | 32.0223 | 16.0459 | 11.7052 | 13.019 | 32.083 | 16.0149 | 11.6827 | 12.8476 | 32.1713 | 15.9796 | 11.6569 | 12.654 | 32.2768 | 15.8895 | 11.5912 | 12.3471 | 32.397 | 15.7784 | 11.5101 | 12.0872 | 32.5272 | 15.6752 | 11.4348 | 11.8513 | 32.6721 | 15.531 | 11.3296 | 11.5119 | 33.1695 | 15.0333 | 10.9666 | 10.3905 | 33.7002 | 13.9904 | 10.2058 | 5.6167 | 33.9047 | 12.9232 | 9.4273 | 1.9379 | 33.9725 | 12.25 | 8.9362 | -0.55277 | 31.9382 | 15.992 | 11.6659 | 13.7233 | 31.9746 | 15.806 | 11.5303 | 13.3742 | 31.9596 | 15.6289 | 11.4011 | 13.2914 | 31.9804 | 15.7289 | 11.474 | 13.2618 | 32.0269 | 15.7657 | 11.5008 | 13.1312 | 32.0962 | 15.7811 | 11.5121 | 12.9801 | 32.1835 | 15.7285 | 11.4737 | 12.8267 | 32.2804 | 15.6597 | 11.4236 | 12.7213 | 32.4007 | 15.5348 | 11.3325 | 12.5203 | 32.6152 | 15.3724 | 11.214 | 11.6933 | 33.181 | 13.7173 | 10.0066 | 6.332 | 33.4756 | 12.8104 | 9.345 | 1.9948 | 33.5078 | 12.0535 | 8.7928 | -0.36456 | 33.3255 | 12.0072 | 8.7591 | 0.61807
CENTRAL MANCHESTER | STUART ST | STALYBRIDGE | 384852 | 397718 | 43.5754 | 7.3669 | 5.374 | 20.1186 | 37.6088 | 6.1005 | 4.4502 | 18.9952 | 27.7975 | 4.509 | 3.2893 | 16.5094 | 17.8245 | 2.8913 | 2.1092 | 14.2777 | 4.1595 | 0.67471 | 0.49219 | 4.1595 | 2.6914 | 0.43658 | 0.31848 | 0.2334 | 2.6914 | 0.43658 | 0.31848 | -8.2248 | 2.6914 | 0.43658 | 0.31848 | -10.3817 | 2.6914 | 0.43658 | 0.31848 | -12.4636 | 2.6914 | 0.43658 | 0.31848 | -12.9107 | 2.6914 | 0.43658 | 0.31848 | -13.4044 | 2.6914 | 0.43658 | 0.31848 | -13.6566 | 0.46299 | 0.075101 | 0.054785 | -13.7242 | 5.9463 | 0.96456 | 0.70363 | -13.4367 | 43.4267 | 7.4579 | 5.4404 | 20.9862 | 38.2147 | 6.1988 | 4.5219 | 20.6345 | 28.1067 | 4.5592 | 3.3259 | 18.0997 | 18.19 | 2.9506 | 2.1524 | 15.7213 | 4.3387 | 0.70378 | 0.5134 | 4.3387 | 2.6914 | 0.43658 | 0.31848 | 1.4754 | 2.6914 | 0.43658 | 0.31848 | -7.0674 | 2.6914 | 0.43658 | 0.31848 | -9.3355 | 2.6914 | 0.43658 | 0.31848 | -11.5698 | 2.6914 | 0.43658 | 0.31848 | -12.1361 | 2.6914 | 0.43658 | 0.31848 | -12.6493 | 2.6914 | 0.43658 | 0.31848 | -13.0312 | 2.6914 | 0.43658 | 0.31848 | -13.214 | 2.6914 | 0.43658 | 0.31848 | -12.9858 | 43.5754 | 7.4576 | 5.4402 | 20.125 | 38.2318 | 6.2016 | 4.524 | 19.0118 | 27.9684 | 4.5367 | 3.3095 | 16.5393 | 17.4692 | 2.8337 | 2.0671 | 14.32 | 3.0953 | 0.50209 | 0.36627 | 3.0953 | 2.6914 | 0.43658 | 0.31848 | 0.29532 | 2.6914 | 0.43658 | 0.31848 | -8.15 | 2.6914 | 0.43658 | 0.31848 | -10.2952 | 2.6914 | 0.43658 | 0.31848 | -12.3641 | 2.6914 | 0.43658 | 0.31848 | -12.7912 | 2.6914 | 0.43658 | 0.31848 | -13.2611 | 2.6914 | 0.43658 | 0.31848 | -13.4974 | 1.4432 | 0.23411 | 0.17078 | -13.5592 | 7.0478 | 1.1432 | 0.83397 | -13.274 | 43.5645 | 7.3747 | 5.3797 | 20.1533 | 37.7064 | 6.1164 | 4.4618 | 19.0625 | 27.843 | 4.5164 | 3.2947 | 16.6085 | 17.7359 | 2.8769 | 2.0987 | 14.4074 | 4.2804 | 0.69432 | 0.5065 | 4.2804 | 2.6914 | 0.43658 | 0.31848 | 0.40095 | 2.6914 | 0.43658 | 0.31848 | -8.0402 | 2.6914 | 0.43658 | 0.31848 | -10.1833 | 2.6914 | 0.43658 | 0.31848 | -12.2469 | 2.6914 | 0.43658 | 0.31848 | -12.6636 | 2.6914 | 0.43658 | 0.31848 | -13.1234 | 2.6914 | 0.43658 | 0.31848 | -14.1316 | 2.6914 | 0.43658 | 0.31848 | -14.8423 | 2.498 | 0.40521 | 0.29559 | -15.01 | 43.5664 | 7.3771 | 5.3815 | 20.1591 | 43.753 | 7.2887 | 5.317 | 19.0697 | 42.3539 | 6.8702 | 5.0117 | 16.6275 | 39.2881 | 6.3729 | 4.649 | 14.4454 | 32.6419 | 5.2948 | 3.8625 | 8.5586 | 22.9785 | 3.7273 | 2.719 | 0.48595 | 13.6569 | 2.2153 | 1.616 | -7.9283 | 10.8429 | 1.7588 | 1.283 | -10.0401 | 7.7963 | 1.2646 | 0.92254 | -12.0615 | 5.8399 | 0.94729 | 0.69103 | -12.658 | 2.6613 | 0.43169 | 0.31491 | -13.9704 | 2.6914 | 0.43658 | 0.31848 | -14.9098 | 0.68211 | 0.11065 | 0.080714 | -15.3655 | 0.65052 | 0.10552 | 0.076975 | -14.6413
CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 26.4292 | 4.2871 | 3.1274 | 26.4292 | 25.4661 | 4.1309 | 3.0134 | 25.4661 | 24.0066 | 3.8941 | 2.8407 | 24.0066 | 22.4338 | 3.639 | 2.6546 | 22.4338 | 20.7104 | 3.3594 | 2.4507 | 20.7104 | 19.4325 | 3.1521 | 2.2994 | 19.4325 | 18.6713 | 3.0287 | 2.2094 | 18.6713 | 18.1843 | 2.9497 | 2.1517 | 18.1843 | 17.4719 | 2.8341 | 2.0674 | 17.4719 | 16.6971 | 2.7084 | 1.9758 | 16.6971 | 13.6635 | 2.2164 | 1.6168 | 13.6635 | 13.9154 | 2.2572 | 1.6466 | 13.9154 | 16.7658 | 2.7196 | 1.9839 | 16.7658 | 16.0698 | 2.6067 | 1.9015 | 16.0698 | 27.4815 | 4.4578 | 3.2519 | 27.4815 | 26.1686 | 4.2448 | 3.0965 | 26.1686 | 24.7603 | 4.0164 | 2.9299 | 24.7603 | 23.4291 | 3.8004 | 2.7724 | 23.4291 | 22.0558 | 3.5777 | 2.6099 | 22.0558 | 20.7285 | 3.3624 | 2.4528 | 20.7285 | 20.1992 | 3.2765 | 2.3902 | 20.1992 | 19.7534 | 3.2042 | 2.3374 | 19.7534 | 19.1209 | 3.1016 | 2.2626 | 19.1209 | 18.5521 | 3.0093 | 2.1953 | 18.5521 | 17.2472 | 2.7977 | 2.0409 | 17.2472 | 17.8765 | 2.8997 | 2.1153 | 17.8765 | 20.4195 | 3.3122 | 2.4162 | 20.4195 | 20.4678 | 3.3201 | 2.422 | 20.4678 | 27.4747 | 4.4567 | 3.2511 | 27.4747 | 26.1908 | 4.2484 | 3.0992 | 26.1908 | 24.7164 | 4.0092 | 2.9247 | 24.7164 | 23.2335 | 3.7687 | 2.7492 | 23.2335 | 21.7081 | 3.5213 | 2.5687 | 21.7081 | 20.2456 | 3.284 | 2.3957 | 20.2456 | 19.6175 | 3.1821 | 2.3213 | 19.6175 | 19.0901 | 3.0966 | 2.2589 | 19.0901 | 18.3836 | 2.982 | 2.1753 | 18.3836 | 17.7213 | 2.8746 | 2.097 | 17.7213 | 15.8425 | 2.5698 | 1.8746 | 15.8425 | 17.3878 | 2.8205 | 2.0575 | 17.3878 | 22.2992 | 3.6172 | 2.6387 | 22.2992 | 22.5117 | 3.6516 | 2.6638 | 22.5117 | 26.4592 | 4.2919 | 3.1309 | 26.4592 | 25.502 | 4.1367 | 3.0176 | 25.502 | 23.9815 | 3.89 | 2.8377 | 23.9815 | 22.2849 | 3.6148 | 2.637 | 22.2849 | 20.7865 | 3.3718 | 2.4597 | 20.7865 | 19.3336 | 3.1361 | 2.2877 | 19.3336 | 18.6384 | 3.0233 | 2.2055 | 18.6384 | 18.0103 | 2.9214 | 2.1312 | 18.0103 | 17.1749 | 2.7859 | 2.0323 | 17.1749 | 16.3148 | 2.6464 | 1.9305 | 16.3148 | 11.8975 | 1.9299 | 1.4078 | 11.8975 | 7.604 | 1.2334 | 0.89978 | 7.604 | 6.1814 | 1.0027 | 0.73144 | 6.1814 | 3.3978 | 0.55116 | 0.40207 | 3.3978 | 26.4707 | 4.2938 | 3.1323 | 26.4707 | 26.1431 | 4.2407 | 3.0935 | 26.1431 | 25.1724 | 4.0832 | 2.9786 | 25.1724 | 23.3118 | 3.7814 | 2.7585 | 23.3118 | 23.063 | 3.741 | 2.729 | 23.063 | 22.0036 | 3.5692 | 2.6037 | 22.0036 | 21.1495 | 3.4306 | 2.5026 | 21.1495 | 20.5167 | 3.328 | 2.4277 | 20.5167 | 19.6797 | 3.1922 | 2.3287 | 19.6797 | 18.4144 | 2.987 | 2.179 | 18.4144 | 17.6058 | 2.8558 | 2.0833 | 17.6058 | 9.4883 | 1.5391 | 1.1228 | 9.4883 | 4.9799 | 0.80779 | 0.58927 | 4.9799 | 4.6644 | 0.75661 | 0.55194 | 4.6644
CHAMBERHALL | BURY | KEARSLEY | 380280 | 411215 | 30.2256 | 9.3257 | 6.803 | 9.6132 | 30.3252 | 9.2553 | 6.7516 | 8.8346 | 30.4209 | 9.2476 | 6.746 | 8.9268 | 30.5568 | 9.1163 | 6.6502 | 8.2675 | 30.7304 | 9.0449 | 6.5981 | 8.1476 | 30.9379 | 8.8842 | 6.4809 | 7.4546 | 31.1767 | 8.7434 | 6.3782 | 6.9001 | 31.4414 | 8.6166 | 6.2857 | 6.4926 | 31.729 | 8.4133 | 6.1374 | 5.7073 | 32.0454 | 8.2139 | 5.9919 | 5.069 | 33.4925 | 7.5108 | 5.479 | 2.81 | 34.8607 | 7.4263 | 5.4174 | 1.4868 | 35.8145 | 7.9609 | 5.8073 | 0.90434 | 36.5731 | 8.0267 | 5.8554 | 0.47686 | 30.2209 | 9.2843 | 6.7728 | 9.7584 | 30.3102 | 9.1183 | 6.6517 | 9.1166 | 30.4349 | 9.0699 | 6.6164 | 9.0827 | 30.5756 | 8.9074 | 6.4979 | 8.4214 | 30.7343 | 8.8421 | 6.4502 | 8.3315 | 30.9148 | 8.678 | 6.3305 | 7.6829 | 31.1173 | 8.5567 | 6.242 | 7.1624 | 31.3383 | 8.4578 | 6.1698 | 6.7786 | 31.5778 | 8.294 | 6.0503 | 6.0107 | 31.8321 | 8.1574 | 5.9507 | 5.4453 | 32.4716 | 7.8414 | 5.7202 | 3.8365 | 33.0711 | 7.8684 | 5.7399 | 2.7271 | 33.6341 | 8.2259 | 6.0007 | 1.829 | 34.1149 | 8.2641 | 6.0286 | 1.3784 | 30.2258 | 9.2825 | 6.7714 | 9.6156 | 30.3258 | 9.1402 | 6.6676 | 8.8766 | 30.4222 | 9.08 | 6.6237 | 8.9754 | 30.5588 | 8.9059 | 6.4967 | 8.3403 | 30.7326 | 8.8211 | 6.4349 | 8.2381 | 30.9394 | 8.6396 | 6.3024 | 7.5723 | 31.1779 | 8.4872 | 6.1913 | 7.0411 | 31.4425 | 8.3605 | 6.0988 | 6.6528 | 31.7266 | 8.1596 | 5.9523 | 5.9034 | 32.0263 | 7.9649 | 5.8103 | 5.3294 | 33.3306 | 7.5305 | 5.4934 | 3.299 | 34.4009 | 7.6443 | 5.5764 | 2.3018 | 35.2488 | 8.3127 | 6.064 | 1.7147 | 35.7943 | 8.3739 | 6.1086 | 1.4745 | 30.2273 | 9.3297 | 6.8059 | 9.6193 | 30.3351 | 9.266 | 6.7594 | 8.8495 | 30.4649 | 9.2551 | 6.7514 | 8.9528 | 30.6584 | 9.1005 | 6.6387 | 8.3063 | 30.9182 | 9.0527 | 6.6038 | 8.2103 | 31.251 | 8.8794 | 6.4774 | 7.5379 | 31.6602 | 8.7168 | 6.3588 | 6.9909 | 32.1373 | 8.5899 | 6.2662 | 6.5895 | 32.6755 | 8.39 | 6.1204 | 5.8671 | 33.2802 | 8.2093 | 5.9886 | 5.3614 | 35.4925 | 7.1597 | 5.2229 | 1.8076 | 37.1358 | 6.0238 | 4.3943 | -4.9284 | 33.7771 | 5.479 | 3.9968 | -10.7691 | 29.8905 | 4.8485 | 3.5369 | -14.5765 | 30.2402 | 9.3375 | 6.8116 | 9.6191 | 30.3664 | 9.3104 | 6.7918 | 8.8173 | 30.512 | 9.2936 | 6.7796 | 8.9342 | 30.7038 | 9.174 | 6.6923 | 8.3513 | 30.9593 | 9.0928 | 6.633 | 8.3235 | 31.2831 | 8.9142 | 6.5028 | 7.7419 | 31.6996 | 8.7471 | 6.3809 | 7.2706 | 32.1734 | 8.6126 | 6.2828 | 6.952 | 32.712 | 8.4014 | 6.1287 | 6.1407 | 33.3557 | 8.0414 | 5.8661 | 4.4765 | 35.7128 | 7.3712 | 5.3772 | -3.3364 | 35.4764 | 5.7546 | 4.1979 | -9.5136 | 30.8162 | 4.9987 | 3.6465 | -13.3386 | 30.9077 | 5.0135 | 3.6573 | -12.448
CHAPEL WHARF | FREDERICK RD | KEARSLEY | 383499 | 398634 | 28.6824 | 10.1737 | 7.4216 | 19.8111 | 28.7041 | 9.9936 | 7.2902 | 18.8485 | 28.7209 | 9.9073 | 7.2273 | 18.5512 | 28.7417 | 9.8549 | 7.189 | 18.4468 | 28.7651 | 9.8027 | 7.1509 | 18.4518 | 28.791 | 9.7673 | 7.1251 | 18.3699 | 28.8178 | 9.7238 | 7.0934 | 18.2863 | 28.8453 | 9.6833 | 7.0638 | 18.2411 | 28.8768 | 9.6181 | 7.0163 | 18.1361 | 28.9229 | 9.529 | 6.9513 | 18.0336 | 29.1242 | 9.4179 | 6.8703 | 17.7113 | 29.295 | 9.3933 | 6.8523 | 17.468 | 29.4134 | 9.3623 | 6.8297 | 17.2917 | 29.4636 | 9.2973 | 6.7822 | 17.251 | 28.6765 | 10.2371 | 7.4678 | 20.3013 | 28.6963 | 10.1321 | 7.3912 | 19.8197 | 28.7208 | 10.0727 | 7.3479 | 19.6285 | 28.7439 | 10.0262 | 7.314 | 19.4971 | 28.7704 | 9.9899 | 7.2875 | 19.4634 | 28.7995 | 9.9465 | 7.2558 | 19.3629 | 28.8309 | 9.9055 | 7.2259 | 19.2538 | 28.864 | 9.8794 | 7.2069 | 19.1738 | 28.8989 | 9.8439 | 7.181 | 19.0393 | 28.9357 | 9.8067 | 7.1539 | 18.9177 | 29.0414 | 9.6762 | 7.0586 | 18.6706 | 29.1713 | 9.4104 | 6.8647 | 18.4175 | 29.2791 | 9.6712 | 7.055 | 18.2085 | 29.3665 | 9.7311 | 7.0987 | 18.0454 | 28.6824 | 10.236 | 7.467 | 19.8138 | 28.7041 | 10.1246 | 7.3858 | 18.8585 | 28.7209 | 10.056 | 7.3357 | 18.5678 | 28.7417 | 9.9824 | 7.282 | 18.4691 | 28.765 | 9.9277 | 7.2421 | 18.4785 | 28.7909 | 9.8662 | 7.1972 | 18.4015 | 28.8176 | 9.8003 | 7.1492 | 18.3227 | 28.8452 | 9.7438 | 7.108 | 18.2821 | 28.8765 | 9.6711 | 7.0549 | 18.1836 | 28.9219 | 9.5866 | 6.9933 | 18.0914 | 29.1201 | 9.535 | 6.9557 | 17.798 | 29.2882 | 9.5555 | 6.9706 | 17.5785 | 29.4052 | 9.6301 | 7.025 | 17.4178 | 29.4549 | 9.5984 | 7.0019 | 17.3793 | 28.6813 | 10.1764 | 7.4236 | 19.82 | 28.7055 | 10.0041 | 7.2979 | 18.8645 | 28.7248 | 9.9117 | 7.2304 | 18.5735 | 28.7515 | 9.8534 | 7.1879 | 18.4725 | 28.7848 | 9.7904 | 7.1419 | 18.4766 | 28.8276 | 9.7532 | 7.1149 | 18.3876 | 28.8822 | 9.7056 | 7.0801 | 18.2847 | 28.9409 | 9.6436 | 7.0349 | 18.2183 | 28.9987 | 9.5641 | 6.9769 | 18.1004 | 29.0605 | 9.4428 | 6.8884 | 18.0018 | 29.3457 | 9.3733 | 6.8377 | 17.6183 | 29.4374 | 9.1492 | 6.6742 | 16.8882 | 29.4766 | 8.9001 | 6.4925 | 16.1524 | 29.4904 | 8.7254 | 6.365 | 15.5834 | 28.6765 | 10.1788 | 7.4253 | 19.8294 | 28.6982 | 10.0347 | 7.3202 | 18.882 | 28.7131 | 9.9514 | 7.2594 | 18.5982 | 28.7381 | 9.8706 | 7.2004 | 18.5056 | 28.7756 | 9.7866 | 7.1392 | 18.5099 | 28.8197 | 9.6331 | 7.0272 | 18.426 | 28.8692 | 9.4869 | 6.9206 | 18.3363 | 28.9221 | 9.5796 | 6.9882 | 18.2837 | 28.9799 | 9.6056 | 7.0072 | 18.1724 | 29.101 | 9.5547 | 6.97 | 17.975 | 29.3106 | 9.344 | 6.8163 | 17.1523 | 29.3824 | 8.965 | 6.5399 | 16.3935 | 29.3969 | 8.8187 | 6.4331 | 15.8488 | 29.3697 | 8.7415 | 6.3768 | 15.9091
CHASSEN RD | BARTON | CARRINGTON | 375542 | 394453 | 30.832 | 11.8465 | 8.6418 | 13.4333 | 30.9244 | 11.7198 | 8.5494 | 13.1108 | 30.9867 | 11.4953 | 8.3857 | 12.6621 | 31.083 | 11.2796 | 8.2283 | 12.0694 | 31.2109 | 11.0973 | 8.0953 | 12.0761 | 31.3646 | 10.9162 | 7.9632 | 11.5401 | 31.5373 | 10.7629 | 7.8514 | 10.8819 | 31.7266 | 10.6539 | 7.7718 | 10.4767 | 31.9307 | 10.4903 | 7.6526 | 9.8378 | 32.1553 | 10.3498 | 7.5501 | 9.3648 | 32.8211 | 9.6292 | 7.0243 | 7.2546 | 33.3333 | 9.1654 | 6.6861 | 6.1521 | 33.6549 | 9.7362 | 7.1024 | 5.929 | 33.8613 | 9.8299 | 7.1707 | 6.1965 | 30.7829 | 11.6367 | 8.4888 | 13.6608 | 30.8349 | 10.942 | 7.982 | 13.5249 | 30.926 | 10.8398 | 7.9075 | 12.9831 | 31.0308 | 10.709 | 7.8121 | 12.3934 | 31.1497 | 10.5321 | 7.683 | 12.4284 | 31.2811 | 10.2661 | 7.4889 | 11.9431 | 31.4257 | 10.1474 | 7.4024 | 11.3286 | 31.5739 | 10.0765 | 7.3507 | 10.9536 | 31.7135 | 9.9654 | 7.2696 | 10.3492 | 31.8575 | 9.8605 | 7.1931 | 9.9861 | 32.2799 | 9.5888 | 6.9949 | 8.4797 | 32.6235 | 9.4787 | 6.9146 | 7.2575 | 32.8328 | 9.6284 | 7.0238 | 6.555 | 32.9336 | 9.6007 | 7.0036 | 6.1325 | 30.8327 | 11.6374 | 8.4893 | 13.4419 | 30.9253 | 10.9056 | 7.9555 | 13.1343 | 30.9878 | 10.8211 | 7.8938 | 12.704 | 31.0842 | 10.6848 | 7.7944 | 12.128 | 31.2115 | 10.4837 | 7.6477 | 12.145 | 31.3639 | 10.208 | 7.4466 | 11.627 | 31.5351 | 10.0821 | 7.3547 | 10.9878 | 31.7229 | 9.9585 | 7.2646 | 10.5968 | 31.9229 | 9.834 | 7.1738 | 9.9854 | 32.1343 | 9.7451 | 7.1089 | 9.5709 | 32.7604 | 9.3249 | 6.8024 | 7.6653 | 33.2109 | 9.2477 | 6.7461 | 6.7053 | 33.4905 | 9.4488 | 6.8928 | 6.5334 | 33.665 | 9.4938 | 6.9256 | 6.7881 | 30.8286 | 11.8488 | 8.6435 | 13.4537 | 30.9235 | 11.7291 | 8.5562 | 13.153 | 31.0051 | 11.5084 | 8.3952 | 12.7349 | 31.1374 | 11.2544 | 8.21 | 12.1782 | 31.3217 | 11.1349 | 8.1228 | 12.2375 | 31.5552 | 10.925 | 7.9696 | 11.7541 | 31.8362 | 10.7469 | 7.8397 | 11.1136 | 32.0793 | 10.6413 | 7.7627 | 10.7298 | 32.3208 | 10.4712 | 7.6386 | 10.1878 | 32.5874 | 10.3777 | 7.5704 | 9.8956 | 33.5298 | 9.4761 | 6.9127 | 7.0716 | 34.3828 | 8.1133 | 5.9186 | 1.0565 | 34.8969 | 7.7699 | 5.668 | -3.5685 | 35.1765 | 7.2485 | 5.2877 | -6.7093 | 30.8281 | 11.8499 | 8.6443 | 13.4393 | 30.9421 | 11.8188 | 8.6216 | 13.0787 | 31.038 | 11.6893 | 8.5272 | 12.6407 | 31.1738 | 11.4898 | 8.3817 | 12.0924 | 31.3603 | 11.4474 | 8.3507 | 12.1435 | 31.5854 | 11.3128 | 8.2525 | 11.6869 | 31.8482 | 11.1525 | 8.1356 | 11.1035 | 32.051 | 11.0567 | 8.0657 | 10.7953 | 32.279 | 10.8676 | 7.9277 | 10.1443 | 32.5706 | 10.5752 | 7.7144 | 8.8176 | 33.5614 | 9.076 | 6.6208 | 2.0234 | 34.1913 | 7.7335 | 5.6415 | -3.4055 | 34.4415 | 7.3756 | 5.3804 | -6.4327 | 34.3673 | 7.4064 | 5.4029 | -5.4839
CHATSWORTH ST | BARROW & SANDGATE | HARKER / HUTTON | 319188 | 470003 | 30.8722 | 10.4815 | 7.5332 | 13.6773 | 30.9273 | 10.4983 | 7.5453 | 13.3565 | 30.9706 | 10.4951 | 7.543 | 13.4274 | 31.035 | 10.3435 | 7.434 | 13.2299 | 31.1219 | 10.2144 | 7.3413 | 13.1728 | 31.2338 | 9.7873 | 7.0343 | 12.812 | 31.3648 | 9.287 | 6.6748 | 12.5393 | 31.5109 | 9.1178 | 6.5531 | 12.3952 | 31.672 | 8.8531 | 6.3629 | 12.0892 | 31.8492 | 8.8259 | 6.3433 | 11.8348 | 32.5379 | 8.413 | 6.0466 | 10.9237 | 32.9076 | 8.0294 | 5.7709 | 10.4595 | 33.1096 | 7.8345 | 5.6308 | 10.3684 | 33.2067 | 7.7464 | 5.5675 | 10.589 | 30.8689 | 10.5847 | 7.6075 | 13.8172 | 30.9294 | 10.5221 | 7.5625 | 13.649 | 31.0238 | 10.3539 | 7.4416 | 13.592 | 31.1381 | 10.1868 | 7.3215 | 13.3299 | 31.2694 | 10.0673 | 7.2356 | 13.247 | 31.4224 | 10.0005 | 7.1876 | 12.8643 | 31.5979 | 9.9838 | 7.1756 | 12.5549 | 31.7938 | 9.7995 | 7.0431 | 12.3333 | 32.0128 | 9.7708 | 7.0225 | 11.9948 | 32.2437 | 9.8367 | 7.0698 | 11.7118 | 32.4963 | 9.9252 | 7.1334 | 11.1697 | 32.692 | 9.7934 | 7.0387 | 10.8049 | 32.7866 | 9.6498 | 6.9355 | 10.621 | 32.8121 | 9.5025 | 6.8296 | 10.638 | 30.876 | 10.5804 | 7.6043 | 13.6876 | 30.9323 | 10.4851 | 7.5358 | 13.3909 | 30.975 | 10.3355 | 7.4283 | 13.4768 | 31.0397 | 10.2131 | 7.3403 | 13.2971 | 31.1262 | 10.3651 | 7.4496 | 13.2549 | 31.236 | 10.2295 | 7.3521 | 12.9142 | 31.3634 | 9.9588 | 7.1576 | 12.6594 | 31.505 | 9.6595 | 6.9425 | 12.5136 | 31.659 | 9.3515 | 6.7211 | 12.2469 | 31.8231 | 9.0805 | 6.5263 | 12.0275 | 32.4834 | 8.6306 | 6.203 | 11.2066 | 32.7816 | 8.3489 | 6.0005 | 10.8167 | 32.9194 | 8.1989 | 5.8927 | 10.7579 | 32.9662 | 8.0232 | 5.7664 | 10.9914 | 30.8756 | 10.4747 | 7.5284 | 13.6783 | 30.9346 | 10.4773 | 7.5303 | 13.356 | 30.9811 | 10.4067 | 7.4795 | 13.4244 | 31.0627 | 10.2358 | 7.3567 | 13.2242 | 31.1781 | 10.0381 | 7.2146 | 13.1578 | 31.334 | 9.4424 | 6.7864 | 12.7814 | 31.5274 | 9.216 | 6.6237 | 12.4811 | 31.7529 | 9.1708 | 6.5913 | 12.2892 | 32.0084 | 9.0713 | 6.5197 | 11.9957 | 32.2941 | 8.8927 | 6.3914 | 11.7842 | 33.087 | 8.0325 | 5.7731 | 9.9201 | 34.1045 | 6.7765 | 4.8704 | 4.8907 | 34.724 | 5.7828 | 4.1562 | 0.75121 | 31.3369 | 5.1594 | 3.7081 | -1.8799 | 30.855 | 10.485 | 7.5358 | 13.7355 | 30.9019 | 10.4745 | 7.5282 | 13.4409 | 30.9363 | 10.3411 | 7.4323 | 13.537 | 31.0011 | 9.8468 | 7.0771 | 13.3898 | 31.0987 | 9.9853 | 7.1766 | 13.3762 | 31.2371 | 9.4155 | 6.7671 | 13.0686 | 31.4213 | 9.4488 | 6.791 | 12.8313 | 31.6356 | 9.3491 | 6.7194 | 12.734 | 31.8868 | 9.0717 | 6.52 | 12.3263 | 32.1939 | 8.6139 | 6.191 | 11.1429 | 33.2142 | 7.0061 | 5.0354 | 5.5608 | 33.9962 | 5.6503 | 4.061 | 0.96195 | 30.2832 | 4.9859 | 3.5835 | -1.7847 | 30.6805 | 5.0513 | 3.6305 | -0.73056
CHEADLE HEATH | ADSWOOD | BREDBURY | 387062 | 389054 | 21.981 | 11.4039 | 8.319 | 8.7163 | 22.0484 | 11.3939 | 8.3117 | 8.6164 | 22.0649 | 11.3304 | 8.2654 | 8.3695 | 22.1139 | 11.2692 | 8.2208 | 8.2062 | 22.1847 | 11.1954 | 8.1669 | 7.953 | 22.2757 | 11.1484 | 8.1326 | 7.7471 | 22.3776 | 11.0243 | 8.042 | 7.1853 | 22.4878 | 10.9516 | 7.9891 | 7.0204 | 22.6061 | 10.8847 | 7.9402 | 6.8963 | 22.7344 | 10.7621 | 7.8508 | 6.4865 | 23.2881 | 10.2757 | 7.496 | 5.3784 | 23.8268 | 9.9699 | 7.2729 | 4.7874 | 24.2344 | 9.6536 | 7.0422 | 4.5266 | 24.6353 | 9.4696 | 6.9079 | 4.5822 | 21.916 | 11.402 | 8.3176 | 8.8199 | 21.9312 | 11.4121 | 8.325 | 8.7992 | 21.9744 | 11.3208 | 8.2584 | 8.4929 | 22.0347 | 11.2454 | 8.2034 | 8.3197 | 22.1029 | 11.1844 | 8.1589 | 8.0822 | 22.1785 | 11.1181 | 8.1105 | 7.8999 | 22.2619 | 11.0016 | 8.0255 | 7.3624 | 22.35 | 10.9618 | 7.9965 | 7.2164 | 22.4434 | 10.915 | 7.9623 | 7.1015 | 22.5395 | 10.8211 | 7.8938 | 6.7374 | 22.8557 | 10.5857 | 7.7221 | 5.9003 | 23.17 | 10.4147 | 7.5974 | 5.3126 | 23.4714 | 10.2653 | 7.4884 | 4.8437 | 23.7163 | 10.0444 | 7.3273 | 4.636 | 21.9811 | 11.4024 | 8.3179 | 8.7214 | 22.0488 | 11.3881 | 8.3075 | 8.6286 | 22.0656 | 11.2971 | 8.2411 | 8.3907 | 22.1152 | 11.2209 | 8.1855 | 8.2333 | 22.1862 | 11.149 | 8.133 | 7.9881 | 22.2772 | 11.0708 | 8.076 | 7.7901 | 22.3791 | 10.9358 | 7.9775 | 7.2392 | 22.4895 | 10.877 | 7.9346 | 7.0808 | 22.6065 | 10.7992 | 7.8779 | 6.9677 | 22.7282 | 10.7057 | 7.8097 | 6.5903 | 23.2255 | 10.3694 | 7.5643 | 5.6013 | 23.6079 | 10.124 | 7.3853 | 5.1394 | 23.9362 | 9.9428 | 7.2531 | 4.9293 | 24.1982 | 9.7385 | 7.1041 | 5.0389 | 21.9751 | 11.4071 | 8.3213 | 8.7272 | 22.0405 | 11.4027 | 8.3181 | 8.6436 | 22.065 | 11.3337 | 8.2678 | 8.4219 | 22.1325 | 11.2564 | 8.2114 | 8.2856 | 22.2339 | 11.196 | 8.1673 | 8.073 | 22.3735 | 11.1508 | 8.1344 | 7.9143 | 22.5442 | 11.0126 | 8.0335 | 7.4038 | 22.7423 | 10.9398 | 7.9804 | 7.2874 | 22.9272 | 10.8719 | 7.9309 | 7.2448 | 23.1117 | 10.747 | 7.8398 | 6.9555 | 24.0489 | 9.9755 | 7.277 | 5.3342 | 25.1363 | 9.0239 | 6.5828 | 1.6075 | 25.7279 | 8.0406 | 5.8655 | -1.5543 | 25.9432 | 7.5234 | 5.4882 | -3.5361 | 21.9757 | 11.4092 | 8.3229 | 8.7324 | 22.0532 | 11.4362 | 8.3426 | 8.6322 | 22.0864 | 11.3838 | 8.3043 | 8.4198 | 22.1553 | 11.3526 | 8.2816 | 8.3225 | 22.2574 | 11.2908 | 8.2365 | 8.1522 | 22.3987 | 11.2343 | 8.1952 | 8.0451 | 22.5804 | 11.0807 | 8.0832 | 7.5803 | 22.7775 | 10.9968 | 8.022 | 7.5097 | 22.9749 | 10.8482 | 7.9136 | 7.3877 | 23.2671 | 10.6337 | 7.7571 | 6.4335 | 24.3396 | 9.567 | 6.979 | 2.3157 | 25.1346 | 8.5563 | 6.2417 | -1.0484 | 25.4363 | 7.8868 | 5.7533 | -3.184 | 25.3819 | 7.8213 | 5.7056 | -2.5693
CHEADLE HULME | ADSWOOD | BREDBURY | 387386 | 386308 | 32.5838 | 13.0374 | 9.3702 | 11.5121 | 32.6503 | 12.8769 | 9.2549 | 11.2164 | 32.6738 | 12.6667 | 9.1038 | 10.7561 | 32.7436 | 12.5631 | 9.0293 | 10.4028 | 32.8416 | 12.5909 | 9.0493 | 10.2542 | 32.9611 | 12.498 | 8.9826 | 9.6899 | 33.0921 | 12.2871 | 8.831 | 8.8624 | 33.2322 | 12.1356 | 8.7221 | 8.4489 | 33.3816 | 11.9281 | 8.5729 | 8.0175 | 33.5438 | 11.63 | 8.3587 | 7.3086 | 34.1713 | 11.3234 | 8.1383 | 5.3559 | 34.6105 | 10.9698 | 7.8842 | 4.6995 | 34.8533 | 10.7076 | 7.6957 | 4.75 | 34.9739 | 10.5623 | 7.5913 | 5.4725 | 32.5248 | 13.098 | 9.4138 | 12.0141 | 32.5494 | 13.1738 | 9.4683 | 12.1113 | 32.6122 | 13.0586 | 9.3855 | 11.4678 | 32.7009 | 12.988 | 9.3347 | 11.0939 | 32.8011 | 12.9429 | 9.3023 | 10.9455 | 32.9126 | 12.8261 | 9.2184 | 10.4381 | 33.0348 | 12.6884 | 9.1194 | 9.6564 | 33.1645 | 12.6128 | 9.0651 | 9.2727 | 33.3027 | 12.5238 | 9.0011 | 8.8521 | 33.4467 | 12.3948 | 8.9084 | 8.213 | 33.7497 | 12.0196 | 8.6387 | 6.5976 | 33.9728 | 11.566 | 8.3127 | 5.6289 | 34.1111 | 11.5813 | 8.3237 | 5.0662 | 34.1881 | 11.5352 | 8.2906 | 5.1042 | 32.5838 | 13.0828 | 9.4029 | 11.5194 | 32.6503 | 13.0938 | 9.4107 | 11.2382 | 32.6738 | 13.013 | 9.3527 | 10.7955 | 32.7436 | 12.9658 | 9.3188 | 10.434 | 32.8411 | 12.9148 | 9.2821 | 10.2964 | 32.9599 | 12.7985 | 9.1986 | 9.746 | 33.0902 | 12.6397 | 9.0844 | 8.9332 | 33.2299 | 12.5379 | 9.0112 | 8.5307 | 33.3772 | 12.4155 | 8.9233 | 8.1198 | 33.5307 | 12.2349 | 8.7935 | 7.4691 | 34.1183 | 11.6303 | 8.3589 | 5.7025 | 34.5237 | 11.432 | 8.2164 | 5.149 | 34.7503 | 11.1061 | 7.9822 | 5.219 | 34.8664 | 10.9468 | 7.8677 | 5.9096 | 32.5764 | 13.042 | 9.3736 | 11.5707 | 32.638 | 12.8746 | 9.2532 | 11.3477 | 32.6649 | 12.6265 | 9.0749 | 10.9802 | 32.7495 | 12.648 | 9.0904 | 10.7405 | 32.8737 | 12.6583 | 9.0978 | 10.722 | 33.0347 | 12.5507 | 9.0204 | 10.3192 | 33.2236 | 12.3489 | 8.8754 | 9.6706 | 33.4375 | 12.1808 | 8.7546 | 9.4439 | 33.6717 | 11.9472 | 8.5867 | 9.2613 | 33.9336 | 11.8643 | 8.5271 | 8.8616 | 34.8816 | 11.263 | 8.095 | 6.7038 | 35.8023 | 9.9185 | 7.1286 | 2.0013 | 36.0813 | 8.7962 | 6.322 | -1.8089 | 36.1892 | 8.0931 | 5.8166 | -3.9406 | 32.5667 | 13.0441 | 9.3751 | 11.5709 | 32.6311 | 12.8104 | 9.2071 | 11.2898 | 32.6585 | 12.7167 | 9.1397 | 10.9175 | 32.7326 | 12.7218 | 9.1434 | 10.6848 | 32.8444 | 12.699 | 9.127 | 10.7238 | 32.9846 | 12.4714 | 8.9634 | 10.4102 | 33.1545 | 12.1629 | 8.7417 | 9.842 | 33.3402 | 12.1897 | 8.761 | 9.7152 | 33.5719 | 12.1807 | 8.7545 | 9.4596 | 33.9521 | 11.9466 | 8.5863 | 8.1868 | 35.0609 | 10.6118 | 7.6269 | 2.6983 | 35.4605 | 9.3074 | 6.6894 | -1.5171 | 35.512 | 8.6066 | 6.1857 | -3.9018 | 35.3127 | 8.6256 | 6.1994 | -2.325
CHEETHAM HILL | AGECROFT | KEARSLEY | 383606 | 402218 | 25.0978 | 16.3187 | 11.9043 | 5.6997 | 25.1814 | 16.1075 | 11.7502 | 5.2957 | 25.2591 | 15.9825 | 11.659 | 5.1521 | 25.3566 | 15.7036 | 11.4555 | 4.7685 | 25.4878 | 15.6109 | 11.3879 | 4.6168 | 25.6315 | 15.3895 | 11.2264 | 4.219 | 25.784 | 15.2692 | 11.1386 | 3.7966 | 25.946 | 15.0927 | 11.0099 | 3.3703 | 26.0843 | 14.9078 | 10.875 | 2.9568 | 26.2368 | 14.6688 | 10.7007 | 2.4425 | 26.7992 | 13.9587 | 10.1827 | 0.59557 | 27.2112 | 13.2465 | 9.6632 | -0.53272 | 27.4672 | 13.3128 | 9.7115 | -1.1159 | 27.6235 | 13.1732 | 9.6097 | -1.0472 | 25.093 | 16.1961 | 11.8148 | 5.8505 | 25.173 | 15.8979 | 11.5973 | 5.568 | 25.2754 | 15.5561 | 11.3479 | 5.3059 | 25.3568 | 15.3853 | 11.2233 | 4.8972 | 25.4682 | 15.1599 | 11.0589 | 4.7368 | 25.5932 | 15.0428 | 10.9735 | 4.3377 | 25.7283 | 14.9465 | 10.9032 | 3.8959 | 25.8714 | 14.826 | 10.8154 | 3.439 | 26.0225 | 14.7187 | 10.7371 | 2.9286 | 26.1804 | 14.604 | 10.6534 | 2.4685 | 26.6472 | 14.2565 | 10.3999 | 1.1775 | 26.8882 | 14.0392 | 10.2414 | 0.0066559 | 27.0406 | 13.9273 | 10.1597 | -0.86904 | 27.1373 | 13.6932 | 9.989 | -1.3363 | 25.0978 | 16.1915 | 11.8115 | 5.7125 | 25.1814 | 15.8651 | 11.5734 | 5.3424 | 25.2591 | 15.5891 | 11.372 | 5.2311 | 25.3566 | 15.3167 | 11.1733 | 4.8732 | 25.4874 | 15.0371 | 10.9693 | 4.747 | 25.6306 | 14.8916 | 10.8632 | 4.3774 | 25.7826 | 14.7578 | 10.7656 | 3.9832 | 25.9443 | 14.6183 | 10.6639 | 3.5848 | 26.081 | 14.4627 | 10.5504 | 3.2063 | 26.2269 | 14.3108 | 10.4395 | 2.7546 | 26.7584 | 13.6641 | 9.9678 | 1.1301 | 27.1437 | 13.3687 | 9.7523 | 0.16836 | 27.3846 | 13.4721 | 9.8277 | -0.32565 | 27.5352 | 13.1566 | 9.5976 | -0.23765 | 25.0965 | 16.3215 | 11.9063 | 5.7163 | 25.1907 | 16.1105 | 11.7524 | 5.3218 | 25.2956 | 15.9746 | 11.6533 | 5.184 | 25.4402 | 15.7425 | 11.484 | 4.7913 | 25.6237 | 15.545 | 11.3399 | 4.6384 | 25.776 | 15.3779 | 11.2179 | 4.2093 | 25.9527 | 15.1408 | 11.045 | 3.7026 | 26.15 | 14.9392 | 10.8979 | 3.1865 | 26.3655 | 14.6536 | 10.6896 | 2.735 | 26.6026 | 14.4731 | 10.5579 | 2.2656 | 27.344 | 13.4577 | 9.8172 | -0.26292 | 27.9723 | 12.2132 | 8.9094 | -5.1125 | 28.2537 | 11.4645 | 8.3632 | -8.798 | 28.3843 | 10.7905 | 7.8715 | -11.0999 | 25.0824 | 16.3275 | 11.9107 | 5.7395 | 25.1723 | 16.1564 | 11.7858 | 5.3483 | 25.2762 | 15.9965 | 11.6692 | 5.2272 | 25.4235 | 15.7672 | 11.5019 | 4.8625 | 25.5704 | 15.5755 | 11.3621 | 4.7133 | 25.7002 | 15.3509 | 11.1983 | 4.3174 | 25.8537 | 15.1651 | 11.0627 | 3.8782 | 26.0198 | 15.0034 | 10.9448 | 3.4397 | 26.2044 | 14.7968 | 10.7941 | 2.9518 | 26.4409 | 14.449 | 10.5403 | 1.7026 | 27.2025 | 13.1296 | 9.5778 | -3.9627 | 27.6501 | 11.7606 | 8.5792 | -8.2964 | 27.7665 | 11.1255 | 8.1159 | -10.7679 | 27.6563 | 11.1235 | 8.1144 | -9.8922
ALDERLEY & CHELFORD | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 33.6532 | 5.8911 | 4.234 | 16.9603 | 33.7943 | 5.6821 | 4.0838 | 15.7963 | 33.8207 | 5.5683 | 4.0021 | 15.3661 | 32.9959 | 5.4325 | 3.9045 | 14.8884 | 31.8637 | 5.2461 | 3.7705 | 14.3369 | 30.7517 | 5.063 | 3.6389 | 13.7004 | 29.4782 | 4.8534 | 3.4882 | 12.9241 | 28.4273 | 4.6803 | 3.3638 | 12.3825 | 24.8963 | 4.099 | 2.946 | 9.317 | 23.6887 | 3.9002 | 2.8031 | 8.608 | 18.3561 | 3.0222 | 2.1721 | 5.3846 | 17.899 | 2.9469 | 2.118 | 3.4979 | 30.6108 | 5.0398 | 3.6222 | 3.1665 | 39.9524 | 6.5779 | 4.7276 | 3.44 | 33.5725 | 5.9923 | 4.3068 | 17.5657 | 33.6467 | 5.8718 | 4.2202 | 16.9467 | 33.7567 | 5.7565 | 4.1373 | 16.4519 | 33.8717 | 5.635 | 4.05 | 15.9733 | 33.4363 | 5.505 | 3.9566 | 15.4639 | 32.6297 | 5.3722 | 3.8611 | 14.8944 | 31.6993 | 5.2191 | 3.751 | 14.1738 | 30.9812 | 5.1008 | 3.6661 | 13.6614 | 30.1775 | 4.9685 | 3.571 | 13.0389 | 29.3881 | 4.8385 | 3.4775 | 12.4243 | 27.0825 | 4.4589 | 3.2047 | 10.519 | 27.1939 | 4.4773 | 3.2179 | 9.0366 | 35.6728 | 6.264 | 4.5021 | 8.1989 | 35.8029 | 7.6537 | 5.5009 | 7.7754 | 33.6532 | 5.9893 | 4.3046 | 16.9676 | 33.7944 | 5.8592 | 4.2112 | 15.8252 | 33.8635 | 5.7217 | 4.1123 | 15.415 | 33.85 | 5.5731 | 4.0055 | 14.9539 | 32.8835 | 5.414 | 3.8912 | 14.4246 | 31.8907 | 5.2506 | 3.7737 | 13.8113 | 30.7807 | 5.0678 | 3.6423 | 13.0585 | 29.7296 | 4.8947 | 3.518 | 12.5362 | 28.5895 | 4.707 | 3.383 | 9.504 | 27.456 | 4.5204 | 3.2489 | 8.8702 | 24.3717 | 4.0126 | 2.8839 | 5.9118 | 24.6358 | 4.0561 | 2.9152 | 4.2132 | 38.8516 | 6.3966 | 4.5974 | 3.9609 | 39.9315 | 7.7521 | 5.5716 | 4.2488 | 33.648 | 5.8969 | 4.2382 | 17.0076 | 33.7931 | 5.691 | 4.0902 | 15.8939 | 33.8131 | 5.5671 | 4.0012 | 15.5222 | 32.9533 | 5.4255 | 3.8994 | 15.1031 | 31.8349 | 5.2414 | 3.7671 | 14.6213 | 30.6961 | 5.0539 | 3.6323 | 14.0563 | 29.3545 | 4.833 | 3.4736 | 13.3298 | 28.2551 | 4.652 | 3.3435 | 12.8457 | 24.7236 | 4.0706 | 2.9256 | 9.9348 | 23.5503 | 3.8774 | 2.7868 | 9.4476 | 17.3804 | 2.8615 | 2.0566 | 6.262 | 12.4233 | 2.0454 | 1.4701 | 1.4657 | 22.6759 | 3.7334 | 2.6833 | -0.47471 | 28.7371 | 4.7313 | 3.4005 | -1.6256 | 33.6635 | 5.8666 | 4.2164 | 16.8168 | 33.8348 | 5.6192 | 4.0386 | 15.5087 | 33.279 | 5.4791 | 3.938 | 15.1587 | 32.3299 | 5.3229 | 3.8257 | 14.7976 | 31.0671 | 5.115 | 3.6762 | 14.3525 | 29.8579 | 4.9159 | 3.5331 | 13.8553 | 28.5201 | 4.6956 | 3.3748 | 13.206 | 27.0942 | 4.4609 | 3.2061 | 12.2609 | 23.6451 | 3.893 | 2.798 | 9.3976 | 22.2586 | 3.6647 | 2.6339 | 8.5386 | 23.1874 | 3.8176 | 2.7438 | 2.8737 | 18.1834 | 2.9938 | 2.1517 | 0.19312 | 33.5899 | 5.5303 | 3.9747 | -0.81511 | 31.1235 | 5.1243 | 3.6829 | 0.042465
CHESTER RD T11 & T12 | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 25.1457 | 8.511 | 6.2087 | 10.1571 | 25.2537 | 8.2301 | 6.0038 | 8.595 | 25.255 | 8.1398 | 5.9379 | 8.2006 | 25.2868 | 8.0832 | 5.8966 | 8.1079 | 25.3349 | 8.0009 | 5.8365 | 7.9835 | 25.4018 | 7.9019 | 5.7643 | 7.7607 | 25.4698 | 7.833 | 5.7141 | 7.614 | 25.5385 | 7.7923 | 5.6844 | 7.4953 | 25.6073 | 7.715 | 5.628 | 7.3027 | 25.6779 | 7.6372 | 5.5712 | 7.173 | 26.0835 | 7.2064 | 5.257 | 6.4294 | 26.6376 | 7.4281 | 5.4187 | 5.7417 | 27.0873 | 7.8861 | 5.7528 | 5.2717 | 27.5742 | 8.0929 | 5.9036 | 4.824 | 25.0346 | 8.7276 | 6.3667 | 11.0181 | 25.0477 | 8.6004 | 6.2739 | 10.2934 | 25.0946 | 8.5429 | 6.2319 | 10.0381 | 25.1594 | 8.5067 | 6.2055 | 9.8875 | 25.2302 | 8.4613 | 6.1724 | 9.7299 | 25.306 | 8.413 | 6.1372 | 9.5109 | 25.387 | 8.371 | 6.1065 | 9.3482 | 25.4712 | 8.3335 | 6.0792 | 9.2048 | 25.5586 | 8.2841 | 6.0431 | 8.9915 | 25.6477 | 8.2425 | 6.0128 | 8.8419 | 25.945 | 8.1217 | 5.9247 | 8.2679 | 26.2853 | 8.1785 | 5.9661 | 7.7459 | 26.6394 | 8.504 | 6.2036 | 7.3009 | 26.9263 | 8.6232 | 6.2905 | 6.9662 | 25.1459 | 8.7272 | 6.3664 | 10.1596 | 25.2543 | 8.5991 | 6.2729 | 8.6004 | 25.2561 | 8.5395 | 6.2295 | 8.2077 | 25.2886 | 8.4987 | 6.1997 | 8.1174 | 25.3375 | 8.4469 | 6.1619 | 7.9957 | 25.405 | 8.3852 | 6.1169 | 7.7764 | 25.4736 | 8.3222 | 6.071 | 7.6329 | 25.5429 | 8.2906 | 6.0479 | 7.5173 | 25.6117 | 8.2349 | 6.0073 | 7.3299 | 25.6802 | 8.1861 | 5.9716 | 7.2106 | 26.0189 | 8.0114 | 5.8442 | 6.5459 | 26.3582 | 8.1779 | 5.9656 | 6.0657 | 26.7007 | 8.7911 | 6.413 | 5.6955 | 26.9836 | 9.0277 | 6.5856 | 5.4351 | 25.1375 | 8.5134 | 6.2104 | 10.1737 | 25.2376 | 8.2302 | 6.0038 | 8.6293 | 25.2329 | 8.1285 | 5.9296 | 8.2514 | 25.2609 | 8.0823 | 5.8959 | 8.1748 | 25.3079 | 7.9991 | 5.8352 | 8.0648 | 25.3843 | 7.9084 | 5.7691 | 7.8486 | 25.4733 | 7.8511 | 5.7273 | 7.6956 | 25.573 | 7.7945 | 5.686 | 7.5633 | 25.6824 | 7.711 | 5.6251 | 7.3564 | 25.8007 | 7.6427 | 5.5752 | 7.2218 | 26.5892 | 7.1656 | 5.2272 | 6.087 | 27.5636 | 7.0417 | 5.1368 | 4.3343 | 28.1934 | 7.2786 | 5.3096 | 3.0916 | 28.4523 | 7.3206 | 5.3403 | 2.2024 | 25.138 | 8.5132 | 6.2103 | 10.1675 | 25.242 | 8.2342 | 6.0067 | 8.6097 | 25.241 | 8.1278 | 5.9291 | 8.2271 | 25.2711 | 8.0776 | 5.8925 | 8.1514 | 25.3212 | 7.9967 | 5.8335 | 8.0395 | 25.4094 | 7.9016 | 5.7641 | 7.8186 | 25.521 | 7.8165 | 5.702 | 7.6531 | 25.6506 | 7.7437 | 5.6489 | 7.5046 | 25.7987 | 7.6405 | 5.5736 | 7.2595 | 25.9915 | 7.5215 | 5.4868 | 6.8953 | 26.998 | 7.7139 | 5.6272 | 4.9299 | 27.8815 | 7.2331 | 5.2764 | 3.3288 | 28.2693 | 7.2538 | 5.2916 | 2.3387 | 28.2445 | 7.2573 | 5.2941 | 2.621
CHESTER RD T13 | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 19.0781 | 19.0781 | 17.1752 | 13.3783 | 19.1036 | 19.1036 | 17.1328 | 13.1891 | 19.1087 | 19.1087 | 17.1102 | 13.0973 | 19.1217 | 19.1217 | 17.0837 | 13.0723 | 19.1397 | 19.1397 | 17.0541 | 13.0055 | 19.1623 | 19.1623 | 17.0289 | 12.9162 | 19.1858 | 19.1858 | 16.9737 | 12.8023 | 19.21 | 19.21 | 16.9318 | 12.7491 | 19.235 | 19.235 | 16.9345 | 12.6643 | 19.262 | 19.262 | 16.9079 | 12.563 | 19.3507 | 19.3507 | 16.792 | 12.2198 | 19.4116 | 19.4116 | 16.7617 | 12.034 | 19.4445 | 19.4445 | 16.8987 | 11.954 | 19.455 | 19.455 | 17.0208 | 11.956 | 19.0576 | 19.0576 | 17.1717 | 13.5172 | 19.0677 | 19.0677 | 17.1533 | 13.4469 | 19.0869 | 19.0869 | 17.1395 | 13.3386 | 19.1118 | 19.1118 | 17.1246 | 13.2871 | 19.1397 | 19.1397 | 17.1051 | 13.2038 | 19.1699 | 19.1699 | 17.0882 | 13.106 | 19.2029 | 19.2029 | 17.0621 | 12.9792 | 19.2361 | 19.2361 | 17.0456 | 12.9068 | 19.2663 | 19.2663 | 17.0256 | 12.8005 | 19.2978 | 19.2978 | 16.9983 | 12.6848 | 19.363 | 19.363 | 16.9461 | 12.45 | 19.4086 | 19.4086 | 16.9665 | 12.2745 | 19.4358 | 19.4358 | 17.1038 | 12.161 | 19.4454 | 19.4454 | 17.1951 | 12.1034 | 19.0781 | 19.0781 | 17.1727 | 13.3814 | 19.1036 | 19.1036 | 17.1479 | 13.1957 | 19.1087 | 19.1087 | 17.126 | 13.1082 | 19.1217 | 19.1217 | 17.1087 | 13.0864 | 19.1397 | 19.1397 | 17.093 | 13.024 | 19.1622 | 19.1622 | 17.0681 | 12.9403 | 19.1856 | 19.1856 | 17.0368 | 12.8303 | 19.2097 | 19.2097 | 17.0091 | 12.7826 | 19.2344 | 19.2344 | 16.9741 | 12.7045 | 19.2603 | 19.2603 | 16.9246 | 12.6137 | 19.3441 | 19.3441 | 16.9074 | 12.2974 | 19.4008 | 19.4008 | 16.9051 | 12.1302 | 19.4317 | 19.4317 | 17.1052 | 12.0575 | 19.4415 | 19.4415 | 17.2219 | 12.0574 | 19.076 | 19.076 | 17.1758 | 13.3838 | 19.0996 | 19.0996 | 17.1343 | 13.2001 | 19.1039 | 19.1039 | 17.1011 | 13.1141 | 19.1176 | 19.1176 | 17.069 | 13.0935 | 19.1377 | 19.1377 | 17.0495 | 13.0297 | 19.1646 | 19.1646 | 17.0232 | 12.9418 | 19.1954 | 19.1954 | 16.9435 | 12.8198 | 19.2283 | 19.2283 | 16.9501 | 12.7608 | 19.263 | 19.263 | 16.9312 | 12.6746 | 19.2998 | 19.2998 | 16.908 | 12.5826 | 19.4051 | 19.4051 | 16.7818 | 12.1977 | 19.4921 | 19.4921 | 16.6782 | 11.6309 | 19.5075 | 19.5075 | 16.7631 | 11.238 | 19.5003 | 19.5003 | 16.8307 | 10.9835 | 19.0742 | 19.0742 | 17.1759 | 13.3826 | 19.0973 | 19.0973 | 17.1336 | 13.1939 | 19.1 | 19.1 | 17.1033 | 13.1088 | 19.1112 | 19.1112 | 17.0638 | 13.0923 | 19.1293 | 19.1293 | 17.001 | 13.0289 | 19.1527 | 19.1527 | 16.993 | 12.9474 | 19.1791 | 19.1791 | 16.959 | 12.8367 | 19.2062 | 19.2062 | 16.9383 | 12.7924 | 19.2346 | 19.2346 | 16.9064 | 12.7192 | 19.2706 | 19.2706 | 16.8656 | 12.5537 | 19.3787 | 19.3787 | 16.7832 | 11.8486 | 19.4151 | 19.4151 | 16.6073 | 11.359 | 19.4052 | 19.4052 | 16.7601 | 11.1133 | 19.3689 | 19.3689 | 16.758 | 11.2414
CHORLEY SOUTH | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 358658 | 417041 | 24.7664 | 13.5911 | 9.7682 | 5.4311 | 24.8748 | 12.9172 | 9.2839 | 4.7 | 24.9439 | 12.197 | 8.7663 | 4.3649 | 25.0341 | 11.5092 | 8.2719 | 3.7972 | 25.1507 | 10.7481 | 7.7249 | 3.3052 | 25.2895 | 9.9414 | 7.1451 | 2.5379 | 25.4436 | 9.7127 | 6.9807 | 1.8587 | 25.6069 | 9.4873 | 6.8187 | 1.1803 | 25.7768 | 9.2173 | 6.6247 | 0.43319 | 25.9661 | 8.837 | 6.3513 | -0.431 | 26.7075 | 8.0883 | 5.8132 | -3.5263 | 27.2883 | 7.5534 | 5.4288 | -5.2975 | 27.6075 | 8.4257 | 6.0557 | -5.7745 | 27.8331 | 9.4025 | 6.7577 | -5.692 | 24.724 | 13.676 | 9.8292 | 5.6846 | 24.7967 | 12.9749 | 9.3253 | 5.1912 | 24.8936 | 12.2623 | 8.8132 | 4.7773 | 25.0005 | 11.5248 | 8.2831 | 4.2517 | 25.123 | 10.8052 | 7.7659 | 3.826 | 25.2578 | 10.1865 | 7.3213 | 3.1441 | 25.4064 | 10.0602 | 7.2304 | 2.5411 | 25.5637 | 9.9088 | 7.1216 | 1.9311 | 25.7308 | 9.7194 | 6.9855 | 1.2164 | 25.9052 | 9.501 | 6.8286 | 0.51775 | 26.3121 | 8.7893 | 6.3171 | -1.6546 | 26.6402 | 8.4857 | 6.0988 | -3.3006 | 26.8784 | 9.275 | 6.6661 | -4.1935 | 27.0491 | 10.0936 | 7.2545 | -4.8433 | 24.7664 | 13.6756 | 9.8289 | 5.4357 | 24.8749 | 12.9107 | 9.2792 | 4.747 | 24.9442 | 12.0241 | 8.642 | 4.4526 | 25.0345 | 10.9144 | 7.8444 | 3.9138 | 25.1509 | 10.2316 | 7.3537 | 3.4595 | 25.2892 | 9.7745 | 7.0251 | 2.7347 | 25.4428 | 9.5446 | 6.8599 | 2.0956 | 25.6059 | 9.3322 | 6.7073 | 1.4566 | 25.7739 | 9.0868 | 6.5308 | 0.76042 | 25.955 | 8.8309 | 6.347 | -0.018955 | 26.6453 | 8.092 | 5.8159 | -2.7939 | 27.1473 | 7.5937 | 5.4577 | -4.3258 | 27.4351 | 8.557 | 6.1501 | -4.7058 | 27.6146 | 9.4109 | 6.7638 | -4.5699 | 24.7624 | 13.594 | 9.7703 | 5.455 | 24.8751 | 12.9181 | 9.2845 | 4.7283 | 24.9488 | 12.2311 | 8.7907 | 4.3901 | 25.0578 | 11.4389 | 8.2214 | 3.8179 | 25.2038 | 10.6357 | 7.6441 | 3.3566 | 25.3877 | 9.749 | 7.0068 | 2.6083 | 25.6031 | 9.3586 | 6.7262 | 1.9192 | 25.8368 | 9.1393 | 6.5686 | 1.2213 | 26.0916 | 8.9594 | 6.4393 | 0.53175 | 26.3751 | 8.7964 | 6.3222 | -0.14801 | 27.3336 | 7.6095 | 5.4691 | -3.5314 | 28.1565 | 5.9691 | 4.2901 | -9.3619 | 28.6113 | 6.2238 | 4.4732 | -13.4061 | 28.8616 | 6.5683 | 4.7207 | -16.458 | 24.765 | 13.5923 | 9.7691 | 5.43 | 24.8788 | 13.3847 | 9.6199 | 4.6473 | 24.948 | 13.1564 | 9.4558 | 4.3016 | 25.0493 | 12.8916 | 9.2655 | 3.7343 | 25.1849 | 12.5782 | 9.0402 | 3.3072 | 25.3497 | 12.2868 | 8.8308 | 2.6296 | 25.5435 | 12.0371 | 8.6513 | 2.0284 | 25.7539 | 11.7205 | 8.4238 | 1.4527 | 25.9846 | 11.3889 | 8.1854 | 0.77618 | 26.2772 | 11.0021 | 7.9074 | -0.692 | 27.2824 | 9.7233 | 6.9883 | -7.3896 | 27.8966 | 8.1215 | 5.8371 | -12.3708 | 28.1021 | 7.4351 | 5.3437 | -15.0035 | 28.0244 | 7.2269 | 5.1941 | -14.3911
CHORLTON | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 19.7474 | 19.7474 | 18.1531 | 10.6458 | 19.788 | 19.788 | 18.1222 | 10.4178 | 19.8235 | 19.8235 | 18.0862 | 10.2095 | 19.878 | 19.878 | 18.0262 | 9.9885 | 19.9489 | 19.9489 | 17.9009 | 9.6988 | 20.0274 | 20.0274 | 17.8415 | 9.3898 | 20.1029 | 20.1029 | 17.8388 | 9.0162 | 20.183 | 20.183 | 17.8097 | 8.6897 | 20.2688 | 20.2688 | 17.745 | 8.381 | 20.3647 | 20.3647 | 17.7085 | 7.9954 | 20.7417 | 20.7417 | 17.4178 | 6.7008 | 21.0116 | 21.0116 | 17.2301 | 6.1504 | 21.1742 | 21.1742 | 17.1002 | 6.1019 | 21.2717 | 21.2717 | 17.0583 | 6.2746 | 19.7343 | 19.7343 | 18.2257 | 10.7266 | 19.7652 | 19.7652 | 18.1877 | 10.5684 | 19.8136 | 19.8136 | 18.138 | 10.3401 | 19.8712 | 19.8712 | 18.1031 | 10.1515 | 19.9373 | 19.9373 | 18.0706 | 9.9102 | 19.9959 | 19.9959 | 18.0365 | 9.6464 | 20.0605 | 20.0605 | 18.0001 | 9.3163 | 20.1289 | 20.1289 | 17.9688 | 9.0266 | 20.2016 | 20.2016 | 17.9341 | 8.7489 | 20.2779 | 20.2779 | 17.8873 | 8.4331 | 20.4576 | 20.4576 | 17.755 | 7.4602 | 20.5888 | 20.5888 | 17.6399 | 6.8276 | 20.6719 | 20.6719 | 17.5538 | 6.4902 | 20.7219 | 20.7219 | 17.5124 | 6.3073 | 19.7474 | 19.7474 | 18.2274 | 10.6521 | 19.788 | 19.788 | 18.1969 | 10.4383 | 19.8235 | 19.8235 | 18.1498 | 10.2444 | 19.878 | 19.878 | 18.1145 | 10.0333 | 19.9485 | 19.9485 | 18.0879 | 9.757 | 20.0267 | 20.0267 | 18.0458 | 9.4615 | 20.1019 | 20.1019 | 17.9875 | 9.1015 | 20.1817 | 20.1817 | 17.9455 | 8.7872 | 20.2664 | 20.2664 | 17.8992 | 8.496 | 20.3576 | 20.3576 | 17.8379 | 8.1501 | 20.7131 | 20.7131 | 17.6274 | 6.9918 | 20.9649 | 20.9649 | 17.4713 | 6.5258 | 21.1174 | 21.1174 | 17.352 | 6.4872 | 21.2114 | 21.2114 | 17.2146 | 6.6555 | 19.747 | 19.747 | 18.1519 | 10.6553 | 19.7918 | 19.7918 | 18.1162 | 10.4361 | 19.841 | 19.841 | 18.067 | 10.2426 | 19.9191 | 19.9191 | 17.997 | 10.0364 | 20.011 | 20.011 | 17.8658 | 9.7743 | 20.1136 | 20.1136 | 17.8656 | 9.4916 | 20.236 | 20.236 | 17.8416 | 9.1357 | 20.3717 | 20.3717 | 17.7934 | 8.8312 | 20.5174 | 20.5174 | 17.7554 | 8.5843 | 20.6781 | 20.6781 | 17.685 | 8.3037 | 21.2262 | 21.2262 | 17.28 | 6.7792 | 21.7579 | 21.7579 | 16.7884 | 4.1932 | 21.9885 | 21.9885 | 16.4161 | 2.4367 | 22.0899 | 22.0899 | 16.1877 | 1.373 | 19.755 | 19.755 | 18.1455 | 10.5941 | 19.8137 | 19.8137 | 18.077 | 10.3194 | 19.8659 | 19.8659 | 17.9982 | 10.1307 | 19.9339 | 19.9339 | 17.9045 | 9.9474 | 20.0125 | 20.0125 | 17.9572 | 9.7045 | 20.1058 | 20.1058 | 17.9235 | 9.4593 | 20.218 | 20.218 | 17.8654 | 9.1454 | 20.3377 | 20.3377 | 17.8205 | 8.896 | 20.4737 | 20.4737 | 17.7339 | 8.6442 | 20.682 | 20.682 | 17.6403 | 7.9423 | 21.2296 | 21.2296 | 17.0487 | 4.7392 | 21.5201 | 21.5201 | 16.5649 | 2.504 | 21.5971 | 21.5971 | 16.3229 | 1.4526 | 21.5363 | 21.5363 | 16.3223 | 2.1225
CHURCH | HUNCOAT | PADIHAM | 374687 | 428919 | 17.3838 | 17.3838 | 17.3838 | 12.1357 | 17.3974 | 17.3974 | 17.3974 | 12.0821 | 17.4197 | 17.4197 | 17.4197 | 12.0437 | 17.4525 | 17.4525 | 17.4525 | 11.9738 | 17.4966 | 17.4966 | 17.4966 | 11.8815 | 17.5531 | 17.5531 | 17.5531 | 11.7714 | 17.6216 | 17.6216 | 17.6216 | 11.6504 | 17.7004 | 17.7004 | 17.7004 | 11.5164 | 17.7892 | 17.7892 | 17.7892 | 11.3719 | 17.8925 | 17.8925 | 17.8925 | 11.2021 | 18.2906 | 18.2906 | 18.2906 | 10.5518 | 18.7449 | 18.7449 | 18.4456 | 9.9758 | 19.0951 | 19.0951 | 18.6851 | 9.6878 | 19.4188 | 19.4188 | 18.6692 | 9.5319 | 17.3859 | 17.3859 | 17.3859 | 12.1622 | 17.4058 | 17.4058 | 17.4058 | 12.1254 | 17.435 | 17.435 | 17.435 | 12.0515 | 17.4689 | 17.4689 | 17.4689 | 11.9709 | 17.5095 | 17.5095 | 17.5095 | 11.8759 | 17.5585 | 17.5585 | 17.5585 | 11.7657 | 17.6161 | 17.6161 | 17.6161 | 11.6428 | 17.6807 | 17.6807 | 17.6807 | 11.5036 | 17.7521 | 17.7521 | 17.7521 | 11.3544 | 17.8286 | 17.8286 | 17.8286 | 11.2008 | 18.1657 | 18.1657 | 18.1657 | 10.7789 | 18.4199 | 18.4199 | 18.4199 | 10.4648 | 18.6389 | 18.6389 | 18.6389 | 10.2505 | 18.8149 | 18.8149 | 18.8149 | 10.0832 | 17.3868 | 17.3868 | 17.3868 | 12.1391 | 17.4014 | 17.4014 | 17.4014 | 12.0907 | 17.4236 | 17.4236 | 17.4236 | 12.0577 | 17.4569 | 17.4569 | 17.4569 | 11.9925 | 17.5012 | 17.5012 | 17.5012 | 11.9057 | 17.5564 | 17.5564 | 17.5564 | 11.8012 | 17.6226 | 17.6226 | 17.6226 | 11.6861 | 17.6981 | 17.6981 | 17.6981 | 11.5633 | 17.7821 | 17.7821 | 17.7821 | 11.4285 | 17.8778 | 17.8778 | 17.8778 | 11.2749 | 18.2356 | 18.2356 | 18.2356 | 10.6898 | 18.5417 | 18.5417 | 18.5417 | 10.2551 | 18.7895 | 18.7895 | 18.7895 | 10.0565 | 18.9834 | 18.9834 | 18.8821 | 9.9998 | 17.3875 | 17.3875 | 17.3875 | 12.1378 | 17.4056 | 17.4056 | 17.4056 | 12.086 | 17.4339 | 17.4339 | 17.4339 | 12.0515 | 17.4799 | 17.4799 | 17.4799 | 11.9867 | 17.5437 | 17.5437 | 17.5437 | 11.9024 | 17.6337 | 17.6337 | 17.6337 | 11.7993 | 17.7511 | 17.7511 | 17.7511 | 11.6814 | 17.893 | 17.893 | 17.893 | 11.5531 | 18.0126 | 18.0126 | 18.0126 | 11.4351 | 18.1234 | 18.1234 | 18.1234 | 11.3089 | 18.8357 | 18.8357 | 18.4068 | 10.0958 | 19.7967 | 19.7967 | 18.0295 | 7.4136 | 20.3985 | 20.3985 | 17.9274 | 5.2652 | 20.6091 | 20.6091 | 17.7309 | 3.9974 | 17.3819 | 17.3819 | 17.3819 | 12.159 | 17.4011 | 17.4011 | 17.4011 | 12.1175 | 17.4331 | 17.4331 | 17.4331 | 12.0926 | 17.4804 | 17.4804 | 17.4804 | 12.0498 | 17.5461 | 17.5461 | 17.5461 | 11.9884 | 17.6451 | 17.6451 | 17.6451 | 11.9101 | 17.7823 | 17.7823 | 17.7823 | 11.8103 | 17.946 | 17.946 | 17.946 | 11.7 | 18.0849 | 18.0849 | 18.0849 | 11.5044 | 18.2804 | 18.2804 | 18.2804 | 10.885 | 19.2125 | 19.2125 | 18.5413 | 7.9659 | 19.9751 | 19.9751 | 18.0757 | 5.517 | 20.3423 | 20.3423 | 17.8074 | 4.134 | 20.33 | 20.33 | 17.8119 | 4.5977
CLARENDON RD | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 369051 | 429883 | 23.1644 | 13.8152 | 10.078 | 15.3846 | 23.2127 | 11.854 | 8.6473 | 14.964 | 23.2513 | 9.8053 | 7.1528 | 14.9508 | 23.3127 | 7.7736 | 5.6707 | 14.5029 | 23.3971 | 5.7193 | 4.1722 | 14.4053 | 23.3267 | 3.7838 | 2.7602 | 13.8707 | 21.7467 | 3.5275 | 2.5733 | 13.5016 | 20.8013 | 3.3742 | 2.4614 | 13.1422 | 19.687 | 3.1934 | 2.3296 | 12.6128 | 18.4155 | 2.9872 | 2.1791 | 12.026 | 17.5158 | 2.8412 | 2.0726 | 10.2606 | 25.0658 | 5.1698 | 3.7713 | 9.3965 | 25.3486 | 9.6902 | 7.0689 | 9.2 | 25.5525 | 10.4346 | 7.6119 | 9.4117 | 23.1449 | 13.8473 | 10.1014 | 15.4984 | 23.1803 | 11.9384 | 8.7089 | 15.1689 | 23.2318 | 10.0471 | 7.3292 | 15.0697 | 23.2907 | 8.0948 | 5.9051 | 14.6114 | 23.3606 | 6.2614 | 4.5676 | 14.533 | 23.4388 | 4.3398 | 3.1658 | 14.0473 | 23.5266 | 4.2018 | 3.0652 | 13.6926 | 23.6199 | 4.1471 | 3.0253 | 13.3809 | 23.719 | 4.0793 | 2.9758 | 12.8948 | 23.8221 | 4.0031 | 2.9202 | 12.4103 | 24.1014 | 4.0179 | 2.931 | 11.1997 | 24.3325 | 5.4823 | 3.9993 | 10.327 | 24.5063 | 8.3583 | 6.0973 | 9.7218 | 24.6311 | 9.4525 | 6.8955 | 9.4582 | 23.1644 | 13.8434 | 10.0986 | 15.3926 | 23.2128 | 11.7774 | 8.5915 | 14.9898 | 23.2515 | 9.8263 | 7.1682 | 14.9897 | 23.3131 | 7.9737 | 5.8167 | 14.5583 | 23.3972 | 6.1541 | 4.4894 | 14.4674 | 23.4979 | 4.4136 | 3.2197 | 13.9606 | 23.6079 | 4.3218 | 3.1527 | 13.612 | 23.7283 | 4.1921 | 3.058 | 13.2684 | 23.8577 | 4.0351 | 2.9435 | 12.766 | 23.9961 | 3.9787 | 2.9024 | 12.2347 | 24.2903 | 3.9401 | 2.8743 | 10.6259 | 24.9422 | 6.0327 | 4.4008 | 9.8991 | 25.191 | 10.5576 | 7.7016 | 9.7408 | 25.3522 | 11.1273 | 8.1172 | 9.9978 | 23.1624 | 13.8138 | 10.077 | 15.3913 | 23.2124 | 11.8507 | 8.6449 | 14.9757 | 23.261 | 9.7594 | 7.1193 | 14.9687 | 23.3418 | 7.6944 | 5.613 | 14.5243 | 23.4507 | 5.6355 | 4.111 | 14.4427 | 22.8078 | 3.6997 | 2.6988 | 13.9183 | 20.8171 | 3.3767 | 2.4633 | 13.6443 | 19.5863 | 3.1771 | 2.3176 | 13.3742 | 17.9194 | 2.9067 | 2.1204 | 12.9409 | 17.5556 | 2.8477 | 2.0774 | 12.536 | 15.5588 | 2.5238 | 1.8411 | 10.3765 | 24.1722 | 3.921 | 2.8603 | 5.741 | 26.6345 | 7.5773 | 5.5275 | 1.972 | 26.8418 | 7.7651 | 5.6645 | -0.36636 | 23.1538 | 13.8173 | 10.0795 | 15.4002 | 23.2048 | 13.6686 | 9.9711 | 14.9711 | 23.2522 | 13.0863 | 9.5463 | 14.9733 | 23.324 | 13.0426 | 9.5144 | 14.5639 | 23.4275 | 12.6312 | 9.2143 | 14.5148 | 23.5562 | 12.5139 | 9.1287 | 14.045 | 23.7201 | 12.5167 | 9.1307 | 13.8254 | 23.8993 | 12.4093 | 9.0524 | 13.6354 | 24.1112 | 12.2078 | 8.9054 | 13.1067 | 24.4214 | 11.9743 | 8.7351 | 11.8997 | 25.4755 | 10.4613 | 7.6313 | 6.77 | 25.9993 | 9.0482 | 6.6005 | 2.6312 | 26.1728 | 8.3731 | 6.1081 | 0.050352 | 26.0873 | 8.2697 | 6.0326 | 0.88203
CLAUGHTON | LANCASTER | HEYSHAM | 355872 | 466268 | 8.7415 | 8.7415 | 8.7415 | 3.3019 | 8.7663 | 8.7663 | 8.7663 | 3.273 | 8.7736 | 8.7736 | 8.7736 | 3.2395 | 8.7896 | 8.7896 | 8.7896 | 3.1661 | 8.8108 | 8.8108 | 8.8108 | 3.0711 | 8.838 | 8.838 | 8.838 | 3.0081 | 8.8684 | 8.8684 | 8.8684 | 2.9183 | 8.9006 | 8.9006 | 8.9006 | 2.7907 | 8.9338 | 8.9338 | 8.9338 | 2.7346 | 8.973 | 8.973 | 8.973 | 2.5859 | 9.1985 | 9.1985 | 9.1985 | 1.9041 | 9.3296 | 9.3296 | 9.3296 | 1.4375 | 9.4162 | 9.4162 | 9.4162 | 1.1781 | 9.4865 | 9.4865 | 9.4865 | 1.381 | 8.7256 | 8.7256 | 8.7256 | 3.344 | 8.7379 | 8.7379 | 8.7379 | 3.3511 | 8.7582 | 8.7582 | 8.7582 | 3.2913 | 8.7824 | 8.7824 | 8.7824 | 3.2259 | 8.8099 | 8.8099 | 8.8099 | 3.1367 | 8.8409 | 8.8409 | 8.8409 | 3.0804 | 8.8755 | 8.8755 | 8.8755 | 2.9944 | 8.907 | 8.907 | 8.907 | 2.8693 | 8.9386 | 8.9386 | 8.9386 | 2.8091 | 8.9713 | 8.9713 | 8.9713 | 2.7124 | 9.0528 | 9.0528 | 9.0528 | 2.4076 | 9.1297 | 9.1297 | 9.1297 | 1.9817 | 9.198 | 9.198 | 9.198 | 1.6252 | 9.2474 | 9.2474 | 9.2474 | 1.5779 | 8.7415 | 8.7415 | 8.7415 | 3.3044 | 8.7663 | 8.7663 | 8.7663 | 3.281 | 8.7738 | 8.7738 | 8.7738 | 3.2539 | 8.7898 | 8.7898 | 8.7898 | 3.1871 | 8.8111 | 8.8111 | 8.8111 | 3.0981 | 8.8382 | 8.8382 | 8.8382 | 3.04 | 8.8686 | 8.8686 | 8.8686 | 2.9553 | 8.9008 | 8.9008 | 8.9008 | 2.8334 | 8.9338 | 8.9338 | 8.9338 | 2.7839 | 8.9716 | 8.9716 | 8.9716 | 2.6512 | 9.1854 | 9.1854 | 9.1854 | 2.0342 | 9.2849 | 9.2849 | 9.2849 | 1.6287 | 9.3555 | 9.3555 | 9.3555 | 1.3516 | 9.3981 | 9.3981 | 9.3981 | 1.6164 | 8.7398 | 8.7398 | 8.7398 | 3.3069 | 8.7641 | 8.7641 | 8.7641 | 3.2738 | 8.7727 | 8.7727 | 8.7727 | 3.2347 | 8.7918 | 8.7918 | 8.7918 | 3.1572 | 8.8189 | 8.8189 | 8.8189 | 3.0466 | 8.8563 | 8.8563 | 8.8563 | 2.957 | 8.9022 | 8.9022 | 8.9022 | 2.8224 | 8.9543 | 8.9543 | 8.9543 | 2.6433 | 9.0045 | 9.0045 | 9.0045 | 2.5569 | 9.1282 | 9.1282 | 9.1282 | 2.3554 | 9.322 | 9.322 | 9.322 | 1.7547 | 9.5077 | 9.5077 | 9.5077 | 0.7774 | 9.5959 | 9.5959 | 9.5959 | 0.18264 | 9.6296 | 9.6296 | 9.6296 | -0.024558 | 8.738 | 8.738 | 8.738 | 3.3133 | 8.7627 | 8.7627 | 8.7627 | 3.2844 | 8.7701 | 8.7701 | 8.7701 | 3.2533 | 8.7867 | 8.7867 | 8.7867 | 3.182 | 8.8116 | 8.8116 | 8.8116 | 3.0707 | 8.9394 | 8.9394 | 8.9394 | 2.8959 | 8.9784 | 8.9784 | 8.9784 | 2.7877 | 9.0233 | 9.0233 | 9.0233 | 2.6402 | 9.0666 | 9.0666 | 9.0666 | 2.5789 | 9.1182 | 9.1182 | 9.1182 | 2.3642 | 9.3331 | 9.3331 | 9.3331 | 1.3178 | 9.4795 | 9.4795 | 9.4795 | 0.50429 | 9.5303 | 9.5303 | 9.5303 | 0.096984 | 9.5078 | 9.5078 | 9.5078 | 0.40823
BLACKBURN RD CLAYTON | HUNCOAT | PADIHAM | 374632 | 430529 | 26.1756 | 13.1878 | 9.6203 | 18.9252 | 26.2138 | 12.808 | 9.3433 | 18.6612 | 26.259 | 12.466 | 9.0938 | 18.5139 | 26.3198 | 12.16 | 8.8705 | 18.3567 | 26.398 | 11.8876 | 8.6719 | 18.1711 | 26.488 | 11.5949 | 8.4583 | 17.9363 | 26.5967 | 11.4649 | 8.3635 | 17.6742 | 26.721 | 11.3912 | 8.3097 | 17.3959 | 26.8609 | 11.246 | 8.2038 | 17.1186 | 27.0201 | 11.1385 | 8.1254 | 16.7897 | 27.8295 | 10.6009 | 7.7332 | 15.5477 | 28.6413 | 10.4437 | 7.6185 | 14.7178 | 29.1264 | 11.3882 | 8.3076 | 14.3668 | 29.5537 | 11.3755 | 8.2982 | 14.2234 | 26.1704 | 13.2112 | 9.6374 | 19.0813 | 26.2034 | 12.9832 | 9.4711 | 18.9448 | 26.2552 | 12.7323 | 9.288 | 18.763 | 26.3121 | 12.4798 | 9.1038 | 18.5929 | 26.3718 | 12.2052 | 8.9035 | 18.4069 | 26.4392 | 11.951 | 8.7181 | 18.1846 | 26.5187 | 11.8437 | 8.6398 | 17.9322 | 26.6075 | 11.7519 | 8.5728 | 17.6604 | 26.7049 | 11.6677 | 8.5115 | 17.3839 | 26.8087 | 11.575 | 8.4438 | 17.095 | 27.3429 | 11.3032 | 8.2455 | 16.3095 | 27.8476 | 11.168 | 8.1469 | 15.7297 | 28.2366 | 11.8593 | 8.6512 | 15.3617 | 28.5629 | 12.2339 | 8.9245 | 15.1499 | 26.179 | 13.2034 | 9.6317 | 18.9333 | 26.2186 | 12.9506 | 9.4473 | 18.6782 | 26.2648 | 12.6629 | 9.2374 | 18.5401 | 26.3264 | 12.3484 | 9.008 | 18.3914 | 26.4048 | 12.0462 | 8.7875 | 18.2044 | 26.4927 | 11.7523 | 8.5731 | 17.9792 | 26.5986 | 11.6303 | 8.4841 | 17.7278 | 26.7191 | 11.5061 | 8.3935 | 17.4676 | 26.8527 | 11.3743 | 8.2974 | 17.2042 | 27.0044 | 11.2195 | 8.1845 | 16.9106 | 27.7387 | 11.0187 | 8.038 | 15.7814 | 28.3439 | 11.1386 | 8.1254 | 15.1977 | 28.7469 | 12.3009 | 8.9733 | 15.0285 | 29.0094 | 12.3451 | 9.0055 | 15.0457 | 26.1803 | 13.1873 | 9.6199 | 18.9308 | 26.2248 | 12.8092 | 9.3441 | 18.6733 | 26.2857 | 12.5025 | 9.1204 | 18.5365 | 26.3708 | 12.194 | 8.8953 | 18.393 | 26.485 | 11.8532 | 8.6468 | 18.2298 | 26.6409 | 11.5915 | 8.4558 | 18.0161 | 26.841 | 11.4784 | 8.3733 | 17.7644 | 27.0555 | 11.2903 | 8.2361 | 17.4951 | 27.2902 | 11.1559 | 8.1381 | 17.263 | 27.5565 | 11.0544 | 8.064 | 17.0206 | 28.8298 | 10.2355 | 7.4667 | 15.0664 | 30.4046 | 9.2608 | 6.7556 | 10.6171 | 31.142 | 9.3379 | 6.8119 | 7.1451 | 31.5095 | 8.8659 | 6.4676 | 5.0315 | 26.1857 | 13.191 | 9.6227 | 18.9277 | 26.2481 | 13.1538 | 9.5955 | 18.6497 | 26.3234 | 13.0218 | 9.4992 | 18.514 | 26.4178 | 12.946 | 9.4439 | 18.3876 | 26.5419 | 12.7612 | 9.3091 | 18.2336 | 26.7163 | 12.69 | 9.2572 | 18.0432 | 26.9197 | 12.5615 | 9.1635 | 17.8113 | 27.1646 | 12.4698 | 9.0965 | 17.5661 | 27.4766 | 12.2592 | 8.9429 | 17.2164 | 27.9405 | 11.9061 | 8.6853 | 16.1813 | 29.4149 | 11.1485 | 8.1327 | 11.345 | 30.6952 | 9.7882 | 7.1403 | 7.3169 | 31.2151 | 9.0275 | 6.5854 | 5.0707 | 31.1606 | 8.9986 | 6.5643 | 5.8154
CLEVELEYS | BISPHAM | PENWORTHAM WEST / STANAH | 332286 | 443104 | 24.3718 | 13.4739 | 9.8291 | 8.1283 | 24.4224 | 12.8274 | 9.3574 | 7.9565 | 24.4557 | 12.4329 | 9.0696 | 7.7023 | 24.5262 | 12.2141 | 8.91 | 7.3302 | 24.6155 | 11.8961 | 8.6781 | 6.9571 | 24.721 | 11.6641 | 8.5088 | 6.5229 | 24.8389 | 11.4765 | 8.3719 | 6.0186 | 24.9666 | 11.2893 | 8.2354 | 5.5078 | 25.1042 | 11.1175 | 8.1101 | 4.9919 | 25.2589 | 10.9086 | 7.9577 | 4.3883 | 25.8542 | 10.1903 | 7.4337 | 2.3948 | 26.2813 | 9.8929 | 7.2167 | 1.4294 | 26.5325 | 10.4943 | 7.6555 | 1.2693 | 26.6781 | 10.4811 | 7.6458 | 1.5376 | 24.356 | 13.2609 | 9.6736 | 8.1636 | 24.3961 | 12.9024 | 9.4121 | 8.0144 | 24.4639 | 12.5403 | 9.148 | 7.7139 | 24.5528 | 12.4373 | 9.0729 | 7.3459 | 24.6517 | 12.0276 | 8.774 | 7.0461 | 24.7623 | 11.7366 | 8.5617 | 6.6559 | 24.8857 | 11.5928 | 8.4568 | 6.1905 | 25.019 | 11.4465 | 8.3501 | 5.7148 | 25.1622 | 11.2987 | 8.2422 | 5.2274 | 25.311 | 11.127 | 8.117 | 4.7165 | 25.5874 | 10.8943 | 7.9472 | 3.2724 | 25.7907 | 10.7701 | 7.8566 | 2.2256 | 25.9156 | 11.1088 | 8.1037 | 1.6506 | 25.9898 | 11.3788 | 8.3007 | 1.3009 | 24.3718 | 13.2503 | 9.6659 | 8.1358 | 24.4224 | 13.0053 | 9.4872 | 7.9825 | 24.4557 | 12.7325 | 9.2882 | 7.7635 | 24.5262 | 12.3074 | 8.978 | 7.41 | 24.6151 | 11.7646 | 8.5821 | 7.0596 | 24.72 | 11.6475 | 8.4967 | 6.6487 | 24.8374 | 11.5126 | 8.3983 | 6.1677 | 24.9647 | 11.3734 | 8.2968 | 5.6793 | 25.1005 | 11.2238 | 8.1876 | 5.1949 | 25.248 | 11.0648 | 8.0716 | 4.6561 | 25.8094 | 10.4319 | 7.6099 | 2.8868 | 26.2078 | 10.3986 | 7.5857 | 2.071 | 26.4434 | 11.0669 | 8.0731 | 1.9666 | 26.5836 | 10.9761 | 8.0069 | 2.2357 | 24.3678 | 13.4723 | 9.8279 | 8.1392 | 24.4175 | 12.8348 | 9.3628 | 7.9796 | 24.4603 | 12.5455 | 9.1518 | 7.7522 | 24.5513 | 12.1879 | 8.8909 | 7.4036 | 24.6717 | 11.9252 | 8.6992 | 7.0804 | 24.8234 | 11.5364 | 8.4156 | 6.6943 | 25.0076 | 11.3059 | 8.2475 | 6.2191 | 25.2159 | 11.0421 | 8.055 | 5.7493 | 25.4419 | 10.7939 | 7.874 | 5.336 | 25.6918 | 10.7561 | 7.8464 | 4.9123 | 26.6313 | 9.8487 | 7.1845 | 2.3499 | 27.4976 | 8.6862 | 6.3365 | -2.8631 | 27.9093 | 8.375 | 6.1095 | -6.8914 | 28.1441 | 7.7065 | 5.6218 | -9.6659 | 24.357 | 13.4769 | 9.8312 | 8.1596 | 24.4093 | 12.9521 | 9.4484 | 7.9667 | 24.4537 | 12.5885 | 9.1832 | 7.7132 | 24.5332 | 12.3961 | 9.0428 | 7.3886 | 24.6477 | 12.2359 | 8.9259 | 7.0813 | 24.7846 | 11.9142 | 8.6913 | 6.7447 | 24.9508 | 11.6595 | 8.5054 | 6.337 | 25.1327 | 11.3866 | 8.3063 | 5.9521 | 25.3523 | 11.2727 | 8.2232 | 5.467 | 25.7013 | 11.054 | 8.0637 | 4.178 | 26.6384 | 10.1748 | 7.4224 | -1.7413 | 27.1676 | 8.8095 | 6.4264 | -6.4415 | 27.3222 | 8.1038 | 5.9116 | -9.0906 | 27.2138 | 8.0513 | 5.8733 | -8.3074
CLIFTON JUNCTION | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 22.3548 | 9.3246 | 6.7018 | 10.8105 | 22.4307 | 9.1582 | 6.5821 | 10.4168 | 22.4482 | 9.0227 | 6.4848 | 10.3497 | 22.4846 | 8.8739 | 6.3778 | 10.1847 | 22.5362 | 8.7437 | 6.2843 | 10.061 | 22.6015 | 8.7018 | 6.2542 | 9.8832 | 22.6715 | 8.5648 | 6.1557 | 9.5703 | 22.7449 | 8.4823 | 6.0964 | 9.2905 | 22.8214 | 8.403 | 6.0394 | 9.0122 | 22.9032 | 8.2843 | 5.9541 | 8.7044 | 23.3759 | 7.653 | 5.5004 | 7.4006 | 23.9508 | 7.3246 | 5.2643 | 6.4599 | 24.4029 | 7.2615 | 5.219 | 6.0089 | 24.8848 | 7.1069 | 5.1079 | 5.6765 | 22.2942 | 9.3433 | 6.7152 | 11.0623 | 22.3169 | 9.1886 | 6.604 | 10.909 | 22.3554 | 9.0893 | 6.5326 | 10.7631 | 22.4062 | 8.9605 | 6.4401 | 10.5594 | 22.4629 | 8.8101 | 6.332 | 10.4162 | 22.5236 | 8.7544 | 6.292 | 10.2436 | 22.5881 | 8.6947 | 6.2491 | 9.9552 | 22.6543 | 8.6225 | 6.1971 | 9.6969 | 22.7227 | 8.5623 | 6.1539 | 9.433 | 22.7916 | 8.491 | 6.1027 | 9.1606 | 23.1153 | 8.1925 | 5.8881 | 8.1153 | 23.454 | 7.9392 | 5.7061 | 7.3014 | 23.7897 | 7.5306 | 5.4124 | 6.775 | 24.0788 | 7.6433 | 5.4934 | 6.4035 | 22.3549 | 9.3443 | 6.7159 | 10.8031 | 22.4311 | 9.1371 | 6.567 | 10.4059 | 22.4493 | 9.0332 | 6.4924 | 10.3713 | 22.4862 | 8.852 | 6.3621 | 10.2118 | 22.5384 | 8.683 | 6.2406 | 10.0959 | 22.6041 | 8.5903 | 6.174 | 9.9002 | 22.6746 | 8.5024 | 6.1108 | 9.5773 | 22.7485 | 8.4116 | 6.0456 | 9.3007 | 22.8249 | 8.3177 | 5.9781 | 9.0293 | 22.9039 | 8.2121 | 5.9022 | 8.7421 | 23.3146 | 7.6409 | 5.4917 | 7.548 | 23.6999 | 7.6007 | 5.4627 | 6.7928 | 24.0568 | 7.3636 | 5.2923 | 6.4219 | 24.3615 | 7.434 | 5.343 | 6.2178 | 22.3499 | 9.3236 | 6.7011 | 10.8243 | 22.4241 | 9.1487 | 6.5754 | 10.4472 | 22.4396 | 9.0199 | 6.4828 | 10.3854 | 22.4809 | 8.8682 | 6.3738 | 10.2211 | 22.5409 | 8.7393 | 6.2811 | 10.1046 | 22.6273 | 8.6433 | 6.2121 | 9.9246 | 22.7321 | 8.5498 | 6.1449 | 9.6571 | 22.8524 | 8.4386 | 6.065 | 9.4075 | 22.9853 | 8.3259 | 5.984 | 9.1516 | 23.1327 | 8.1922 | 5.8879 | 8.8704 | 24.0103 | 7.1688 | 5.1523 | 7.1721 | 25.031 | 6.5726 | 4.7239 | 4.2754 | 25.6967 | 6.1555 | 4.4241 | 2.0229 | 26.0001 | 5.8883 | 4.2321 | 0.49166 | 22.3526 | 9.3276 | 6.7039 | 10.8281 | 22.4277 | 9.1064 | 6.5449 | 10.4426 | 22.4478 | 9.0601 | 6.5117 | 10.3774 | 22.4931 | 8.9329 | 6.4202 | 10.2151 | 22.5571 | 8.7635 | 6.2985 | 10.1063 | 22.6543 | 8.5766 | 6.1641 | 9.9318 | 22.7798 | 8.4303 | 6.0591 | 9.6628 | 22.9262 | 8.2523 | 5.9311 | 9.3899 | 23.0964 | 8.0826 | 5.8091 | 9.0726 | 23.3163 | 7.7818 | 5.593 | 8.3906 | 24.3968 | 7.0105 | 5.0386 | 5.1705 | 25.2993 | 6.4504 | 4.636 | 2.5015 | 25.6751 | 6.1274 | 4.4038 | 0.92759 | 25.687 | 5.853 | 4.2067 | 1.0261
CLOVER HILL | NELSON | PADIHAM | 386638 | 437064 | 29.636 | 13.3182 | 9.7155 | 18.1298 | 29.6703 | 13.1189 | 9.5701 | 17.9643 | 29.6972 | 12.7878 | 9.3285 | 17.8449 | 29.7405 | 12.7378 | 9.2921 | 17.6708 | 29.7988 | 12.6604 | 9.2355 | 17.4757 | 29.8704 | 12.5319 | 9.1418 | 17.2357 | 29.9516 | 12.5696 | 9.1694 | 16.9721 | 30.0401 | 12.5575 | 9.1605 | 16.6557 | 30.1365 | 12.5617 | 9.1636 | 16.3034 | 30.2471 | 12.4461 | 9.0792 | 15.9087 | 30.6493 | 12.0779 | 8.8107 | 14.5505 | 30.9339 | 11.8949 | 8.6771 | 13.8634 | 31.0981 | 11.4407 | 8.3459 | 13.7704 | 31.2015 | 11.2734 | 8.2238 | 13.9367 | 29.6255 | 13.3123 | 9.7111 | 18.2021 | 29.6537 | 13.1506 | 9.5932 | 18.0905 | 29.6993 | 12.9743 | 9.4646 | 17.923 | 29.7488 | 12.818 | 9.3505 | 17.7443 | 29.8068 | 12.7111 | 9.2726 | 17.5619 | 29.8741 | 12.5765 | 9.1744 | 17.3413 | 29.9494 | 12.5163 | 9.1305 | 17.0863 | 30.0306 | 12.4272 | 9.0655 | 16.7921 | 30.1177 | 12.3531 | 9.0114 | 16.4827 | 30.2095 | 12.3197 | 8.987 | 16.1717 | 30.4068 | 12.1625 | 8.8724 | 15.3132 | 30.5545 | 12.0614 | 8.7986 | 14.7433 | 30.651 | 12.0481 | 8.7889 | 14.4679 | 30.7156 | 12.0161 | 8.7656 | 14.3163 | 29.636 | 13.3124 | 9.7112 | 18.1366 | 29.6703 | 13.1534 | 9.5953 | 17.9807 | 29.6972 | 12.9479 | 9.4453 | 17.8709 | 29.7406 | 12.8325 | 9.3612 | 17.7064 | 29.7987 | 12.7215 | 9.2802 | 17.5226 | 29.8699 | 12.6019 | 9.1929 | 17.2943 | 29.9508 | 12.5364 | 9.1451 | 17.0423 | 30.039 | 12.4492 | 9.0815 | 16.7326 | 30.1341 | 12.3528 | 9.0112 | 16.3983 | 30.2399 | 12.2387 | 8.928 | 16.0437 | 30.6158 | 11.8635 | 8.6543 | 14.8095 | 30.8697 | 11.7205 | 8.5499 | 14.2223 | 31.0184 | 11.3343 | 8.2682 | 14.163 | 31.1075 | 11.1235 | 8.1145 | 14.3309 | 29.635 | 13.3218 | 9.7181 | 18.1343 | 29.6708 | 13.1592 | 9.5995 | 17.9712 | 29.7036 | 12.9565 | 9.4516 | 17.8565 | 29.7577 | 12.7819 | 9.3242 | 17.688 | 29.8324 | 12.6521 | 9.2295 | 17.5052 | 29.9284 | 12.5561 | 9.1595 | 17.2741 | 30.0451 | 12.6238 | 9.2089 | 17.0078 | 30.1781 | 12.5797 | 9.1767 | 16.7253 | 30.3213 | 12.5405 | 9.1481 | 16.4782 | 30.4817 | 12.4451 | 9.0785 | 16.223 | 31.2049 | 11.7515 | 8.5725 | 14.1399 | 31.8594 | 10.5031 | 7.6619 | 9.1814 | 32.187 | 9.2058 | 6.7155 | 5.3079 | 32.3592 | 8.6949 | 6.3428 | 2.9576 | 29.6259 | 13.3307 | 9.7246 | 18.1558 | 29.6584 | 13.375 | 9.7569 | 17.9991 | 29.688 | 13.3727 | 9.7552 | 17.8987 | 29.7338 | 13.3765 | 9.758 | 17.764 | 29.8009 | 13.3318 | 9.7254 | 17.6104 | 29.8848 | 13.1962 | 9.6264 | 17.4237 | 29.9903 | 13.1265 | 9.5756 | 17.2054 | 30.1075 | 13.0679 | 9.5329 | 16.9788 | 30.2687 | 12.9683 | 9.4602 | 16.5887 | 30.5935 | 12.6344 | 9.2166 | 15.3819 | 31.313 | 11.2452 | 8.2032 | 9.8121 | 31.7117 | 9.8788 | 7.2064 | 5.3704 | 31.8534 | 8.8938 | 6.4879 | 2.9856 | 31.7641 | 9.0386 | 6.5935 | 4.0911
COG LANE | HUNCOAT | PADIHAM | 382462 | 432232 | 37.3625 | 11.5147 | 8.3998 | 16.7404 | 37.455 | 9.8672 | 7.198 | 15.9683 | 37.5117 | 8.3119 | 6.0634 | 15.6298 | 37.5924 | 6.7658 | 4.9356 | 15.3943 | 31.7475 | 5.1498 | 3.7567 | 15.1161 | 22.2104 | 3.6027 | 2.6282 | 14.7493 | 21.2834 | 3.4524 | 2.5185 | 14.3561 | 20.4914 | 3.3239 | 2.4247 | 13.937 | 19.2873 | 3.1286 | 2.2823 | 13.5338 | 18.4305 | 2.9896 | 2.1809 | 13.0455 | 15.792 | 2.5616 | 1.8687 | 11.0466 | 27.0896 | 4.3942 | 3.2055 | 9.7376 | 40.8948 | 8.4798 | 6.1859 | 9.2242 | 41.6254 | 9.1681 | 6.688 | 9.0163 | 37.3078 | 11.6016 | 8.4632 | 17.1968 | 37.3607 | 10.0106 | 7.3026 | 16.829 | 37.4497 | 8.4049 | 6.1313 | 16.4706 | 37.5343 | 6.8082 | 4.9665 | 16.1755 | 31.9226 | 5.1782 | 3.7774 | 15.8679 | 21.907 | 3.5535 | 2.5923 | 15.4973 | 21.0372 | 3.4124 | 2.4893 | 15.089 | 20.2654 | 3.2872 | 2.398 | 14.6492 | 19.5118 | 3.165 | 2.3088 | 14.1897 | 18.6516 | 3.0255 | 2.207 | 13.7156 | 17.3459 | 2.8137 | 2.0525 | 12.2813 | 24.5018 | 3.9744 | 2.8993 | 11.1536 | 39.8774 | 6.7174 | 4.9002 | 10.4443 | 40.2902 | 7.6051 | 5.5478 | 9.9252 | 37.3628 | 11.6024 | 8.4638 | 16.7554 | 37.4556 | 9.9845 | 7.2836 | 16.0034 | 37.5132 | 8.3525 | 6.093 | 15.6847 | 37.5949 | 6.6983 | 4.8863 | 15.4645 | 30.7451 | 4.9871 | 3.6381 | 15.206 | 20.4321 | 3.3143 | 2.4177 | 14.8594 | 19.4002 | 3.1469 | 2.2956 | 14.4865 | 18.2697 | 2.9635 | 2.1619 | 14.0878 | 16.9666 | 2.7521 | 2.0077 | 13.7109 | 15.458 | 2.5074 | 1.8291 | 13.2693 | 15.9518 | 2.5875 | 1.8876 | 11.5101 | 28.7259 | 4.6596 | 3.3991 | 10.4913 | 40.3459 | 9.0849 | 6.6273 | 10.1062 | 40.8006 | 9.6814 | 7.0624 | 10.0599 | 37.3599 | 11.5142 | 8.3994 | 16.7512 | 37.4608 | 9.8718 | 7.2013 | 15.9886 | 37.5414 | 8.3106 | 6.0624 | 15.6567 | 37.6727 | 6.7508 | 4.9246 | 15.4169 | 31.3994 | 5.0933 | 3.7155 | 15.1476 | 21.9924 | 3.5674 | 2.6024 | 14.7765 | 20.9849 | 3.404 | 2.4831 | 14.3504 | 19.4722 | 3.1586 | 2.3041 | 13.8865 | 18.6217 | 3.0206 | 2.2035 | 13.4846 | 17.4428 | 2.8294 | 2.064 | 13.0604 | 12.0505 | 1.9547 | 1.4259 | 9.8612 | 15.4541 | 2.5068 | 1.8287 | 2.3031 | 33.3787 | 5.4144 | 3.9497 | -3.661 | 31.9332 | 5.1799 | 3.7786 | -7.8382 | 37.3404 | 11.5275 | 8.4091 | 16.8084 | 37.4402 | 11.4209 | 8.3314 | 16.0774 | 37.5209 | 11.373 | 8.2964 | 15.7725 | 37.6553 | 11.2787 | 8.2276 | 15.583 | 37.8508 | 11.1383 | 8.1252 | 15.3608 | 38.0095 | 10.9647 | 7.9986 | 15.0469 | 38.2188 | 10.8127 | 7.8877 | 14.6743 | 38.4666 | 10.6415 | 7.7628 | 14.2643 | 38.7806 | 10.5064 | 7.6643 | 13.6675 | 39.2336 | 9.9958 | 7.2918 | 11.9249 | 41.0442 | 8.8758 | 6.4748 | 3.6922 | 42.2586 | 6.8548 | 5.0005 | -3.2576 | 35.3315 | 5.7311 | 4.1808 | -7.2583 | 34.4797 | 5.5929 | 4.08 | -6.4131
CONISTON | ULVERSTON | HARKER / HUTTON | 329874 | 497641 | 4.6166 | 4.6166 | 4.6166 | 1.4761 | 4.6552 | 4.6552 | 4.6552 | 1.3152 | 4.7091 | 4.7091 | 4.7091 | 1.2853 | 4.7644 | 4.7644 | 4.7644 | 1.2331 | 4.8057 | 4.8057 | 4.8057 | 1.1051 | 4.8342 | 4.8342 | 4.8342 | 0.99715 | 4.8683 | 4.8683 | 4.8683 | 0.89524 | 4.8971 | 4.8971 | 4.8971 | 0.84285 | 4.9287 | 4.9287 | 4.9287 | 0.71055 | 4.9671 | 4.9671 | 4.9671 | 0.56859 | 5.1004 | 5.1004 | 5.1004 | 0.083482 | 5.1905 | 5.1905 | 5.1905 | -0.14949 | 5.2351 | 5.2351 | 5.2351 | -0.22616 | 5.2388 | 5.2388 | 5.2388 | -0.12496 | 4.6337 | 4.6337 | 4.6337 | 1.5444 | 4.6893 | 4.6893 | 4.6893 | 1.4433 | 4.7474 | 4.7474 | 4.7474 | 1.3799 | 4.7809 | 4.7809 | 4.7809 | 1.313 | 4.8152 | 4.8152 | 4.8152 | 1.1781 | 4.8545 | 4.8545 | 4.8545 | 1.0557 | 4.9007 | 4.9007 | 4.9007 | 0.93975 | 4.9336 | 4.9336 | 4.9336 | 0.88037 | 4.9691 | 4.9691 | 4.9691 | 0.72929 | 5.007 | 5.007 | 5.007 | 0.59122 | 5.0644 | 5.0644 | 5.0644 | 0.32133 | 5.1179 | 5.1179 | 5.1179 | 0.054113 | 5.1532 | 5.1532 | 5.1532 | -0.14475 | 5.1687 | 5.1687 | 5.1687 | -0.25552 | 4.6166 | 4.6166 | 4.6166 | 1.4796 | 4.6552 | 4.6552 | 4.6552 | 1.3233 | 4.7091 | 4.7091 | 4.7091 | 1.2965 | 4.7644 | 4.7644 | 4.7644 | 1.2387 | 4.8056 | 4.8056 | 4.8056 | 1.1157 | 4.834 | 4.834 | 4.834 | 1.0155 | 4.8679 | 4.8679 | 4.8679 | 0.91658 | 4.8967 | 4.8967 | 4.8967 | 0.86568 | 4.928 | 4.928 | 4.928 | 0.7398 | 4.965 | 4.965 | 4.965 | 0.60875 | 5.0916 | 5.0916 | 5.0916 | 0.14673 | 5.1761 | 5.1761 | 5.1761 | -0.075027 | 5.2182 | 5.2182 | 5.2182 | -0.15236 | 5.2214 | 5.2214 | 5.2214 | -0.057396 | 4.6173 | 4.6173 | 4.6173 | 1.4785 | 4.6563 | 4.6563 | 4.6563 | 1.3169 | 4.7081 | 4.7081 | 4.7081 | 1.2877 | 4.7602 | 4.7602 | 4.7602 | 1.2384 | 4.817 | 4.817 | 4.817 | 1.11 | 4.863 | 4.863 | 4.863 | 0.99752 | 4.9092 | 4.9092 | 4.9092 | 0.89125 | 4.9563 | 4.9563 | 4.9563 | 0.84667 | 5.0069 | 5.0069 | 5.0069 | 0.72943 | 5.0579 | 5.0579 | 5.0579 | 0.63502 | 5.2079 | 5.2079 | 5.2079 | 0.17583 | 5.3104 | 5.3104 | 5.3104 | -0.54854 | 5.3437 | 5.3437 | 5.3437 | -1.0585 | 5.3485 | 5.3485 | 5.3485 | -1.4076 | 4.6295 | 4.6295 | 4.6295 | 1.4628 | 4.6775 | 4.6775 | 4.6775 | 1.2889 | 4.7209 | 4.7209 | 4.7209 | 1.266 | 4.7555 | 4.7555 | 4.7555 | 1.2184 | 4.7953 | 4.7953 | 4.7953 | 1.0889 | 4.8364 | 4.8364 | 4.8364 | 0.991 | 4.8868 | 4.8868 | 4.8868 | 0.89736 | 4.9315 | 4.9315 | 4.9315 | 0.86151 | 4.9743 | 4.9743 | 4.9743 | 0.75819 | 5.0272 | 5.0272 | 5.0272 | 0.55015 | 5.1849 | 5.1849 | 5.1849 | -0.39217 | 5.2497 | 5.2497 | 5.2497 | -1.049 | 5.2454 | 5.2454 | 5.2454 | -1.4082 | 5.2127 | 5.2127 | 5.2127 | -1.2146
COPSE RD | THORNTON | PENWORTHAM WEST / STANAH | 333013 | 446934 | 21.8708 | 3.6732 | 2.6795 | 11.6016 | 21.6665 | 3.5145 | 2.5638 | 11.1734 | 21.0137 | 3.4086 | 2.4865 | 10.9176 | 19.2938 | 3.1297 | 2.283 | 10.6007 | 19.2121 | 3.1164 | 2.2734 | 10.3978 | 18.6685 | 3.0282 | 2.209 | 10.0884 | 18.4105 | 2.9864 | 2.1785 | 9.7114 | 17.9348 | 2.9092 | 2.1222 | 9.3039 | 17.1598 | 2.7835 | 2.0305 | 8.9474 | 15.8018 | 2.5632 | 1.8698 | 8.3871 | 11.6219 | 1.8852 | 1.3752 | 6.0777 | 8.6477 | 1.4027 | 1.0233 | 4.6519 | 24.7942 | 6.09 | 4.4426 | 4.1785 | 25.0825 | 10.6197 | 7.7469 | 4.1459 | 21.8523 | 3.7211 | 2.7145 | 11.9116 | 21.9295 | 3.6391 | 2.6547 | 11.7452 | 21.3399 | 3.4615 | 2.5251 | 11.3772 | 20.1445 | 3.2676 | 2.3837 | 10.9959 | 19.1377 | 3.1043 | 2.2646 | 10.7527 | 17.8268 | 2.8917 | 2.1094 | 10.4276 | 17.269 | 2.8012 | 2.0434 | 10.021 | 16.4319 | 2.6654 | 1.9444 | 9.502 | 14.9535 | 2.4256 | 1.7694 | 8.8001 | 13.589 | 2.2043 | 1.608 | 7.9123 | 12.1889 | 1.9772 | 1.4423 | 6.9964 | 10.8222 | 1.7555 | 1.2806 | 5.7675 | 24.3552 | 5.6602 | 4.129 | 5.0491 | 24.5045 | 9.6442 | 7.0353 | 4.5675 | 21.872 | 3.7241 | 2.7166 | 11.6153 | 21.9576 | 3.6616 | 2.6711 | 11.2095 | 21.0281 | 3.411 | 2.4882 | 10.978 | 20.2499 | 3.2847 | 2.3962 | 10.6813 | 18.2443 | 2.9594 | 2.1588 | 10.5004 | 14.381 | 2.3327 | 1.7017 | 10.2141 | 15.8337 | 2.5684 | 1.8736 | 9.861 | 15.0953 | 2.4486 | 1.7862 | 9.4783 | 13.8745 | 2.2506 | 1.6418 | 9.152 | 12.378 | 2.0078 | 1.4647 | 8.6945 | 7.6313 | 1.2379 | 0.903 | 6.5656 | 3.2059 | 0.52003 | 0.37935 | 3.2059 | 24.5403 | 5.6074 | 4.0906 | 4.9637 | 24.7587 | 10.1883 | 7.4322 | 4.991 | 21.8678 | 3.6744 | 2.6804 | 11.6169 | 21.6785 | 3.5165 | 2.5652 | 11.1983 | 21.3881 | 3.4694 | 2.5309 | 10.9441 | 21.0818 | 3.4197 | 2.4946 | 10.6154 | 20.0638 | 3.2545 | 2.3741 | 10.4024 | 19.0907 | 3.0967 | 2.259 | 10.0658 | 18.1026 | 2.9364 | 2.1421 | 9.6253 | 16.6526 | 2.7012 | 1.9705 | 9.1426 | 15.9161 | 2.5817 | 1.8833 | 8.741 | 14.652 | 2.3767 | 1.7338 | 8.2622 | 7.5373 | 1.2226 | 0.89189 | 5.4954 | 2.6914 | 0.43658 | 0.31848 | -1.0381 | 20.4903 | 3.3237 | 2.4246 | -6.1656 | 26.4778 | 7.3371 | 5.3523 | -9.6595 | 21.8526 | 3.679 | 2.6838 | 11.6297 | 21.9366 | 3.6635 | 2.6724 | 11.2025 | 21.5093 | 3.489 | 2.5452 | 10.9533 | 22.1059 | 3.7356 | 2.7251 | 10.6413 | 22.2477 | 3.7524 | 2.7373 | 10.4377 | 22.4022 | 3.6664 | 2.6746 | 10.1306 | 21.3356 | 3.4608 | 2.5246 | 9.7344 | 20.8984 | 3.3899 | 2.4729 | 9.3072 | 19.3321 | 3.1359 | 2.2876 | 8.8411 | 17.3033 | 2.8068 | 2.0475 | 7.5145 | 6.1424 | 0.99636 | 0.72683 | 0.21385 | 2.6914 | 0.43658 | 0.31848 | -5.7575 | 25.6383 | 7.8609 | 5.7344 | -9.1998 | 25.626 | 7.7327 | 5.6409 | -8.3159
COX GREEN | BOLTON | KEARSLEY | 371893 | 413641 | 23.5964 | 12.7126 | 9.1368 | 9.1899 | 23.6327 | 12.5409 | 9.0134 | 8.4993 | 23.6686 | 12.6158 | 9.0673 | 8.5959 | 23.7303 | 12.445 | 8.9445 | 7.825 | 23.8121 | 12.3213 | 8.8555 | 7.9347 | 23.9106 | 12.2742 | 8.8217 | 7.3591 | 24.0254 | 12.1783 | 8.7528 | 6.8124 | 24.1514 | 12.0777 | 8.6804 | 6.4638 | 24.2894 | 11.903 | 8.5549 | 5.7947 | 24.4473 | 11.703 | 8.4112 | 5.0571 | 25.0472 | 11.0362 | 7.9319 | 3.1699 | 25.4379 | 10.537 | 7.5732 | 2.5761 | 25.6601 | 10.3944 | 7.4707 | 2.6495 | 25.7816 | 10.1211 | 7.2742 | 3.1936 | 23.5811 | 12.6761 | 9.1106 | 9.3101 | 23.6079 | 12.5844 | 9.0447 | 8.7303 | 23.6568 | 12.5751 | 9.038 | 8.794 | 23.7151 | 12.3496 | 8.8759 | 8.0817 | 23.783 | 12.3242 | 8.8576 | 8.3071 | 23.8605 | 12.2718 | 8.82 | 7.8433 | 23.948 | 12.1852 | 8.7577 | 7.4127 | 24.0416 | 12.1267 | 8.7157 | 7.1712 | 24.1413 | 12.0009 | 8.6253 | 6.6216 | 24.2454 | 11.8434 | 8.5121 | 6.0759 | 24.5123 | 11.5507 | 8.3017 | 4.7646 | 24.7246 | 11.3185 | 8.1348 | 3.9476 | 24.8414 | 11.2902 | 8.1145 | 3.4154 | 24.9022 | 11.3613 | 8.1656 | 3.2605 | 23.5964 | 12.6688 | 9.1053 | 9.1923 | 23.6327 | 12.6027 | 9.0578 | 8.5222 | 23.6686 | 12.5746 | 9.0376 | 8.6334 | 23.7303 | 12.3901 | 8.905 | 7.8763 | 23.8116 | 12.3526 | 8.878 | 7.9804 | 23.9095 | 12.1408 | 8.7258 | 7.419 | 24.0236 | 12.0611 | 8.6685 | 6.8847 | 24.1492 | 11.9188 | 8.5663 | 6.5447 | 24.2851 | 11.7431 | 8.44 | 5.8982 | 24.4343 | 11.517 | 8.2775 | 5.2215 | 24.9948 | 11.1802 | 8.0354 | 3.5396 | 25.3531 | 10.8147 | 7.7727 | 3.0589 | 25.5584 | 10.7652 | 7.7372 | 3.1586 | 25.6781 | 10.3016 | 7.404 | 3.7197 | 23.5947 | 12.7178 | 9.1406 | 9.2088 | 23.6336 | 12.5655 | 9.0311 | 8.546 | 23.6815 | 12.6397 | 9.0844 | 8.6868 | 23.7656 | 12.4599 | 8.9552 | 7.9775 | 23.8811 | 12.3849 | 8.9013 | 8.1832 | 24.0276 | 12.3335 | 8.8643 | 7.7179 | 24.2093 | 12.202 | 8.7698 | 7.2881 | 24.4077 | 12.0798 | 8.682 | 7.0732 | 24.6255 | 11.945 | 8.5851 | 6.6193 | 24.8508 | 11.7929 | 8.4758 | 6.1837 | 25.5956 | 10.8701 | 7.8126 | 4.2298 | 26.2379 | 9.6683 | 6.9488 | 0.56345 | 26.5574 | 8.9764 | 6.4515 | -2.1843 | 26.7094 | 8.3292 | 5.9864 | -3.7664 | 23.597 | 12.7089 | 9.1342 | 9.1447 | 23.6481 | 12.6118 | 9.0643 | 8.3874 | 23.7002 | 12.6942 | 9.1236 | 8.5245 | 23.7806 | 12.5375 | 9.011 | 7.8461 | 23.8936 | 12.4971 | 8.9819 | 8.0528 | 24.0286 | 12.3317 | 8.863 | 7.6487 | 24.1857 | 12.1087 | 8.7028 | 7.2834 | 24.3576 | 12.1354 | 8.722 | 7.1553 | 24.5531 | 12.0104 | 8.6321 | 6.65 | 24.7978 | 11.6965 | 8.4065 | 5.5501 | 25.5412 | 10.5366 | 7.5728 | 1.1381 | 25.9477 | 9.3272 | 6.7037 | -1.9876 | 26.0347 | 8.7987 | 6.3238 | -3.716 | 25.9205 | 8.7218 | 6.2686 | -2.5591
CRAGGS ROW & BUSHELL ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353740 | 430080 | 31.903 | 12.5883 | 9.183 | 9.7266 | 31.9925 | 12.4363 | 9.0721 | 9.3896 | 32.0083 | 12.243 | 8.9311 | 9.1546 | 32.0584 | 12.226 | 8.9187 | 8.8259 | 32.1301 | 12.1496 | 8.863 | 8.5531 | 32.2242 | 12.0067 | 8.7587 | 8.236 | 32.3256 | 11.8415 | 8.6382 | 7.792 | 32.4309 | 11.6934 | 8.5302 | 7.3913 | 32.5419 | 11.5304 | 8.4112 | 7.0055 | 32.6646 | 11.3449 | 8.2759 | 6.4806 | 33.0952 | 10.5414 | 7.6898 | 4.7609 | 33.3704 | 10.1743 | 7.422 | 3.9149 | 33.5028 | 10.0833 | 7.3557 | 3.633 | 33.5371 | 10.014 | 7.3051 | 3.9664 | 31.8196 | 12.6673 | 9.2406 | 9.9784 | 31.8487 | 12.6006 | 9.1919 | 9.8474 | 31.9158 | 12.4897 | 9.111 | 9.5084 | 32.0043 | 12.4081 | 9.0515 | 9.1319 | 32.1068 | 12.3293 | 8.9941 | 8.8375 | 32.2209 | 12.2275 | 8.9198 | 8.509 | 32.3468 | 12.1135 | 8.8367 | 8.0418 | 32.4804 | 12.0056 | 8.7579 | 7.6074 | 32.6232 | 11.8829 | 8.6684 | 7.1395 | 32.7739 | 11.7515 | 8.5725 | 6.6085 | 33.0044 | 11.4013 | 8.3171 | 5.4609 | 33.1742 | 11.103 | 8.0995 | 4.5728 | 33.2625 | 10.8868 | 7.9418 | 3.9811 | 33.2838 | 10.8095 | 7.8854 | 3.8028 | 31.903 | 12.6657 | 9.2394 | 9.7387 | 31.9925 | 12.5592 | 9.1618 | 9.4209 | 32.0083 | 12.4878 | 9.1097 | 9.2071 | 32.0584 | 12.3611 | 9.0172 | 8.8975 | 32.1299 | 12.2243 | 8.9175 | 8.6452 | 32.2235 | 12.0856 | 8.8163 | 8.3485 | 32.3245 | 11.945 | 8.7137 | 7.9262 | 32.4296 | 11.7923 | 8.6023 | 7.5461 | 32.5393 | 11.6252 | 8.4804 | 7.1882 | 32.6567 | 11.445 | 8.349 | 6.7196 | 33.0634 | 10.9216 | 7.9672 | 5.1768 | 33.3187 | 10.4094 | 7.5935 | 4.4531 | 33.4408 | 10.4896 | 7.652 | 4.2253 | 33.472 | 10.2971 | 7.5116 | 4.5515 | 31.8951 | 12.5885 | 9.1831 | 9.7407 | 31.9793 | 12.4278 | 9.0659 | 9.4188 | 31.9948 | 12.2424 | 8.9306 | 9.2048 | 32.0511 | 12.2225 | 8.9161 | 8.8959 | 32.1368 | 12.129 | 8.848 | 8.6501 | 32.2552 | 11.9726 | 8.7338 | 8.3581 | 32.3951 | 11.7924 | 8.6024 | 7.9093 | 32.5482 | 11.6416 | 8.4924 | 7.5079 | 32.7117 | 11.4713 | 8.3682 | 7.1741 | 32.8891 | 11.2652 | 8.2178 | 6.7766 | 33.4713 | 10.2233 | 7.4578 | 4.6302 | 34.0614 | 9.3072 | 6.7895 | 0.41136 | 34.3172 | 8.4362 | 6.1541 | -2.758 | 34.3518 | 7.9879 | 5.827 | -4.5825 | 31.8827 | 12.5919 | 9.1857 | 9.7523 | 31.9608 | 12.4552 | 9.0859 | 9.4204 | 31.9682 | 12.2843 | 8.9612 | 9.2246 | 32.0143 | 12.2411 | 8.9297 | 8.9561 | 32.0913 | 12.1426 | 8.8579 | 8.7292 | 32.1928 | 11.9779 | 8.7377 | 8.4835 | 32.3136 | 11.7885 | 8.5995 | 8.1048 | 32.4417 | 11.624 | 8.4795 | 7.786 | 32.5874 | 11.4414 | 8.3464 | 7.4457 | 32.8012 | 11.0573 | 8.0661 | 6.3428 | 33.5428 | 9.5655 | 6.9779 | 1.3758 | 33.8329 | 8.5366 | 6.2274 | -2.3617 | 33.8353 | 7.8896 | 5.7554 | -4.4112 | 33.6523 | 8.0095 | 5.8428 | -3.3323
CROWN LANE | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 32.6581 | 8.8489 | 6.3599 | 8.0579 | 32.7673 | 8.2562 | 5.9339 | 6.9472 | 32.8292 | 7.5282 | 5.4107 | 6.8502 | 32.9345 | 7.6481 | 5.4969 | 6.2339 | 33.0727 | 7.4498 | 5.3543 | 5.8246 | 33.2467 | 7.1528 | 5.1409 | 5.1954 | 33.4493 | 6.9814 | 5.0177 | 4.5511 | 33.6726 | 6.7681 | 4.8644 | 3.7666 | 33.9103 | 6.4727 | 4.6521 | 2.9649 | 34.1815 | 6.3177 | 4.5407 | 2.2325 | 31.0231 | 5.1077 | 3.671 | -1.253 | 37.1801 | 7.209 | 5.1813 | -3.7415 | 38.3622 | 10.8255 | 7.7805 | -4.9393 | 39.4342 | 11.2777 | 8.1055 | -4.9284 | 32.6205 | 8.8531 | 6.3629 | 8.4224 | 32.6967 | 8.573 | 6.1616 | 7.6492 | 32.8183 | 8.3481 | 5.9999 | 7.5086 | 32.9633 | 7.8885 | 5.6696 | 6.9549 | 33.1295 | 7.1245 | 5.1205 | 6.6358 | 33.3208 | 7.0644 | 5.0773 | 6.1077 | 33.5402 | 6.9985 | 5.0299 | 5.578 | 33.7822 | 6.8575 | 4.9286 | 4.9085 | 34.047 | 6.7529 | 4.8534 | 4.1622 | 34.3329 | 6.6604 | 4.7869 | 3.651 | 35.1425 | 6.4931 | 4.6667 | 1.7332 | 35.9859 | 7.6297 | 5.4836 | 0.39256 | 36.7207 | 9.9087 | 7.1215 | -0.76376 | 37.3121 | 10.9907 | 7.8992 | -1.2832 | 32.6624 | 8.8444 | 6.3567 | 8.067 | 32.7735 | 8.619 | 6.1947 | 6.9705 | 32.8356 | 8.3315 | 5.988 | 6.8799 | 32.9422 | 7.7301 | 5.5558 | 6.2763 | 33.0812 | 7.3394 | 5.275 | 5.8792 | 33.2539 | 7.1598 | 5.1459 | 5.2791 | 33.4538 | 7.0361 | 5.057 | 4.659 | 33.6732 | 6.8424 | 4.9178 | 3.8929 | 33.9037 | 6.6471 | 4.7774 | 3.1204 | 34.1583 | 6.4503 | 4.636 | 2.4474 | 35.3954 | 6.1664 | 4.4319 | -0.61083 | 36.5105 | 7.9828 | 5.7374 | -2.3863 | 37.3791 | 12.141 | 8.726 | -3.2607 | 38.0398 | 12.6229 | 9.0724 | -2.9728 | 32.6589 | 8.8514 | 6.3617 | 8.076 | 32.7697 | 8.2373 | 5.9203 | 6.9708 | 32.8429 | 7.7406 | 5.5633 | 6.8915 | 32.9714 | 7.6712 | 5.5134 | 6.3329 | 33.1483 | 7.4733 | 5.3712 | 5.9837 | 33.3961 | 7.1312 | 5.1253 | 5.414 | 33.7118 | 6.9342 | 4.9837 | 4.8029 | 34.0832 | 6.7437 | 4.8468 | 4.0362 | 34.4997 | 6.4644 | 4.6461 | 3.3183 | 34.9689 | 6.235 | 4.4812 | 2.8404 | 30.5523 | 5.0302 | 3.6153 | -2.0775 | 34.295 | 5.6464 | 4.0582 | -9.7801 | 41.4038 | 8.3382 | 5.9928 | -15.3184 | 41.8859 | 8.1757 | 5.876 | -18.6067 | 32.6526 | 8.8509 | 6.3613 | 8.0617 | 32.7718 | 8.4683 | 6.0863 | 6.907 | 32.8501 | 8.5657 | 6.1563 | 6.826 | 32.9772 | 8.5957 | 6.1779 | 6.2815 | 33.1535 | 8.5011 | 6.1099 | 5.953 | 33.4145 | 8.195 | 5.8899 | 5.4348 | 33.7684 | 7.8683 | 5.6551 | 4.8867 | 34.186 | 7.5649 | 5.437 | 4.2175 | 34.6639 | 7.4195 | 5.3326 | 3.5086 | 35.2501 | 7.539 | 5.4185 | 2.1143 | 37.8765 | 11.7353 | 8.4344 | -6.4725 | 40.0026 | 9.9242 | 7.1327 | -12.7979 | 40.9406 | 8.8189 | 6.3384 | -16.3759 | 41.0311 | 8.7345 | 6.2777 | -15.3481
CULCHETH | GOLBORNE | BOLD | 365430 | 395366 | 20.2161 | 20.2161 | 20.2161 | 9.2018 | 20.263 | 20.263 | 20.263 | 8.8897 | 20.2808 | 20.2808 | 20.2808 | 8.752 | 20.3161 | 20.3161 | 20.3161 | 8.5189 | 20.3626 | 20.3626 | 20.3626 | 8.3445 | 20.4221 | 20.4221 | 20.4221 | 8.035 | 20.4884 | 20.4884 | 20.4884 | 7.7526 | 20.559 | 20.559 | 20.559 | 7.5586 | 20.6305 | 20.6305 | 20.6305 | 7.2556 | 20.7172 | 20.7172 | 20.7172 | 6.8329 | 21.1176 | 21.1176 | 20.7302 | 5.598 | 21.4819 | 21.4819 | 20.1912 | 4.8899 | 21.7207 | 21.7207 | 20.3279 | 4.7397 | 21.9165 | 21.9165 | 20.1346 | 4.9422 | 20.1755 | 20.1755 | 20.1755 | 9.3196 | 20.193 | 20.193 | 20.193 | 9.1129 | 20.2287 | 20.2287 | 20.2287 | 8.955 | 20.2684 | 20.2684 | 20.2684 | 8.7693 | 20.3149 | 20.3149 | 20.3149 | 8.6494 | 20.367 | 20.367 | 20.367 | 8.4036 | 20.4251 | 20.4251 | 20.4251 | 8.1836 | 20.4865 | 20.4865 | 20.4865 | 8.0467 | 20.5516 | 20.5516 | 20.5516 | 7.771 | 20.6193 | 20.6193 | 20.6193 | 7.4736 | 20.8058 | 20.8058 | 20.8058 | 6.8462 | 20.986 | 20.986 | 20.986 | 6.2988 | 21.1423 | 21.1423 | 21.1423 | 5.9522 | 21.2607 | 21.2607 | 20.8098 | 5.7462 | 20.2161 | 20.2161 | 20.2161 | 9.2052 | 20.2632 | 20.2632 | 20.2632 | 8.9058 | 20.2812 | 20.2812 | 20.2812 | 8.7809 | 20.3167 | 20.3167 | 20.3167 | 8.5601 | 20.3633 | 20.3633 | 20.3633 | 8.3979 | 20.4227 | 20.4227 | 20.4227 | 8.1017 | 20.489 | 20.489 | 20.489 | 7.8315 | 20.5597 | 20.5597 | 20.5597 | 7.6478 | 20.6305 | 20.6305 | 20.6305 | 7.3609 | 20.7136 | 20.7136 | 20.7136 | 6.9715 | 21.0782 | 21.0782 | 21.0255 | 5.8561 | 21.3608 | 21.3608 | 20.9628 | 5.2527 | 21.5582 | 21.5582 | 20.8879 | 5.1451 | 21.6857 | 21.6857 | 20.6866 | 5.3762 | 20.2121 | 20.2121 | 20.2121 | 9.2138 | 20.2592 | 20.2592 | 20.2592 | 8.9005 | 20.2812 | 20.2812 | 20.2812 | 8.7636 | 20.324 | 20.324 | 20.324 | 8.5414 | 20.3876 | 20.3876 | 20.3876 | 8.3692 | 20.4762 | 20.4762 | 20.4762 | 8.0449 | 20.5862 | 20.5862 | 20.5862 | 7.7208 | 20.7124 | 20.7124 | 20.7124 | 7.4726 | 20.8457 | 20.8457 | 20.8457 | 7.1539 | 20.9948 | 20.9948 | 20.9102 | 6.8011 | 21.6127 | 21.6127 | 20.5428 | 5.6614 | 22.2416 | 22.2416 | 20.0116 | 3.7122 | 22.5781 | 22.5781 | 19.6352 | 2.5868 | 22.7304 | 22.7304 | 19.2563 | 1.4876 | 20.2103 | 20.2103 | 20.2103 | 9.2047 | 20.2606 | 20.2606 | 20.2606 | 8.8692 | 20.2842 | 20.2842 | 20.2842 | 8.7336 | 20.3308 | 20.3308 | 20.3308 | 8.5193 | 20.3933 | 20.3933 | 20.3933 | 8.3625 | 20.4794 | 20.4794 | 20.4794 | 8.0749 | 20.5887 | 20.5887 | 20.5887 | 7.8039 | 20.7112 | 20.7112 | 20.7112 | 7.63 | 20.8392 | 20.8392 | 20.8392 | 7.3985 | 21.0079 | 21.0079 | 20.8872 | 6.877 | 21.7008 | 21.7008 | 20.3448 | 4.7699 | 22.1694 | 22.1694 | 20.0693 | 3.2823 | 22.3077 | 22.3077 | 19.7925 | 2.5868 | 22.2696 | 22.2696 | 19.571 | 2.8082
CUTACRE | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 26.3837 | 15.5665 | 11.188 | 23.3601 | 26.4154 | 15.3112 | 11.0045 | 23.0522 | 26.4114 | 15.1191 | 10.8664 | 22.9649 | 26.4122 | 15.0148 | 10.7914 | 22.9519 | 26.4175 | 14.8826 | 10.6964 | 22.9387 | 26.4285 | 14.6512 | 10.5301 | 22.9215 | 26.4402 | 14.519 | 10.4351 | 22.8717 | 26.452 | 14.3434 | 10.3089 | 22.8592 | 26.4637 | 14.2621 | 10.2504 | 22.8499 | 26.4757 | 14.456 | 10.3898 | 22.8201 | 26.6218 | 14.8555 | 10.677 | 22.6629 | 26.8724 | 14.3014 | 10.2787 | 22.3948 | 26.9972 | 14.8964 | 10.7063 | 22.2014 | 27.137 | 14.6024 | 10.495 | 21.9641 | 26.3488 | 15.7315 | 11.3065 | 23.5884 | 26.3509 | 15.567 | 11.1883 | 23.4895 | 26.3561 | 15.4036 | 11.0709 | 23.4216 | 26.365 | 15.2407 | 10.9538 | 23.3856 | 26.3751 | 15.0758 | 10.8353 | 23.3567 | 26.3862 | 14.908 | 10.7147 | 23.3338 | 26.3984 | 14.8918 | 10.703 | 23.2796 | 26.4109 | 14.8696 | 10.687 | 23.2571 | 26.4235 | 14.835 | 10.6622 | 23.2357 | 26.4357 | 14.7846 | 10.626 | 23.1952 | 26.5425 | 14.3687 | 10.3271 | 23.0695 | 26.6912 | 14.78 | 10.6227 | 22.8907 | 26.846 | 15.0332 | 10.8046 | 22.728 | 26.9412 | 14.9741 | 10.7622 | 22.609 | 26.3838 | 15.732 | 11.3069 | 23.3605 | 26.4157 | 15.558 | 11.1818 | 23.0527 | 26.4121 | 15.3128 | 11.0056 | 22.9655 | 26.4134 | 15.0074 | 10.7861 | 22.9526 | 26.4193 | 14.6537 | 10.5319 | 22.9395 | 26.4309 | 14.5569 | 10.4623 | 22.9234 | 26.443 | 14.6722 | 10.5452 | 22.874 | 26.4553 | 14.7508 | 10.6017 | 22.8618 | 26.4674 | 14.844 | 10.6687 | 22.853 | 26.4789 | 14.9102 | 10.7162 | 22.8249 | 26.5886 | 15.0893 | 10.845 | 22.7061 | 26.7324 | 14.8181 | 10.6501 | 22.5691 | 26.8421 | 15.1148 | 10.8633 | 22.4396 | 26.9063 | 15.0171 | 10.7931 | 22.3262 | 26.3808 | 15.561 | 11.184 | 23.3687 | 26.4097 | 15.3226 | 11.0127 | 23.0695 | 26.4052 | 15.13 | 10.8742 | 22.9906 | 26.4054 | 15.0395 | 10.8092 | 22.9862 | 26.4105 | 14.8362 | 10.6631 | 22.982 | 26.427 | 14.526 | 10.4401 | 22.9706 | 26.4496 | 14.261 | 10.2497 | 22.9223 | 26.4775 | 14.4178 | 10.3624 | 22.9055 | 26.5101 | 14.6153 | 10.5043 | 22.888 | 26.5411 | 14.7513 | 10.6021 | 22.8495 | 26.7804 | 14.8773 | 10.6926 | 22.5068 | 27.0515 | 14.7933 | 10.6322 | 22.0694 | 27.1974 | 14.4611 | 10.3935 | 21.8363 | 27.2218 | 14.2206 | 10.2207 | 21.7999 | 26.3879 | 15.5585 | 11.1822 | 23.3618 | 26.4205 | 15.249 | 10.9598 | 23.0558 | 26.417 | 15.1998 | 10.9244 | 22.974 | 26.4215 | 14.9029 | 10.711 | 22.9671 | 26.4317 | 14.466 | 10.397 | 22.9597 | 26.4597 | 14.6222 | 10.5093 | 22.9405 | 26.5006 | 14.7012 | 10.566 | 22.8785 | 26.5475 | 14.8274 | 10.6567 | 22.8395 | 26.5863 | 14.8878 | 10.7001 | 22.798 | 26.6321 | 14.9256 | 10.7274 | 22.7309 | 26.9227 | 14.9898 | 10.7734 | 22.3097 | 27.1626 | 14.7113 | 10.5733 | 21.9203 | 27.2396 | 14.5936 | 10.4887 | 21.8087 | 27.2072 | 14.4726 | 10.4017 | 21.8681
ASKAM & DALTON | ULVERSTON | HARKER / HUTTON | 323582 | 474255 | 31.4059 | 9.7311 | 6.9939 | 8.9708 | 31.4834 | 9.6121 | 6.9084 | 8.5149 | 31.5737 | 9.521 | 6.843 | 8.3699 | 31.7212 | 9.3314 | 6.7066 | 7.8969 | 31.8844 | 9.1837 | 6.6005 | 7.655 | 32.0705 | 8.9385 | 6.4243 | 7.1204 | 32.2828 | 8.6874 | 6.2438 | 6.5304 | 32.5146 | 8.4696 | 6.0872 | 6.0948 | 32.7562 | 8.2288 | 5.9142 | 5.542 | 33.1316 | 7.9167 | 5.6899 | 4.6427 | 34.4849 | 6.778 | 4.8715 | 1.7411 | 35.0845 | 6.0134 | 4.322 | 0.24807 | 35.3692 | 5.8504 | 4.2048 | -0.17445 | 33.9418 | 5.5883 | 4.0164 | 0.55466 | 31.3978 | 9.7668 | 7.0196 | 9.1271 | 31.4637 | 9.6901 | 6.9644 | 8.8372 | 31.5682 | 9.603 | 6.9018 | 8.6051 | 31.6514 | 9.4681 | 6.8049 | 8.2396 | 31.7526 | 9.3782 | 6.7403 | 8.0985 | 31.8729 | 9.2187 | 6.6257 | 7.6648 | 32.0112 | 9.0546 | 6.5077 | 7.1719 | 32.1617 | 8.9233 | 6.4133 | 6.823 | 32.3243 | 8.7691 | 6.3025 | 6.3329 | 32.4955 | 8.5981 | 6.1796 | 5.7495 | 32.9783 | 8.1362 | 5.8476 | 4.4054 | 33.5962 | 7.6251 | 5.4803 | 3.0248 | 34.0494 | 7.4143 | 5.3288 | 2.0107 | 34.103 | 7.3168 | 5.2587 | 1.4885 | 31.4059 | 9.7705 | 7.0222 | 8.9805 | 31.4834 | 9.6885 | 6.9633 | 8.5626 | 31.5738 | 9.5735 | 6.8807 | 8.4248 | 31.7213 | 9.3919 | 6.7502 | 7.9855 | 31.884 | 9.2525 | 6.6499 | 7.7716 | 32.0693 | 9.0032 | 6.4708 | 7.2685 | 32.2809 | 8.7503 | 6.289 | 6.7101 | 32.512 | 8.5269 | 6.1285 | 6.3022 | 32.7509 | 8.2734 | 5.9462 | 5.7845 | 33.1146 | 7.9981 | 5.7484 | 4.9786 | 34.4314 | 7.2255 | 5.1931 | 2.3819 | 34.9881 | 6.4532 | 4.638 | 1.0604 | 35.2525 | 6.0664 | 4.36 | 0.70255 | 33.5478 | 5.5234 | 3.9698 | 1.4662 | 31.4057 | 9.7288 | 6.9923 | 8.9722 | 31.5168 | 9.5874 | 6.8906 | 8.4653 | 31.6643 | 9.4604 | 6.7994 | 8.266 | 31.8778 | 9.2429 | 6.6431 | 7.7591 | 32.1587 | 9.0561 | 6.5088 | 7.4369 | 32.517 | 8.7584 | 6.2948 | 6.7788 | 32.9717 | 8.4363 | 6.0633 | 5.9989 | 33.4795 | 8.1427 | 5.8523 | 5.3653 | 33.7521 | 7.8461 | 5.6391 | 4.7263 | 34.0495 | 7.5236 | 5.4074 | 3.9812 | 35.2375 | 6.0253 | 4.3305 | 0.59159 | 24.3492 | 4.0089 | 2.8813 | -5.7062 | 17.0142 | 2.8013 | 2.0133 | -9.8485 | 9.93 | 1.6349 | 1.175 | -12.6775 | 31.3836 | 9.7402 | 7.0005 | 9.0206 | 31.4901 | 9.6096 | 6.9066 | 8.5152 | 31.6412 | 9.4715 | 6.8073 | 8.3384 | 31.8644 | 9.2402 | 6.6411 | 7.8683 | 32.1656 | 9.0368 | 6.4949 | 7.5607 | 32.5874 | 8.7253 | 6.2711 | 6.9058 | 33.0113 | 8.4196 | 6.0514 | 6.2511 | 33.4573 | 8.1561 | 5.862 | 5.7773 | 33.7145 | 7.8739 | 5.6591 | 5.2051 | 34.1845 | 7.351 | 5.2833 | 3.5109 | 32.6613 | 5.3774 | 3.8649 | -3.8976 | 20.917 | 3.4438 | 2.4751 | -9.1847 | 14.5593 | 2.3971 | 1.7228 | -11.749 | 12.9638 | 2.1344 | 1.534 | -10.2984
DEANSGATE | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 30.6014 | 11.7576 | 8.577 | 12.0041 | 30.6919 | 11.6317 | 8.4852 | 11.3919 | 30.6851 | 11.6006 | 8.4624 | 11.4365 | 30.699 | 11.5304 | 8.4112 | 11.3749 | 30.7235 | 11.4432 | 8.3476 | 11.2644 | 30.7612 | 11.3799 | 8.3015 | 11.0384 | 30.7967 | 11.3061 | 8.2476 | 10.8824 | 30.8293 | 11.2467 | 8.2043 | 10.7543 | 30.8592 | 11.1311 | 8.12 | 10.5703 | 30.8866 | 10.963 | 7.9974 | 10.4713 | 30.9477 | 10.7177 | 7.8184 | 10.0934 | 30.9628 | 10.5356 | 7.6856 | 9.9837 | 30.9442 | 10.5025 | 7.6614 | 10.0358 | 30.9013 | 10.5345 | 7.6848 | 10.188 | 30.5054 | 11.8912 | 8.6745 | 12.562 | 30.5173 | 11.8139 | 8.6181 | 12.4222 | 30.5556 | 11.7878 | 8.5991 | 12.2799 | 30.6064 | 11.7132 | 8.5446 | 12.0503 | 30.6631 | 11.6105 | 8.4697 | 11.8054 | 30.7232 | 11.5402 | 8.4184 | 11.4972 | 30.7878 | 11.458 | 8.3584 | 11.2293 | 30.8547 | 11.3953 | 8.3127 | 10.9691 | 30.9249 | 11.3181 | 8.2564 | 10.6301 | 30.9986 | 11.2503 | 8.2069 | 10.3601 | 31.0831 | 11.0973 | 8.0953 | 9.8883 | 31.1348 | 11.0253 | 8.0428 | 9.621 | 31.1425 | 11.0822 | 8.0843 | 9.56 | 31.1083 | 11.1896 | 8.1626 | 9.669 | 30.6014 | 11.89 | 8.6736 | 12.0132 | 30.6919 | 11.8089 | 8.6144 | 11.4108 | 30.6851 | 11.7637 | 8.5815 | 11.4645 | 30.699 | 11.6722 | 8.5147 | 11.4131 | 30.7235 | 11.5609 | 8.4335 | 11.3134 | 30.7612 | 11.4746 | 8.3706 | 11.0995 | 30.7966 | 11.3797 | 8.3013 | 10.9553 | 30.8292 | 11.2821 | 8.2301 | 10.8393 | 30.859 | 11.1341 | 8.1222 | 10.6695 | 30.8861 | 11.0491 | 8.0602 | 10.5856 | 30.946 | 10.8835 | 7.9394 | 10.2153 | 30.9603 | 10.793 | 7.8733 | 10.1099 | 30.9414 | 10.8265 | 7.8978 | 10.1632 | 30.8985 | 10.7847 | 7.8673 | 10.3154 | 30.5935 | 11.7616 | 8.5799 | 12.0384 | 30.6769 | 11.6307 | 8.4844 | 11.4627 | 30.6641 | 11.4961 | 8.3863 | 11.5424 | 30.6722 | 11.4797 | 8.3743 | 11.517 | 30.692 | 11.477 | 8.3723 | 11.4406 | 30.7272 | 11.4231 | 8.333 | 11.2525 | 30.761 | 11.3628 | 8.289 | 11.1342 | 30.7925 | 11.2796 | 8.2283 | 11.044 | 30.8208 | 11.1427 | 8.1284 | 10.8998 | 30.846 | 11.0357 | 8.0504 | 10.8474 | 30.8711 | 10.8372 | 7.9056 | 10.6023 | 30.866 | 10.5331 | 7.6837 | 10.0852 | 30.8087 | 10.3951 | 7.5831 | 9.7652 | 30.7236 | 10.3499 | 7.5501 | 9.6809 | 30.5894 | 11.7627 | 8.5807 | 12.0493 | 30.6687 | 11.6286 | 8.4829 | 11.4836 | 30.6509 | 11.6236 | 8.4793 | 11.5781 | 30.653 | 11.5701 | 8.4402 | 11.5702 | 30.6664 | 11.4654 | 8.3639 | 11.5132 | 30.6945 | 11.2999 | 8.2431 | 11.3476 | 30.7211 | 11.1629 | 8.1432 | 11.2523 | 30.7447 | 11.1469 | 8.1315 | 11.1877 | 30.7633 | 11.0662 | 8.0727 | 11.0739 | 30.7856 | 10.9514 | 7.9889 | 10.9034 | 30.8354 | 10.3886 | 7.5783 | 10.0834 | 30.8191 | 9.8275 | 7.169 | 9.5807 | 30.7499 | 9.8257 | 7.1677 | 9.413 | 30.6328 | 9.8378 | 7.1765 | 9.9013
DENTON EAST | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 24.2376 | 15.5168 | 11.3193 | 8.6308 | 24.2932 | 15.1969 | 11.086 | 8.2496 | 24.3324 | 15.2325 | 11.1119 | 8.1276 | 24.3953 | 15.1581 | 11.0576 | 7.8031 | 24.4803 | 15.0152 | 10.9534 | 7.5093 | 24.5845 | 14.8209 | 10.8117 | 7.1393 | 24.7038 | 14.6907 | 10.7166 | 6.6926 | 24.8348 | 14.539 | 10.606 | 6.2467 | 24.9703 | 14.4118 | 10.5132 | 5.7703 | 25.1067 | 14.2833 | 10.4194 | 5.2062 | 25.6431 | 13.5666 | 9.8967 | 3.3064 | 26.0296 | 12.9175 | 9.4231 | 2.3384 | 26.2597 | 13.2191 | 9.6432 | 2.1016 | 26.3981 | 13.0277 | 9.5035 | 2.3046 | 24.222 | 15.5453 | 11.3401 | 8.7145 | 24.2701 | 15.4515 | 11.2716 | 8.3851 | 24.3443 | 15.2971 | 11.159 | 8.1836 | 24.4291 | 15.1188 | 11.029 | 7.8537 | 24.5268 | 14.9105 | 10.877 | 7.6201 | 24.6375 | 14.6541 | 10.69 | 7.254 | 24.7449 | 14.5435 | 10.6093 | 6.8413 | 24.8551 | 14.4384 | 10.5326 | 6.4307 | 24.9737 | 14.3206 | 10.4467 | 5.9872 | 25.099 | 14.1962 | 10.3559 | 5.5179 | 25.3481 | 13.8817 | 10.1265 | 4.2186 | 25.547 | 13.4991 | 9.8474 | 3.2361 | 25.6765 | 13.679 | 9.9786 | 2.6644 | 25.7608 | 13.8726 | 10.1199 | 2.339 | 24.2376 | 15.5444 | 11.3394 | 8.6581 | 24.2932 | 15.4428 | 11.2653 | 8.3123 | 24.3324 | 15.2853 | 11.1504 | 8.1697 | 24.3953 | 15.034 | 10.9671 | 7.8551 | 24.48 | 14.7643 | 10.7703 | 7.6234 | 24.5835 | 14.5314 | 10.6004 | 7.2748 | 24.7022 | 14.4246 | 10.5225 | 6.832 | 24.8328 | 14.2928 | 10.4264 | 6.3999 | 24.967 | 14.1406 | 10.3154 | 5.9512 | 25.0971 | 13.9685 | 10.1898 | 5.4451 | 25.603 | 13.5305 | 9.8703 | 3.7178 | 25.9637 | 13.1124 | 9.5653 | 2.8692 | 26.18 | 13.3274 | 9.7221 | 2.7053 | 26.3137 | 13.085 | 9.5453 | 2.9001 | 24.2346 | 15.5122 | 11.3159 | 8.635 | 24.2912 | 15.2301 | 11.1101 | 8.2522 | 24.3413 | 15.25 | 11.1247 | 8.1301 | 24.4252 | 15.1439 | 11.0473 | 7.7978 | 24.5442 | 14.9757 | 10.9246 | 7.5354 | 24.6962 | 14.7573 | 10.7652 | 7.1696 | 24.8814 | 14.5585 | 10.6202 | 6.7076 | 25.0792 | 14.4466 | 10.5386 | 6.262 | 25.2808 | 14.3045 | 10.4349 | 5.8445 | 25.5047 | 14.136 | 10.312 | 5.4081 | 26.3459 | 12.9811 | 9.4695 | 2.7004 | 27.1268 | 11.4327 | 8.34 | -3.2318 | 27.5121 | 10.5679 | 7.7091 | -7.9492 | 27.7446 | 9.709 | 7.0826 | -11.2144 | 24.2204 | 15.5189 | 11.3208 | 8.6647 | 24.2734 | 15.3021 | 11.1627 | 8.2864 | 24.321 | 15.4107 | 11.2419 | 8.1718 | 24.3939 | 15.4226 | 11.2505 | 7.8946 | 24.5009 | 15.3764 | 11.2169 | 7.6386 | 24.6328 | 15.2473 | 11.1227 | 7.334 | 24.7988 | 15.0769 | 10.9984 | 6.9374 | 24.983 | 14.9922 | 10.9366 | 6.5734 | 25.1828 | 14.8426 | 10.8274 | 6.0697 | 25.4681 | 14.497 | 10.5754 | 4.6225 | 26.3699 | 12.7319 | 9.2878 | -2.0504 | 26.9009 | 11.2791 | 8.2279 | -7.4035 | 27.0827 | 10.5336 | 7.6841 | -10.5499 | 27.0015 | 10.3839 | 7.5749 | -9.7019
DENTON WEST | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 31.5908 | 11.4546 | 8.3559 | 13.8809 | 31.6539 | 11.2218 | 8.1862 | 13.6726 | 31.6805 | 10.967 | 8.0003 | 13.4765 | 31.7434 | 10.6015 | 7.7336 | 13.1618 | 31.8298 | 10.3387 | 7.5419 | 12.898 | 31.9321 | 10.2472 | 7.4752 | 12.456 | 32.3385 | 10.1003 | 7.368 | 11.7103 | 32.4508 | 9.9937 | 7.2903 | 11.2744 | 32.5732 | 9.8553 | 7.1893 | 10.8194 | 32.7116 | 9.6535 | 7.0421 | 10.2575 | 33.3195 | 9.2597 | 6.7548 | 8.3933 | 33.8801 | 8.9172 | 6.505 | 7.3273 | 34.2528 | 9.1603 | 6.6823 | 7.0453 | 34.5785 | 9.032 | 6.5887 | 7.0708 | 31.5449 | 11.4758 | 8.3715 | 13.983 | 31.5728 | 11.2867 | 8.2335 | 13.8528 | 31.6328 | 11.1114 | 8.1056 | 13.5948 | 31.7115 | 10.9364 | 7.9779 | 13.2863 | 31.8036 | 10.8948 | 7.9476 | 13.0437 | 31.9052 | 10.728 | 7.8259 | 12.6663 | 32.015 | 10.643 | 7.7639 | 12.2593 | 32.1328 | 10.5618 | 7.7047 | 11.8567 | 32.2587 | 10.4759 | 7.642 | 11.4324 | 32.3916 | 10.3716 | 7.5659 | 10.9644 | 32.7088 | 10.0385 | 7.3229 | 9.5559 | 32.9862 | 9.7404 | 7.1055 | 8.5185 | 33.2118 | 9.8805 | 7.2077 | 7.9338 | 33.3818 | 9.9454 | 7.2551 | 7.5582 | 31.5909 | 11.4686 | 8.3662 | 13.8882 | 31.6541 | 11.3017 | 8.2445 | 13.6774 | 31.6809 | 11.0107 | 8.0322 | 13.4768 | 31.744 | 10.9994 | 8.0239 | 13.167 | 31.8304 | 10.8913 | 7.945 | 12.9167 | 31.9325 | 10.7004 | 7.8058 | 12.4869 | 32.3386 | 10.5855 | 7.7219 | 11.7515 | 32.4508 | 10.4633 | 7.6328 | 11.328 | 32.5717 | 10.3056 | 7.5178 | 10.8915 | 32.7031 | 10.1999 | 7.4407 | 10.3758 | 33.257 | 9.7258 | 7.0948 | 8.6486 | 33.7139 | 9.4113 | 6.8654 | 7.7153 | 34.0329 | 9.7521 | 7.114 | 7.4753 | 34.3015 | 9.379 | 6.8419 | 7.5237 | 31.5857 | 11.4542 | 8.3557 | 13.8938 | 31.6476 | 11.2129 | 8.1797 | 13.7 | 31.6847 | 10.9357 | 7.9774 | 13.5293 | 31.7652 | 10.5415 | 7.6899 | 13.2404 | 31.8742 | 10.3736 | 7.5674 | 13.0281 | 32.0212 | 10.249 | 7.4765 | 12.6448 | 32.468 | 10.0915 | 7.3616 | 11.9624 | 32.6563 | 9.9421 | 7.2526 | 11.5848 | 32.8693 | 9.7389 | 7.1044 | 11.2368 | 33.1134 | 9.5509 | 6.9672 | 10.8427 | 34.07 | 8.9797 | 6.5506 | 8.3962 | 34.9915 | 7.7467 | 5.6511 | 3.667 | 35.5231 | 7.2201 | 5.267 | 0.13274 | 35.8169 | 6.5851 | 4.8037 | -2.0645 | 31.5762 | 11.4614 | 8.3609 | 13.9212 | 31.6406 | 11.3694 | 8.2938 | 13.717 | 31.6823 | 11.2275 | 8.1903 | 13.5296 | 31.7508 | 10.9866 | 8.0145 | 13.2612 | 31.8539 | 10.791 | 7.8719 | 13.0859 | 31.9914 | 10.8089 | 7.885 | 12.7521 | 32.4336 | 10.6643 | 7.7795 | 12.1278 | 32.6123 | 10.5336 | 7.6841 | 11.8236 | 32.8222 | 10.2872 | 7.5044 | 11.3951 | 33.097 | 10.0803 | 7.3534 | 10.2225 | 34.1193 | 8.9695 | 6.5432 | 4.7895 | 34.8298 | 7.7443 | 5.6494 | 0.5182 | 35.1085 | 7.073 | 5.1596 | -1.7092 | 35.0228 | 7.0669 | 5.1552 | -0.74554
DICKINSON ST | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 39.0887 | 10.0036 | 7.2975 | 3.8052 | 39.2675 | 9.8535 | 7.188 | 3.2416 | 39.2292 | 9.8216 | 7.1647 | 3.3726 | 39.2496 | 9.7434 | 7.1077 | 3.273 | 39.2941 | 9.6495 | 7.0392 | 3.0843 | 39.3671 | 9.5142 | 6.9404 | 2.751 | 39.4345 | 9.392 | 6.8514 | 2.261 | 39.4952 | 9.3777 | 6.8409 | 2.2468 | 39.5503 | 9.3112 | 6.7924 | 2.0559 | 39.6034 | 9.2134 | 6.721 | 1.8192 | 39.7693 | 8.7709 | 6.3983 | 0.92425 | 39.835 | 8.6033 | 6.276 | 0.78078 | 39.8206 | 8.4521 | 6.1657 | 0.79964 | 39.7349 | 8.6038 | 6.2764 | 1.0336 | 38.8648 | 10.2173 | 7.4534 | 4.7114 | 38.856 | 10.1736 | 7.4215 | 4.9036 | 38.9016 | 10.1096 | 7.3748 | 4.7547 | 38.9842 | 10.0186 | 7.3084 | 4.4421 | 39.0758 | 9.9041 | 7.2249 | 4.1035 | 39.1708 | 9.772 | 7.1286 | 3.7131 | 39.2705 | 9.6858 | 7.0657 | 3.1359 | 39.3696 | 9.6542 | 7.0426 | 3.0013 | 39.4694 | 9.5803 | 6.9887 | 2.6744 | 39.5696 | 9.4919 | 6.9242 | 2.3005 | 39.7752 | 9.299 | 6.7835 | 1.2869 | 39.9179 | 9.1176 | 6.6512 | 0.87653 | 39.9618 | 9.2152 | 6.7224 | 0.68844 | 39.9096 | 9.3101 | 6.7916 | 0.79634 | 39.0887 | 10.217 | 7.4531 | 3.8119 | 39.2675 | 10.1694 | 7.4185 | 3.2576 | 39.2292 | 10.1235 | 7.3849 | 3.399 | 39.2496 | 10.0128 | 7.3042 | 3.3074 | 39.294 | 9.8974 | 7.22 | 3.1268 | 39.3669 | 9.7802 | 7.1345 | 2.8019 | 39.4343 | 9.6559 | 7.0438 | 2.3215 | 39.495 | 9.6002 | 7.0032 | 2.3145 | 39.5499 | 9.5116 | 6.9386 | 2.1333 | 39.6022 | 9.4008 | 6.8577 | 1.9115 | 39.765 | 9.073 | 6.6186 | 1.0441 | 39.8283 | 8.9491 | 6.5283 | 0.91774 | 39.8128 | 8.9792 | 6.5502 | 0.94482 | 39.7267 | 8.96 | 6.5362 | 1.1795 | 39.0695 | 10.0141 | 7.3052 | 3.8674 | 39.2292 | 9.8791 | 7.2067 | 3.3687 | 39.173 | 9.8375 | 7.1763 | 3.5639 | 39.1778 | 9.7666 | 7.1246 | 3.5235 | 39.2091 | 9.6683 | 7.0529 | 3.3859 | 39.2729 | 9.4835 | 6.9181 | 3.1027 | 39.3345 | 9.4719 | 6.9096 | 2.6596 | 39.3906 | 9.4522 | 6.8953 | 2.6855 | 39.4402 | 9.3714 | 6.8363 | 2.5431 | 39.4845 | 9.2681 | 6.7609 | 2.3753 | 39.5575 | 8.8701 | 6.4706 | 1.6963 | 39.5774 | 8.5038 | 6.2034 | 0.83948 | 39.4527 | 8.24 | 6.0109 | 0.33982 | 39.26 | 8.2491 | 6.0176 | 0.23559 | 39.0668 | 10.0155 | 7.3061 | 3.8711 | 39.223 | 9.8977 | 7.2202 | 3.3746 | 39.1607 | 9.8516 | 7.1866 | 3.5803 | 39.1581 | 9.7214 | 7.0916 | 3.5563 | 39.1835 | 9.7223 | 7.0923 | 3.4327 | 39.2401 | 9.5976 | 7.0013 | 3.1692 | 39.2935 | 9.4458 | 6.8906 | 2.7494 | 39.3405 | 9.245 | 6.7441 | 2.8009 | 39.3783 | 9.2664 | 6.7597 | 2.6927 | 39.4285 | 9.1507 | 6.6753 | 2.3062 | 39.565 | 8.5091 | 6.2073 | 0.64818 | 39.5623 | 7.9751 | 5.8177 | -0.13858 | 39.4051 | 7.8777 | 5.7467 | -0.35219 | 39.1276 | 7.9828 | 5.8233 | 0.5508
DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 32.0012 | 13.3495 | 9.7383 | 12.3511 | 32.0741 | 13.2138 | 9.6393 | 11.783 | 32.1183 | 13.1185 | 9.5698 | 11.6418 | 32.2169 | 13.0384 | 9.5113 | 11.412 | 32.3457 | 12.894 | 9.406 | 10.9935 | 32.48 | 12.7289 | 9.2856 | 10.4486 | 32.6279 | 12.5179 | 9.1316 | 9.9225 | 32.7874 | 12.2243 | 8.9175 | 9.36 | 32.9573 | 12.1815 | 8.8862 | 8.8121 | 33.1427 | 12.1388 | 8.8551 | 8.2844 | 33.8104 | 11.6182 | 8.4753 | 6.2722 | 34.201 | 11.113 | 8.1067 | 5.4416 | 34.4238 | 10.9733 | 8.0049 | 5.4231 | 34.547 | 10.8782 | 7.9355 | 5.7689 | 31.9604 | 13.3326 | 9.7259 | 12.5463 | 32.0009 | 13.2411 | 9.6592 | 12.1487 | 32.0803 | 13.1721 | 9.6089 | 11.9211 | 32.1931 | 13.0763 | 9.539 | 11.685 | 32.3232 | 12.9465 | 9.4443 | 11.296 | 32.4697 | 12.8155 | 9.3488 | 10.7879 | 32.6306 | 12.6546 | 9.2314 | 10.2869 | 32.7873 | 12.4849 | 9.1076 | 9.7763 | 32.9425 | 12.2916 | 8.9665 | 9.2184 | 33.1068 | 12.2634 | 8.946 | 8.769 | 33.4288 | 12.1313 | 8.8496 | 7.2205 | 33.6588 | 11.9275 | 8.701 | 6.2666 | 33.7946 | 11.8103 | 8.6154 | 5.8267 | 33.8685 | 11.706 | 8.5394 | 5.611 | 32.0012 | 13.3254 | 9.7207 | 12.3584 | 32.0741 | 13.2266 | 9.6486 | 11.7999 | 32.1183 | 13.1253 | 9.5747 | 11.6658 | 32.2169 | 12.9717 | 9.4627 | 11.4434 | 32.3453 | 12.7784 | 9.3217 | 11.0358 | 32.4788 | 12.606 | 9.1959 | 10.5042 | 32.626 | 12.5942 | 9.1873 | 9.9906 | 32.7851 | 12.5368 | 9.1454 | 9.4249 | 32.9528 | 12.4409 | 9.0755 | 8.8959 | 33.1292 | 12.346 | 9.0063 | 8.4139 | 33.7552 | 11.84 | 8.6371 | 6.5283 | 34.1266 | 11.4378 | 8.3437 | 5.7572 | 34.3334 | 11.1561 | 8.1382 | 5.7351 | 34.4509 | 11.0507 | 8.0613 | 6.048 | 31.9967 | 13.3521 | 9.7402 | 12.3707 | 32.0714 | 13.2212 | 9.6447 | 11.8302 | 32.1343 | 13.1362 | 9.5827 | 11.7286 | 32.2633 | 13.0378 | 9.5109 | 11.5343 | 32.4115 | 12.8922 | 9.4047 | 11.1737 | 32.5997 | 12.7107 | 9.2723 | 10.6983 | 32.8188 | 12.4503 | 9.0823 | 10.2454 | 33.0656 | 12.2509 | 8.9368 | 9.8011 | 33.3373 | 12.251 | 8.9369 | 9.3847 | 33.5997 | 12.2036 | 8.9023 | 9.0868 | 34.3292 | 11.4129 | 8.3256 | 6.9882 | 34.9112 | 9.9901 | 7.2876 | 2.6222 | 35.1722 | 9.1895 | 6.7036 | -1.0345 | 35.2837 | 8.5174 | 6.2133 | -3.5658 | 31.9982 | 13.3635 | 9.7485 | 12.3438 | 32.0916 | 13.2635 | 9.6756 | 11.7493 | 32.1475 | 13.2012 | 9.6301 | 11.6534 | 32.2368 | 13.1065 | 9.561 | 11.5076 | 32.366 | 12.8939 | 9.4059 | 11.2084 | 32.5257 | 12.6024 | 9.1933 | 10.8179 | 32.7182 | 12.5245 | 9.1364 | 10.4399 | 32.9269 | 12.5182 | 9.1319 | 10.0804 | 33.1571 | 12.4487 | 9.0812 | 9.6892 | 33.4236 | 12.2397 | 8.9287 | 8.7672 | 34.1487 | 10.8435 | 7.9102 | 3.8089 | 34.5453 | 9.5443 | 6.9624 | -0.67788 | 34.6001 | 8.8514 | 6.457 | -3.0733 | 34.4361 | 8.8499 | 6.4559 | -2.1583
DODGSON RD | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 355190 | 430397 | 29.675 | 11.4456 | 8.3494 | 19.2488 | 29.7175 | 11.1842 | 8.1587 | 18.9896 | 29.7333 | 10.9515 | 7.989 | 18.9657 | 29.7696 | 10.6684 | 7.7824 | 18.7213 | 29.8228 | 10.4195 | 7.6009 | 18.7078 | 29.8946 | 10.0914 | 7.3615 | 18.4299 | 29.9788 | 10.0357 | 7.3209 | 18.2956 | 30.0728 | 9.9674 | 7.2711 | 18.1541 | 30.1772 | 9.8711 | 7.2008 | 17.9257 | 30.296 | 9.7444 | 7.1084 | 17.601 | 30.8844 | 9.1403 | 6.6677 | 16.5197 | 31.4414 | 9.0714 | 6.6174 | 15.42 | 31.7823 | 9.6569 | 7.0445 | 14.7378 | 32.0222 | 9.3913 | 6.8508 | 14.2613 | 29.6454 | 11.3603 | 8.2872 | 19.3349 | 29.6697 | 11.1068 | 8.1022 | 19.1182 | 29.7153 | 10.805 | 7.8821 | 19.0536 | 29.7733 | 10.4262 | 7.6058 | 18.801 | 29.843 | 10.1013 | 7.3688 | 18.7559 | 29.9251 | 10.1866 | 7.431 | 18.479 | 30.0121 | 10.1216 | 7.3836 | 18.3005 | 30.1067 | 10.0723 | 7.3476 | 18.1084 | 30.2094 | 10.0126 | 7.3041 | 17.8826 | 30.3191 | 9.9225 | 7.2383 | 17.5531 | 30.7352 | 9.6699 | 7.0541 | 16.7461 | 31.1152 | 9.4855 | 6.9195 | 16.1285 | 31.3296 | 9.9091 | 7.2285 | 15.6004 | 31.4744 | 10.1428 | 7.399 | 15.3042 | 29.6785 | 11.3514 | 8.2807 | 19.24 | 29.7223 | 11.1279 | 8.1176 | 19.0193 | 29.7389 | 10.7188 | 7.8192 | 18.9805 | 29.7757 | 10.409 | 7.5932 | 18.7379 | 29.8288 | 10.311 | 7.5218 | 18.7717 | 29.8986 | 10.1034 | 7.3703 | 18.5095 | 29.9791 | 9.9773 | 7.2783 | 18.3834 | 30.0679 | 9.9136 | 7.2318 | 18.2344 | 30.1651 | 9.8283 | 7.1696 | 18.0406 | 30.2734 | 9.7305 | 7.0982 | 17.7447 | 30.8132 | 9.4478 | 6.892 | 16.7534 | 31.2177 | 9.3197 | 6.7986 | 15.9408 | 31.4672 | 10.0775 | 7.3514 | 15.4853 | 31.6147 | 10.0054 | 7.2988 | 15.3462 | 29.677 | 11.4445 | 8.3486 | 19.2499 | 29.7197 | 11.1772 | 8.1536 | 18.9844 | 29.7384 | 10.8971 | 7.9493 | 18.9511 | 29.7811 | 10.6182 | 7.7458 | 18.6979 | 29.8426 | 10.3401 | 7.543 | 18.6599 | 29.9342 | 10.0685 | 7.3449 | 18.3544 | 30.0513 | 9.9596 | 7.2654 | 18.1747 | 30.1892 | 9.8771 | 7.2052 | 17.996 | 30.3425 | 9.7501 | 7.1125 | 17.7177 | 30.4988 | 9.604 | 7.006 | 17.406 | 31.31 | 8.9147 | 6.5032 | 15.6542 | 32.2688 | 8.1665 | 5.9573 | 11.7993 | 32.9472 | 8.1097 | 5.9159 | 8.4776 | 33.3087 | 7.6219 | 5.56 | 6.4221 | 29.6676 | 11.4499 | 8.3526 | 19.272 | 29.7048 | 11.368 | 8.2928 | 19.0263 | 29.7209 | 11.3003 | 8.2434 | 19.0089 | 29.7589 | 11.1561 | 8.1382 | 18.7737 | 29.8171 | 11.0419 | 8.0549 | 18.7682 | 29.9143 | 10.8648 | 7.9257 | 18.4949 | 30.048 | 10.6856 | 7.795 | 18.3438 | 30.2101 | 10.623 | 7.7493 | 18.1942 | 30.3765 | 10.4661 | 7.6349 | 17.8542 | 30.6056 | 10.2186 | 7.4544 | 16.9524 | 31.5709 | 9.2736 | 6.7649 | 13.0183 | 32.3972 | 8.3745 | 6.1091 | 9.5842 | 32.8864 | 7.9554 | 5.8033 | 7.3595 | 32.9593 | 7.7324 | 5.6407 | 7.3346
DOUGLAS ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 352220 | 429932 | 28.344 | 7.1849 | 5.2413 | 15.2055 | 28.4321 | 7.0877 | 5.1704 | 14.9708 | 28.4503 | 7.1391 | 5.2079 | 14.849 | 28.5086 | 7.0572 | 5.1481 | 14.5923 | 28.56 | 6.9158 | 5.045 | 14.5323 | 28.6288 | 6.6743 | 4.8688 | 14.4058 | 28.7024 | 6.6632 | 4.8607 | 14.1069 | 28.7784 | 6.6712 | 4.8666 | 13.8729 | 28.8571 | 6.6447 | 4.8472 | 13.7228 | 28.9409 | 6.5428 | 4.7728 | 13.3423 | 29.3982 | 6.1146 | 4.4605 | 12.2782 | 29.942 | 5.8477 | 4.2658 | 11.5941 | 30.3455 | 6.828 | 4.981 | 11.0982 | 30.7676 | 7.0332 | 5.1306 | 10.8822 | 28.2575 | 7.3246 | 5.3432 | 15.4878 | 28.278 | 7.2304 | 5.2745 | 15.4683 | 28.3395 | 7.0521 | 5.1444 | 15.2659 | 28.4221 | 6.9583 | 5.076 | 14.9517 | 28.4925 | 6.9715 | 5.0856 | 14.8547 | 28.5672 | 6.9478 | 5.0683 | 14.6032 | 28.6492 | 6.9333 | 5.0578 | 14.3547 | 28.7345 | 6.8919 | 5.0275 | 14.0721 | 28.8241 | 6.821 | 4.9758 | 13.7347 | 28.9164 | 6.715 | 4.8985 | 13.1527 | 29.2078 | 6.5193 | 4.7558 | 12.6561 | 29.52 | 6.4591 | 4.7118 | 12.3517 | 29.8159 | 7.1508 | 5.2164 | 11.9695 | 30.0483 | 7.8308 | 5.7125 | 11.8018 | 28.3442 | 7.3185 | 5.3387 | 15.2302 | 28.4326 | 7.0895 | 5.1717 | 15.011 | 28.4512 | 7.2219 | 5.2683 | 14.8986 | 28.5103 | 7.2065 | 5.257 | 14.6517 | 28.5623 | 7.1527 | 5.2178 | 14.5648 | 28.6318 | 7.0287 | 5.1273 | 14.4422 | 28.706 | 6.9233 | 5.0504 | 14.1523 | 28.7825 | 6.7736 | 4.9413 | 13.9267 | 28.8611 | 6.6859 | 4.8773 | 13.7875 | 28.9419 | 6.5355 | 4.7676 | 13.4341 | 29.3287 | 6.2998 | 4.5956 | 12.5054 | 29.6746 | 6.2597 | 4.5664 | 12.0463 | 29.9777 | 7.2744 | 5.3066 | 11.6649 | 30.2134 | 7.2733 | 5.3058 | 11.6094 | 28.3362 | 7.1782 | 5.2364 | 15.2209 | 28.4196 | 7.1143 | 5.1898 | 15.0006 | 28.4434 | 7.1809 | 5.2384 | 14.8925 | 28.4896 | 7.0225 | 5.1228 | 14.6442 | 28.5462 | 6.7711 | 4.9395 | 14.5861 | 28.6365 | 6.7394 | 4.9163 | 14.4492 | 28.7473 | 6.7236 | 4.9048 | 14.1266 | 28.8726 | 6.6792 | 4.8724 | 13.8583 | 29.0064 | 6.6157 | 4.8261 | 13.6784 | 29.1557 | 6.5226 | 4.7582 | 13.2829 | 30.0022 | 5.8432 | 4.2625 | 11.6266 | 30.9833 | 5.0609 | 3.6918 | 8.938 | 31.5786 | 5.7993 | 4.2305 | 6.7933 | 31.8018 | 5.6226 | 4.1016 | 5.6537 | 28.3368 | 7.1772 | 5.2357 | 15.2214 | 28.4327 | 7.1585 | 5.2221 | 14.9888 | 28.4543 | 7.2135 | 5.2621 | 14.878 | 28.4852 | 6.8651 | 5.008 | 14.6382 | 28.5417 | 7.1124 | 5.1884 | 14.5671 | 28.6381 | 7.1088 | 5.1858 | 14.4346 | 28.7647 | 6.9642 | 5.0803 | 14.1125 | 28.9127 | 6.9215 | 5.0492 | 13.8467 | 29.0898 | 6.8972 | 5.0314 | 13.6233 | 29.3203 | 6.7099 | 4.8948 | 12.8133 | 30.3695 | 6.6727 | 4.8676 | 9.6239 | 31.1745 | 5.6373 | 4.1123 | 7.2443 | 31.4569 | 5.6025 | 4.0869 | 5.8482 | 31.3871 | 5.6104 | 4.0927 | 6.3993
DROYLSDEN EAST | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 31.31 | 6.7749 | 4.9422 | 11.6932 | 31.3595 | 6.4867 | 4.7319 | 11.2787 | 31.3924 | 6.2059 | 4.5271 | 10.9699 | 31.4623 | 5.8416 | 4.2613 | 10.6027 | 31.5594 | 5.5839 | 4.0734 | 10.2689 | 31.6792 | 5.2973 | 3.8643 | 9.8464 | 31.6043 | 5.1265 | 3.7397 | 9.3321 | 30.5857 | 4.9613 | 3.6192 | 8.8534 | 29.5952 | 4.8006 | 3.502 | 8.343 | 28.2949 | 4.5897 | 3.3481 | 7.7226 | 23.6671 | 3.839 | 2.8005 | 5.6482 | 20.2493 | 3.2846 | 2.3961 | 4.5216 | 21.8078 | 3.5374 | 2.5805 | 4.2111 | 19.9022 | 3.2283 | 2.355 | 4.3994 | 31.2882 | 6.7897 | 4.953 | 11.8592 | 31.3241 | 6.455 | 4.7088 | 11.5906 | 31.3895 | 6.1667 | 4.4985 | 11.2419 | 31.4752 | 5.7935 | 4.2263 | 10.8834 | 31.5748 | 5.5956 | 4.0819 | 10.5863 | 31.6878 | 5.3346 | 3.8915 | 10.2035 | 31.8141 | 5.2172 | 3.8059 | 9.726 | 31.4869 | 5.1075 | 3.7258 | 9.2807 | 30.7108 | 4.9816 | 3.634 | 8.7983 | 29.9165 | 4.8527 | 3.54 | 8.2836 | 26.5717 | 4.3102 | 3.1442 | 6.7968 | 25.5773 | 4.1489 | 3.0266 | 5.702 | 25.4086 | 4.1215 | 3.0066 | 5.0433 | 27.6208 | 4.4804 | 3.2684 | 4.6633 | 31.31 | 6.785 | 4.9495 | 11.7051 | 31.3596 | 6.4531 | 4.7075 | 11.3136 | 31.3926 | 6.1196 | 4.4642 | 11.0283 | 31.4626 | 5.7671 | 4.207 | 10.6795 | 31.5594 | 5.5507 | 4.0492 | 10.3681 | 31.6787 | 5.1671 | 3.7693 | 9.9689 | 30.8465 | 5.0036 | 3.6501 | 9.4784 | 29.545 | 4.7925 | 3.4961 | 9.022 | 28.8183 | 4.6746 | 3.4101 | 8.5432 | 28.4303 | 4.6117 | 3.3642 | 7.9881 | 25.5714 | 4.1479 | 3.0259 | 6.1498 | 22.971 | 3.7261 | 2.7182 | 5.1189 | 24.5107 | 3.9759 | 2.9003 | 4.8699 | 22.3322 | 3.6225 | 2.6426 | 5.0732 | 31.306 | 6.7726 | 4.9405 | 11.7044 | 31.3555 | 6.4838 | 4.7299 | 11.3008 | 31.4002 | 6.1533 | 4.4887 | 11.009 | 31.4958 | 5.8109 | 4.239 | 10.6591 | 31.6343 | 5.5396 | 4.0411 | 10.3673 | 31.8142 | 5.2214 | 3.8089 | 9.9839 | 30.9085 | 5.0137 | 3.6574 | 9.4862 | 29.7913 | 4.8324 | 3.5252 | 9.0272 | 28.4382 | 4.613 | 3.3651 | 8.6097 | 26.9887 | 4.3778 | 3.1936 | 8.1644 | 19.4865 | 3.1609 | 2.3058 | 5.1575 | 8.7766 | 1.4237 | 1.0385 | -1.6857 | 2.9194 | 0.47356 | 0.34545 | -7.2097 | -3.7696 | -0.61146 | -0.44605 | -10.9355 | 31.2932 | 6.781 | 4.9467 | 11.7364 | 31.3429 | 6.6715 | 4.8667 | 11.3264 | 31.3906 | 6.5636 | 4.788 | 11.0378 | 31.48 | 6.3618 | 4.6409 | 10.7247 | 31.6113 | 6.2127 | 4.5321 | 10.4628 | 31.7763 | 6.046 | 4.4105 | 10.1395 | 31.9843 | 5.8614 | 4.2758 | 9.7149 | 32.2165 | 5.685 | 4.1471 | 9.3426 | 32.4601 | 5.4441 | 3.9714 | 8.7828 | 30.6864 | 4.9776 | 3.6311 | 7.1458 | 18.6284 | 3.0217 | 2.2043 | -0.43385 | 9.0959 | 1.4754 | 1.0763 | -6.641 | 2.5703 | 0.41693 | 0.30415 | -10.3176 | 1.4452 | 0.23442 | 0.17101 | -9.3336
DUKINFIELD | HYDE | STALYBRIDGE | 394372 | 396438 | 22.2445 | 4.1568 | 3.0323 | 15.3785 | 22.2716 | 4.0542 | 2.9575 | 15.0831 | 22.2812 | 4.0236 | 2.9352 | 15.1423 | 22.3048 | 3.8654 | 2.8198 | 15.0377 | 22.3384 | 3.8154 | 2.7833 | 15.0445 | 22.3816 | 3.7211 | 2.7145 | 14.8533 | 22.3857 | 3.6312 | 2.6489 | 14.7591 | 21.9481 | 3.5602 | 2.5971 | 14.6572 | 21.4427 | 3.4782 | 2.5373 | 14.4727 | 20.2567 | 3.2858 | 2.397 | 14.3171 | 21.149 | 3.4306 | 2.5026 | 13.7263 | 23.3114 | 5.6179 | 4.0982 | 13.2488 | 23.5813 | 9.4277 | 6.8774 | 13.0471 | 23.8482 | 10.2298 | 7.4625 | 12.9137 | 22.2293 | 4.1646 | 3.038 | 15.5674 | 22.2403 | 4.0104 | 2.9255 | 15.4247 | 22.2637 | 4.0545 | 2.9577 | 15.4071 | 22.2943 | 3.9954 | 2.9146 | 15.2646 | 22.3296 | 3.9564 | 2.8861 | 15.2536 | 22.37 | 3.8362 | 2.7985 | 15.0623 | 22.4157 | 3.7589 | 2.7421 | 14.9634 | 22.4652 | 3.6848 | 2.688 | 14.8547 | 21.9611 | 3.5623 | 2.5986 | 14.6614 | 21.8182 | 3.5391 | 2.5817 | 14.5139 | 22.7452 | 3.7976 | 2.7703 | 14.1025 | 22.9196 | 5.2633 | 3.8395 | 13.7126 | 23.0921 | 7.5764 | 5.5269 | 13.4922 | 23.2397 | 8.1164 | 5.9208 | 13.366 | 22.2445 | 4.1569 | 3.0324 | 15.3829 | 22.2719 | 4.0641 | 2.9647 | 15.0939 | 22.2817 | 4.0386 | 2.9461 | 15.1584 | 22.3055 | 3.9752 | 2.8999 | 15.0587 | 22.3394 | 3.8287 | 2.793 | 15.0665 | 22.3827 | 3.729 | 2.7203 | 14.8855 | 22.4331 | 3.7611 | 2.7437 | 14.7966 | 22.4888 | 3.7489 | 2.7347 | 14.6955 | 22.5485 | 3.7009 | 2.6997 | 14.5234 | 22.4939 | 3.6487 | 2.6617 | 14.3831 | 22.9102 | 3.7868 | 2.7624 | 13.8588 | 23.1689 | 6.0601 | 4.4208 | 13.4779 | 23.3877 | 9.9119 | 7.2306 | 13.3135 | 23.5662 | 10.7171 | 7.818 | 13.2594 | 22.2445 | 4.1577 | 3.033 | 15.394 | 22.2687 | 4.0622 | 2.9633 | 15.1136 | 22.2816 | 4.0006 | 2.9184 | 15.1852 | 22.313 | 3.8547 | 2.812 | 15.0905 | 22.3597 | 3.796 | 2.7691 | 15.1027 | 22.4255 | 3.679 | 2.6838 | 14.9179 | 22.1094 | 3.5864 | 2.6162 | 14.8109 | 21.5792 | 3.5004 | 2.5535 | 14.6867 | 20.3346 | 3.2985 | 2.4062 | 14.4992 | 20.4384 | 3.3153 | 2.4185 | 14.3569 | 18.665 | 3.0277 | 2.2086 | 13.3785 | 24.0277 | 4.9314 | 3.5974 | 11.1085 | 24.3625 | 8.247 | 6.0161 | 9.2548 | 24.5231 | 8.7689 | 6.3968 | 8.0191 | 22.2403 | 4.1604 | 3.035 | 15.4014 | 22.2664 | 4.0697 | 2.9688 | 15.118 | 22.2822 | 4.0591 | 2.961 | 15.1885 | 22.3135 | 3.9162 | 2.8568 | 15.101 | 22.3603 | 3.8466 | 2.8061 | 15.1162 | 22.4275 | 3.7463 | 2.7329 | 14.9456 | 22.5183 | 3.6622 | 2.6715 | 14.8412 | 22.6246 | 3.6815 | 2.6856 | 14.7257 | 22.7482 | 3.7104 | 2.7067 | 14.5029 | 22.9017 | 3.8644 | 2.819 | 14.0575 | 23.5608 | 10.0619 | 7.34 | 11.616 | 24.0207 | 9.5539 | 6.9694 | 9.4764 | 24.2018 | 9.1676 | 6.6876 | 8.2836 | 24.1914 | 9.0751 | 6.6201 | 8.6132
DUMERS LANE | BURY | KEARSLEY | 380057 | 408141 | 28.4023 | 10.679 | 7.6752 | 14.9341 | 28.4851 | 10.2274 | 7.3506 | 14.4408 | 28.4995 | 9.8901 | 7.1082 | 14.4549 | 28.539 | 9.6935 | 6.9669 | 14.2304 | 28.5998 | 9.4691 | 6.8056 | 14.1817 | 28.679 | 9.4406 | 6.7851 | 13.9701 | 28.7652 | 9.3946 | 6.7521 | 13.7423 | 28.8577 | 9.3472 | 6.718 | 13.6107 | 28.9569 | 9.26 | 6.6554 | 13.3382 | 29.0723 | 9.1482 | 6.575 | 13.0796 | 29.7724 | 8.674 | 6.2342 | 12.1092 | 30.6071 | 8.9142 | 6.4068 | 11.2506 | 31.2531 | 10.0424 | 7.2177 | 10.6533 | 31.8907 | 10.6802 | 7.6761 | 10.2102 | 28.3218 | 10.7864 | 7.7524 | 15.2676 | 28.3396 | 10.4194 | 7.4886 | 15.0612 | 28.3853 | 10.1102 | 7.2664 | 15.0022 | 28.4378 | 9.7475 | 7.0057 | 14.7294 | 28.5013 | 9.4389 | 6.7839 | 14.6523 | 28.5714 | 9.3664 | 6.7318 | 14.4451 | 28.6483 | 9.2664 | 6.6599 | 14.2145 | 28.7294 | 9.1673 | 6.5888 | 14.0723 | 28.8142 | 9.118 | 6.5533 | 13.7884 | 28.9005 | 9.1044 | 6.5435 | 13.5333 | 29.3472 | 9.011 | 6.4764 | 12.8857 | 29.8322 | 9.1455 | 6.5731 | 12.3269 | 30.2881 | 9.9376 | 7.1423 | 11.7949 | 30.6756 | 10.3675 | 7.4513 | 11.4938 | 28.4029 | 10.7813 | 7.7488 | 14.937 | 28.4863 | 10.3658 | 7.4501 | 14.4519 | 28.5017 | 9.9537 | 7.1539 | 14.4728 | 28.5422 | 9.7149 | 6.9823 | 14.2541 | 28.6038 | 9.4173 | 6.7684 | 14.211 | 28.6833 | 9.3208 | 6.699 | 14.0062 | 28.7695 | 9.2229 | 6.6287 | 13.7853 | 28.8618 | 9.247 | 6.646 | 13.6596 | 28.9597 | 9.2213 | 6.6275 | 13.3971 | 29.0704 | 9.1888 | 6.6042 | 13.158 | 29.686 | 9.0784 | 6.5248 | 12.2962 | 30.2612 | 9.3001 | 6.6842 | 11.6962 | 30.7659 | 10.4437 | 7.5061 | 11.2274 | 31.1641 | 11.1911 | 8.0433 | 10.9816 | 28.3964 | 10.6776 | 7.6742 | 14.9504 | 28.4762 | 10.1809 | 7.3172 | 14.4745 | 28.495 | 9.9527 | 7.1532 | 14.5044 | 28.546 | 9.7433 | 7.0027 | 14.2932 | 28.6231 | 9.4879 | 6.8191 | 14.2564 | 28.7383 | 9.4567 | 6.7967 | 14.049 | 28.8828 | 9.4006 | 6.7564 | 13.8134 | 29.0527 | 9.3313 | 6.7066 | 13.6643 | 29.2371 | 9.2158 | 6.6236 | 13.3782 | 29.444 | 9.0777 | 6.5243 | 13.1185 | 30.9129 | 8.5295 | 6.1303 | 11.4104 | 32.4969 | 8.1709 | 5.8726 | 8.3958 | 33.205 | 8.8812 | 6.3831 | 5.9237 | 33.4678 | 9.228 | 6.6323 | 4.4227 | 28.3937 | 10.9347 | 7.859 | 14.9498 | 28.4773 | 10.7959 | 7.7592 | 14.4594 | 28.5026 | 10.9152 | 7.845 | 14.4839 | 28.5586 | 10.9117 | 7.8425 | 14.2795 | 28.6423 | 10.8668 | 7.8102 | 14.2512 | 28.7733 | 10.7221 | 7.7062 | 14.0509 | 28.9463 | 10.5905 | 7.6116 | 13.8098 | 29.1529 | 10.459 | 7.5171 | 13.653 | 29.4317 | 10.2194 | 7.3449 | 13.2908 | 29.9392 | 10.1428 | 7.2898 | 12.6226 | 31.692 | 10.312 | 7.4114 | 9.2499 | 32.6998 | 9.7972 | 7.0415 | 6.4717 | 33.1131 | 9.3635 | 6.7297 | 4.7897 | 33.0936 | 9.3044 | 6.6872 | 5.1655
DUMPLINGTON | BARTON | CARRINGTON | 376770 | 397157 | 20.3215 | 3.3458 | 2.4047 | 20.3215 | 16.4072 | 2.7013 | 1.9415 | 16.4072 | 13.9064 | 2.2896 | 1.6456 | 13.9064 | 11.545 | 1.9008 | 1.3661 | 11.545 | 9.2922 | 1.5299 | 1.0996 | 9.2922 | 7.7765 | 1.2803 | 0.9202 | 7.7765 | 7.2001 | 1.1854 | 0.852 | 7.2001 | 6.6805 | 1.0999 | 0.79052 | 6.6805 | 6.2617 | 1.0309 | 0.74096 | 6.2617 | 5.5409 | 0.91227 | 0.65567 | 5.5409 | 4.0549 | 0.6676 | 0.47982 | 4.0549 | 5.9361 | 0.97734 | 0.70243 | 5.9361 | 10.9106 | 1.7963 | 1.2911 | 10.9106 | 13.943 | 2.2956 | 1.6499 | 13.943 | 21.2148 | 3.4929 | 2.5104 | 21.2148 | 17.7873 | 2.9286 | 2.1048 | 17.7873 | 15.4744 | 2.5477 | 1.8311 | 15.4744 | 12.5799 | 2.0712 | 1.4886 | 12.5799 | 10.4358 | 1.7182 | 1.2349 | 10.4358 | 8.7436 | 1.4396 | 1.0346 | 8.7436 | 8.229 | 1.3548 | 0.97375 | 8.229 | 7.766 | 1.2786 | 0.91896 | 7.766 | 7.4219 | 1.222 | 0.87825 | 7.4219 | 6.8022 | 1.1199 | 0.80492 | 6.8022 | 6.2081 | 1.0221 | 0.73462 | 6.2081 | 7.6735 | 1.2634 | 0.90802 | 7.6735 | 11.2134 | 1.8462 | 1.3269 | 11.2134 | 13.3195 | 2.193 | 1.5761 | 13.3195 | 21.2013 | 3.4906 | 2.5088 | 21.2013 | 17.7686 | 2.9255 | 2.1026 | 17.7686 | 15.4049 | 2.5363 | 1.8229 | 15.4049 | 12.6559 | 2.0837 | 1.4976 | 12.6559 | 10.2952 | 1.695 | 1.2182 | 10.2952 | 8.5816 | 1.4129 | 1.0155 | 8.5816 | 8.0227 | 1.3209 | 0.94934 | 8.0227 | 7.5098 | 1.2364 | 0.88864 | 7.5098 | 7.1314 | 1.1741 | 0.84387 | 7.1314 | 6.4845 | 1.0676 | 0.76732 | 6.4845 | 5.7465 | 0.94611 | 0.67999 | 5.7465 | 8.3376 | 1.3727 | 0.98661 | 8.3376 | 14.4458 | 2.3784 | 1.7094 | 14.4458 | 17.5401 | 2.8878 | 2.0755 | 17.5401 | 20.3759 | 3.3547 | 2.4111 | 20.3759 | 16.5009 | 2.7167 | 1.9526 | 16.5009 | 13.9884 | 2.3031 | 1.6553 | 13.9884 | 11.6643 | 1.9204 | 1.3803 | 11.6643 | 9.4911 | 1.5626 | 1.1231 | 9.4911 | 8.0471 | 1.3249 | 0.95223 | 8.0471 | 7.4939 | 1.2338 | 0.88677 | 7.4939 | 7.0777 | 1.1653 | 0.83752 | 7.0777 | 6.7498 | 1.1113 | 0.79872 | 6.7498 | 6.0881 | 1.0024 | 0.72042 | 6.0881 | 4.5505 | 0.74921 | 0.53847 | 4.5505 | 5.8678 | 0.96609 | 0.69435 | 5.8678 | 9.6971 | 1.5966 | 1.1475 | 9.6971 | 11.0096 | 1.8126 | 1.3028 | 11.0096 | 20.3636 | 3.3527 | 2.4097 | 20.3636 | 18.1196 | 2.9833 | 2.1441 | 18.1196 | 16.9539 | 2.7913 | 2.0062 | 16.9539 | 15.8968 | 2.6173 | 1.8811 | 15.8968 | 14.8171 | 2.4395 | 1.7533 | 14.8171 | 14.3152 | 2.3569 | 1.6939 | 14.3152 | 13.5542 | 2.2316 | 1.6039 | 13.5542 | 13.1863 | 2.171 | 1.5604 | 13.1863 | 12.7854 | 2.105 | 1.5129 | 12.7854 | 11.835 | 1.9485 | 1.4005 | 11.835 | 11.3964 | 1.8763 | 1.3486 | 11.3964 | 9.3043 | 1.5319 | 1.101 | 9.3043 | 9.789 | 1.6117 | 1.1583 | 9.789 | 10.3726 | 1.7078 | 1.2274 | 10.3726
EASTLANDS | STUART ST | STALYBRIDGE | 386458 | 398693 | 31.5587 | 7.5025 | 5.473 | 15.5364 | 31.6348 | 7.0459 | 5.1399 | 14.1013 | 31.6387 | 6.3735 | 4.6494 | 11.3341 | 31.6649 | 5.4551 | 3.9794 | 6.72 | 27.5994 | 4.4769 | 3.2658 | 2.2431 | 21.7557 | 3.529 | 2.5744 | -2.3504 | 16.3937 | 2.6592 | 1.9399 | -7.0011 | 16.0605 | 2.6052 | 1.9004 | -7.114 | 15.3883 | 2.4961 | 1.8209 | -7.2827 | 14.8146 | 2.4031 | 1.753 | -7.476 | 12.928 | 2.097 | 1.5298 | -8.1363 | 12.4492 | 2.0194 | 1.4731 | -8.5316 | 13.1031 | 2.1255 | 1.5505 | -8.6525 | 12.8474 | 2.084 | 1.5202 | -8.5247 | 31.4704 | 7.6106 | 5.5518 | 16.37 | 31.4811 | 7.3443 | 5.3575 | 15.7251 | 31.5215 | 6.7677 | 4.9369 | 13.1028 | 31.5855 | 5.8232 | 4.2479 | 8.4285 | 30.2077 | 4.9 | 3.5745 | 3.8964 | 24.6329 | 3.9957 | 2.9148 | -0.72673 | 19.6231 | 3.1831 | 2.322 | -5.4177 | 19.3207 | 3.134 | 2.2862 | -5.5829 | 18.9352 | 3.0715 | 2.2406 | -5.8115 | 18.5527 | 3.0094 | 2.1953 | -6.0432 | 17.5972 | 2.8544 | 2.0823 | -6.597 | 16.4215 | 2.6637 | 1.9432 | -7.0357 | 16.6278 | 2.6972 | 1.9676 | -7.2634 | 17.453 | 2.831 | 2.0652 | -7.2868 | 31.5587 | 7.6078 | 5.5498 | 15.5416 | 31.6348 | 7.3258 | 5.3441 | 14.1153 | 31.6388 | 6.6666 | 4.8632 | 11.3576 | 31.665 | 5.7478 | 4.1929 | 6.7514 | 30.009 | 4.8678 | 3.551 | 2.2821 | 24.0733 | 3.9049 | 2.8486 | -2.3033 | 18.4244 | 2.9886 | 2.1802 | -6.9457 | 17.6431 | 2.8619 | 2.0877 | -7.0507 | 16.8572 | 2.7344 | 1.9947 | -7.2091 | 17.0279 | 2.7621 | 2.0149 | -7.3844 | 16.3133 | 2.6462 | 1.9304 | -7.9945 | 15.7838 | 2.5603 | 1.8677 | -8.348 | 16.7598 | 2.7186 | 1.9832 | -8.4509 | 16.7137 | 2.7111 | 1.9777 | -8.3158 | 31.552 | 7.506 | 5.4756 | 15.5587 | 31.6207 | 7.0476 | 5.1411 | 14.1469 | 31.6138 | 6.3719 | 4.6482 | 11.4047 | 31.635 | 5.4346 | 3.9644 | 6.8123 | 27.391 | 4.4431 | 3.2412 | 2.3531 | 21.7061 | 3.5209 | 2.5685 | -2.2228 | 16.4898 | 2.6748 | 1.9512 | -6.8671 | 15.9137 | 2.5814 | 1.8831 | -6.9758 | 15.3504 | 2.49 | 1.8164 | -7.1193 | 14.6109 | 2.37 | 1.7289 | -7.2665 | 12.6451 | 2.0512 | 1.4963 | -7.9815 | 10.3432 | 1.6778 | 1.2239 | -9.3368 | 9.3562 | 1.5177 | 1.1071 | -10.2464 | 8.3755 | 1.3586 | 0.99107 | -10.7865 | 31.5467 | 7.5081 | 5.477 | 15.5663 | 31.6145 | 7.1695 | 5.2301 | 14.1552 | 31.5971 | 6.6217 | 4.8305 | 11.4252 | 31.607 | 5.7089 | 4.1646 | 6.8544 | 28.6685 | 4.6503 | 3.3923 | 2.4122 | 23.8156 | 3.8631 | 2.8181 | -2.1398 | 18.1703 | 2.9474 | 2.1501 | -6.7563 | 17.2243 | 2.794 | 2.0382 | -6.8341 | 15.8583 | 2.5724 | 1.8765 | -6.9577 | 15.866 | 2.5736 | 1.8774 | -7.2954 | 12.8981 | 2.0922 | 1.5262 | -8.87 | 9.5859 | 1.5549 | 1.1343 | -10.0797 | 8.6775 | 1.4076 | 1.0268 | -10.6525 | 8.2883 | 1.3444 | 0.98075 | -10.2423
EASTON | - | HARKER / HUTTON | 343201 | 571738 | 2.229 | 2.229 | 2.229 | 0.23747 | 2.2441 | 2.2441 | 2.2441 | 0.19267 | 2.2664 | 2.2664 | 2.2664 | 0.14354 | 2.2904 | 2.2904 | 2.2904 | 0.065454 | 2.3157 | 2.3157 | 2.3157 | 0.094257 | 2.3428 | 2.3428 | 2.3428 | 0.022891 | 2.375 | 2.375 | 2.375 | -0.055403 | 2.4089 | 2.4089 | 2.4089 | -0.081081 | 2.4445 | 2.4445 | 2.4445 | -0.1397 | 2.484 | 2.484 | 2.484 | -0.27606 | 2.5794 | 2.5794 | 2.5794 | -0.6879 | 2.6305 | 2.6305 | 2.6305 | -0.87754 | 2.6571 | 2.6571 | 2.6571 | -1.0313 | 2.6463 | 2.6463 | 2.6463 | -0.92787 | 2.2369 | 2.2369 | 2.2369 | 0.27729 | 2.2598 | 2.2598 | 2.2598 | 0.26552 | 2.289 | 2.289 | 2.289 | 0.20238 | 2.3177 | 2.3177 | 2.3177 | 0.12862 | 2.3395 | 2.3395 | 2.3395 | 0.15438 | 2.3596 | 2.3596 | 2.3596 | 0.081973 | 2.3843 | 2.3843 | 2.3843 | 0.001058 | 2.4108 | 2.4108 | 2.4108 | -0.03122 | 2.4389 | 2.4389 | 2.4389 | -0.08393 | 2.4683 | 2.4683 | 2.4683 | -0.1769 | 2.5456 | 2.5456 | 2.5456 | -0.35676 | 2.5937 | 2.5937 | 2.5937 | -0.64444 | 2.618 | 2.618 | 2.618 | -0.95364 | 2.6273 | 2.6273 | 2.6273 | -1.125 | 2.229 | 2.229 | 2.229 | 0.23895 | 2.2441 | 2.2441 | 2.2441 | 0.1972 | 2.2664 | 2.2664 | 2.2664 | 0.15218 | 2.2904 | 2.2904 | 2.2904 | 0.078695 | 2.3156 | 2.3156 | 2.3156 | 0.10857 | 2.3425 | 2.3425 | 2.3425 | 0.040456 | 2.3745 | 2.3745 | 2.3745 | -0.034699 | 2.4083 | 2.4083 | 2.4083 | -0.061837 | 2.4434 | 2.4434 | 2.4434 | -0.11873 | 2.4808 | 2.4808 | 2.4808 | -0.23796 | 2.5736 | 2.5736 | 2.5736 | -0.61922 | 2.6208 | 2.6208 | 2.6208 | -0.7866 | 2.6456 | 2.6456 | 2.6456 | -0.9249 | 2.6302 | 2.6302 | 2.6302 | -0.82149 | 2.2293 | 2.2293 | 2.2293 | 0.24065 | 2.246 | 2.246 | 2.246 | 0.19104 | 2.2697 | 2.2697 | 2.2697 | 0.13588 | 2.2932 | 2.2932 | 2.2932 | 0.051575 | 2.3174 | 2.3174 | 2.3174 | 0.064588 | 2.3441 | 2.3441 | 2.3441 | -0.029395 | 2.3762 | 2.3762 | 2.3762 | -0.13945 | 2.4091 | 2.4091 | 2.4091 | -0.19044 | 2.4422 | 2.4422 | 2.4422 | -0.25504 | 2.4755 | 2.4755 | 2.4755 | -0.35827 | 2.5876 | 2.5876 | 2.5876 | -0.66135 | 2.6627 | 2.6627 | 2.6627 | -0.79461 | 2.6903 | 2.6903 | 2.6903 | -0.80249 | 2.6985 | 2.6985 | 2.6985 | -0.732 | 2.2311 | 2.2311 | 2.2311 | 0.2337 | 2.25 | 2.25 | 2.25 | 0.17684 | 2.2716 | 2.2716 | 2.2716 | 0.12293 | 2.2921 | 2.2921 | 2.2921 | 0.038395 | 2.3128 | 2.3128 | 2.3128 | 0.038526 | 2.3343 | 2.3343 | 2.3343 | -0.061162 | 2.361 | 2.361 | 2.361 | -0.16552 | 2.3867 | 2.3867 | 2.3867 | -0.20739 | 2.4113 | 2.4113 | 2.4113 | -0.26165 | 2.4423 | 2.4423 | 2.4423 | -0.36845 | 2.56 | 2.56 | 2.56 | -0.69742 | 2.6127 | 2.6127 | 2.6127 | -0.78899 | 2.6187 | 2.6187 | 2.6187 | -0.76612 | 2.5931 | 2.5931 | 2.5931 | -0.64888
EGREMONT | EGREMONT | HARKER / HUTTON | 301070 | 513074 | 21.1215 | 18.4918 | 13.2904 | 5.2877 | 21.1931 | 18.4613 | 13.2685 | 5.1517 | 21.2303 | 18.3684 | 13.2017 | 4.7933 | 21.3021 | 18.2064 | 13.0853 | 4.1921 | 21.3964 | 18.0976 | 13.0071 | 3.9647 | 21.5148 | 17.8436 | 12.8246 | 3.4802 | 21.6505 | 17.5478 | 12.612 | 2.8831 | 21.8 | 17.2391 | 12.3901 | 2.2968 | 21.9557 | 16.951 | 12.183 | 1.798 | 22.1453 | 16.5725 | 11.911 | 1.0108 | 22.9649 | 15.675 | 11.2659 | -1.7525 | 23.6144 | 15.1776 | 10.9084 | -3.0311 | 23.9758 | 16.1942 | 11.6391 | -3.1005 | 24.114 | 15.7971 | 11.3537 | -2.3104 | 21.0775 | 18.5111 | 13.3043 | 5.3951 | 21.1156 | 18.5165 | 13.3082 | 5.4107 | 21.1911 | 18.4288 | 13.2452 | 4.9594 | 21.2704 | 18.3245 | 13.1702 | 4.4991 | 21.365 | 18.293 | 13.1475 | 4.4799 | 21.4755 | 18.2049 | 13.0842 | 4.1463 | 21.6018 | 18.0937 | 13.0043 | 3.6941 | 21.741 | 17.9879 | 12.9283 | 3.2701 | 21.8912 | 17.8883 | 12.8566 | 2.8553 | 22.0522 | 17.7792 | 12.7782 | 2.3586 | 22.4393 | 17.4817 | 12.5645 | 1.078 | 22.7722 | 17.165 | 12.3368 | 0.18013 | 22.9296 | 17.5259 | 12.5962 | -0.26204 | 22.9734 | 17.9588 | 12.9074 | -0.33486 | 21.1235 | 18.512 | 13.3049 | 5.2947 | 21.1958 | 18.5111 | 13.3043 | 5.1725 | 21.2334 | 18.4033 | 13.2268 | 4.8526 | 21.3053 | 18.2679 | 13.1295 | 4.2894 | 21.3992 | 18.202 | 13.0821 | 4.0783 | 21.5157 | 17.8284 | 12.8136 | 3.6264 | 21.6486 | 17.3966 | 12.5032 | 3.0635 | 21.7945 | 16.934 | 12.1708 | 2.5104 | 21.9443 | 16.2003 | 11.6435 | 2.0479 | 22.1216 | 16.3578 | 11.7566 | 1.3347 | 22.8857 | 15.8441 | 11.3874 | -1.1435 | 23.4388 | 15.705 | 11.2875 | -2.1986 | 23.7006 | 16.5036 | 11.8615 | -2.1575 | 23.7863 | 16.4338 | 11.8113 | -1.3484 | 21.1202 | 18.49 | 13.2891 | 5.2924 | 21.2 | 18.4429 | 13.2553 | 5.1213 | 21.2578 | 18.3069 | 13.1575 | 4.7122 | 21.3569 | 18.123 | 13.0254 | 4.1006 | 21.4994 | 17.9961 | 12.9341 | 3.8626 | 21.6921 | 17.7023 | 12.723 | 3.3108 | 21.9328 | 17.35 | 12.4698 | 2.5878 | 22.2136 | 16.9706 | 12.1971 | 1.8497 | 22.5008 | 16.6195 | 11.9447 | 1.2908 | 22.8205 | 16.1824 | 11.6306 | 0.62296 | 24.0472 | 14.9473 | 10.7429 | -2.2787 | 25.3516 | 13.8731 | 9.9709 | -7.5524 | 26.1336 | 14.0091 | 10.0686 | -10.8657 | 26.4164 | 13.1649 | 9.4619 | -13.3777 | 21.1095 | 18.4947 | 13.2925 | 5.3128 | 21.1892 | 18.4366 | 13.2507 | 5.0981 | 21.2476 | 18.2913 | 13.1463 | 4.6973 | 21.3429 | 18.0838 | 12.9972 | 4.1024 | 21.4779 | 17.9313 | 12.8876 | 3.8485 | 21.6535 | 17.6105 | 12.657 | 3.3673 | 21.8739 | 17.2571 | 12.403 | 2.7541 | 22.1211 | 16.9085 | 12.1524 | 2.1749 | 22.3842 | 16.5395 | 11.8872 | 1.7308 | 22.781 | 15.9628 | 11.4728 | 0.38472 | 24.156 | 15.8067 | 11.3606 | -5.652 | 25.0536 | 14.529 | 10.4423 | -9.8032 | 25.5092 | 13.9747 | 10.0439 | -11.8157 | 25.5563 | 13.7621 | 9.8911 | -10.7478
EMBLETON | STAINBURN & SIDDICK | HARKER / HUTTON | 315767 | 529389 | 29.6752 | 18.7503 | 13.4762 | 15.4621 | 29.762 | 18.6396 | 13.3966 | 15.0757 | 29.7937 | 18.543 | 13.3272 | 14.9113 | 29.8547 | 18.3957 | 13.2214 | 14.5444 | 29.9383 | 18.2932 | 13.1477 | 14.4343 | 30.0433 | 18.1195 | 13.0228 | 13.9994 | 30.1644 | 17.9551 | 12.9047 | 13.5182 | 30.2969 | 17.8234 | 12.81 | 13.2119 | 30.4355 | 17.683 | 12.7091 | 12.8777 | 30.5948 | 17.5093 | 12.5843 | 12.3678 | 31.2786 | 16.8341 | 12.099 | 10.5694 | 31.8466 | 16.4577 | 11.8285 | 9.6202 | 32.2087 | 17.1437 | 12.3215 | 9.3609 | 32.4808 | 16.92 | 12.1607 | 9.6478 | 29.6411 | 18.7843 | 13.5006 | 15.5937 | 29.6937 | 18.7233 | 13.4568 | 15.3679 | 29.7729 | 18.6381 | 13.3955 | 15.1079 | 29.8647 | 18.5282 | 13.3166 | 14.7699 | 29.9702 | 18.4636 | 13.2701 | 14.6872 | 30.0887 | 18.3224 | 13.1687 | 14.2857 | 30.2228 | 18.208 | 13.0865 | 13.8325 | 30.3693 | 18.1196 | 13.0229 | 13.5425 | 30.5277 | 18.0144 | 12.9473 | 13.1988 | 30.6978 | 17.8955 | 12.8619 | 12.7718 | 30.9911 | 17.5978 | 12.6479 | 11.8353 | 31.266 | 17.305 | 12.4374 | 11.0429 | 31.5036 | 17.5896 | 12.642 | 10.444 | 31.6835 | 17.9211 | 12.8802 | 10.1609 | 29.6753 | 18.7831 | 13.4998 | 15.4716 | 29.7623 | 18.7171 | 13.4523 | 15.097 | 29.7943 | 18.6112 | 13.3763 | 14.9562 | 29.8557 | 18.4713 | 13.2757 | 14.6154 | 29.9394 | 18.3762 | 13.2073 | 14.526 | 30.0443 | 18.2072 | 13.0859 | 14.1185 | 30.1653 | 18.041 | 12.9664 | 13.6656 | 30.2978 | 17.9042 | 12.8681 | 13.383 | 30.435 | 17.7446 | 12.7534 | 13.0783 | 30.5875 | 17.5503 | 12.6137 | 12.6248 | 31.2073 | 17.08 | 12.2757 | 11.0446 | 31.6515 | 16.7046 | 12.0059 | 10.2744 | 31.9463 | 17.1152 | 12.301 | 10.0381 | 32.1294 | 16.6359 | 11.9565 | 10.3478 | 29.6706 | 18.7496 | 13.4757 | 15.4707 | 29.7561 | 18.6304 | 13.3901 | 15.0709 | 29.7961 | 18.5131 | 13.3057 | 14.8872 | 29.875 | 18.347 | 13.1863 | 14.5122 | 29.9903 | 18.2217 | 13.0963 | 14.3814 | 30.1462 | 18.0173 | 12.9494 | 13.9024 | 30.3421 | 17.8117 | 12.8016 | 13.3418 | 30.5704 | 17.6348 | 12.6745 | 12.9458 | 30.8233 | 17.4598 | 12.5487 | 12.5898 | 31.1077 | 17.2676 | 12.4106 | 12.1572 | 32.0186 | 16.4032 | 11.7893 | 10.3071 | 32.7574 | 15.4058 | 11.0725 | 7.1464 | 33.1501 | 15.5478 | 11.1745 | 5.091 | 33.3141 | 14.8986 | 10.7079 | 3.5957 | 29.6709 | 18.7567 | 13.4808 | 15.5025 | 29.7436 | 18.6627 | 13.4133 | 15.1102 | 29.784 | 18.5515 | 13.3333 | 14.9373 | 29.8582 | 18.3914 | 13.2183 | 14.5863 | 29.968 | 18.2729 | 13.1331 | 14.4829 | 30.1163 | 18.0819 | 12.9958 | 14.0611 | 30.3107 | 17.8807 | 12.8512 | 13.5799 | 30.5326 | 17.7341 | 12.7459 | 13.2846 | 30.7755 | 17.5937 | 12.6449 | 13.0025 | 31.0686 | 17.3654 | 12.4808 | 12.2117 | 32.0413 | 17.1793 | 12.3471 | 8.5262 | 32.6237 | 16.0922 | 11.5658 | 5.974 | 32.7974 | 15.4648 | 11.1149 | 4.6483 | 32.7126 | 15.246 | 10.9576 | 5.2236
EXCHANGE ST | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 24.6801 | 15.6556 | 11.4205 | 10.1523 | 24.7488 | 15.564 | 11.3537 | 9.6981 | 24.7682 | 15.457 | 11.2757 | 9.3714 | 24.8124 | 15.2614 | 11.1329 | 9.0631 | 24.877 | 15.1391 | 11.0438 | 8.9706 | 24.9605 | 14.8873 | 10.86 | 8.6472 | 25.0552 | 14.7845 | 10.7851 | 8.2947 | 25.1584 | 14.7275 | 10.7435 | 7.9989 | 25.2695 | 14.6575 | 10.6925 | 7.7222 | 25.3923 | 14.5038 | 10.5803 | 7.2431 | 25.9341 | 13.9625 | 10.1854 | 5.8519 | 26.5222 | 13.9057 | 10.144 | 5.1418 | 26.9638 | 14.1522 | 10.3239 | 4.7983 | 27.3785 | 14.1722 | 10.3384 | 4.8691 | 24.6352 | 15.7164 | 11.4649 | 10.3935 | 24.6685 | 15.5206 | 11.3221 | 10.145 | 24.7305 | 15.243 | 11.1196 | 9.8294 | 24.8045 | 14.8782 | 10.8534 | 9.5127 | 24.8903 | 14.8588 | 10.8393 | 9.4268 | 24.9868 | 14.8031 | 10.7986 | 9.1174 | 25.0959 | 14.6966 | 10.721 | 8.7744 | 25.2144 | 14.6071 | 10.6557 | 8.4823 | 25.343 | 14.5014 | 10.5785 | 8.2021 | 25.4805 | 14.3993 | 10.5041 | 7.7754 | 25.7774 | 14.2254 | 10.3772 | 6.8309 | 26.0822 | 13.974 | 10.1938 | 6.19 | 26.3793 | 14.8626 | 10.842 | 5.6507 | 26.6208 | 14.9489 | 10.905 | 5.4145 | 24.6802 | 15.7036 | 11.4555 | 10.1611 | 24.7492 | 15.4741 | 11.2881 | 9.7061 | 24.769 | 15.193 | 11.0831 | 9.389 | 24.8137 | 14.9591 | 10.9125 | 9.0921 | 24.8788 | 14.5617 | 10.6226 | 9.0089 | 24.9624 | 14.6954 | 10.7201 | 8.6982 | 25.0574 | 14.591 | 10.6439 | 8.3583 | 25.1608 | 14.47 | 10.5556 | 8.0738 | 25.2711 | 14.3339 | 10.4564 | 7.8137 | 25.3888 | 14.1549 | 10.3258 | 7.375 | 25.8634 | 13.9362 | 10.1663 | 6.1268 | 26.2754 | 14.1308 | 10.3082 | 5.5751 | 26.6277 | 14.6785 | 10.7077 | 5.2997 | 26.9071 | 14.6533 | 10.6894 | 5.4365 | 24.6753 | 15.6598 | 11.4236 | 10.153 | 24.7423 | 15.5493 | 11.343 | 9.7005 | 24.7673 | 15.437 | 11.2611 | 9.3779 | 24.8243 | 15.258 | 11.1305 | 9.0678 | 24.9108 | 15.0729 | 10.9955 | 9.0062 | 25.032 | 14.8364 | 10.823 | 8.701 | 25.1831 | 14.7562 | 10.7644 | 8.3517 | 25.3591 | 14.6868 | 10.7138 | 8.0599 | 25.5578 | 14.5487 | 10.6131 | 7.8296 | 25.7812 | 14.3161 | 10.4434 | 7.4532 | 26.7567 | 13.566 | 9.8962 | 5.3335 | 27.6786 | 12.6305 | 9.2138 | 0.9006 | 28.2446 | 12.0821 | 8.8137 | -2.6538 | 28.4848 | 11.635 | 8.4876 | -4.6527 | 24.6624 | 15.6708 | 11.4316 | 10.1828 | 24.7246 | 15.5938 | 11.3755 | 9.7199 | 24.7453 | 15.539 | 11.3355 | 9.4119 | 24.7921 | 15.4568 | 11.2755 | 9.1514 | 24.8685 | 15.4584 | 11.2767 | 9.1066 | 24.9821 | 15.3514 | 11.1986 | 8.8472 | 25.1343 | 15.2779 | 11.145 | 8.5455 | 25.3119 | 15.1949 | 11.0845 | 8.3062 | 25.5206 | 15.0629 | 10.9882 | 7.9897 | 25.7817 | 14.8087 | 10.8027 | 6.8168 | 26.8844 | 14.1789 | 10.3433 | 1.6946 | 27.6762 | 12.7604 | 9.3085 | -2.2449 | 27.9745 | 12.1003 | 8.827 | -4.5546 | 27.9179 | 12.0351 | 8.7795 | -3.5804
FAILSWORTH | CHADDERTON | WHITEGATE | 389631 | 401496 | 23.6649 | 9.922 | 7.2379 | 14.2743 | 23.7312 | 9.5613 | 6.9749 | 13.8981 | 23.7616 | 9.3932 | 6.8522 | 13.8262 | 23.8121 | 9.2285 | 6.7321 | 13.5506 | 23.882 | 9.0236 | 6.5826 | 13.338 | 23.9679 | 8.8006 | 6.4199 | 12.9897 | 24.0634 | 8.6945 | 6.3425 | 12.7093 | 24.1663 | 8.59 | 6.2663 | 12.3459 | 24.2756 | 8.4691 | 6.1781 | 11.9285 | 24.396 | 8.316 | 6.0664 | 11.4895 | 24.9011 | 7.7726 | 5.67 | 9.9733 | 25.3353 | 7.6889 | 5.609 | 9.1361 | 25.629 | 7.9766 | 5.8188 | 8.8459 | 25.8775 | 7.9869 | 5.8264 | 8.8173 | 23.6292 | 9.9598 | 7.2656 | 14.4167 | 23.6698 | 9.7467 | 7.1101 | 14.1566 | 23.7368 | 9.5645 | 6.9772 | 13.9955 | 23.8081 | 9.3672 | 6.8332 | 13.6918 | 23.8914 | 9.2007 | 6.7118 | 13.4752 | 23.9841 | 9.0125 | 6.5745 | 13.1355 | 24.0871 | 8.9267 | 6.5119 | 12.8572 | 24.1978 | 8.8151 | 6.4305 | 12.495 | 24.3161 | 8.7098 | 6.3537 | 12.0695 | 24.4411 | 8.5975 | 6.2717 | 11.6666 | 24.7198 | 8.3991 | 6.127 | 10.5277 | 24.964 | 8.4068 | 6.1326 | 9.7157 | 25.159 | 8.5814 | 6.26 | 9.2184 | 25.3107 | 8.6123 | 6.2825 | 8.8834 | 23.665 | 9.9542 | 7.2614 | 14.286 | 23.7313 | 9.6527 | 7.0415 | 13.9234 | 23.7619 | 9.4985 | 6.929 | 13.8629 | 23.8125 | 9.2948 | 6.7804 | 13.5999 | 23.8824 | 9.1137 | 6.6484 | 13.4015 | 23.9681 | 8.9484 | 6.5277 | 13.069 | 24.0634 | 8.861 | 6.464 | 12.8028 | 24.1663 | 8.7602 | 6.3905 | 12.4542 | 24.2745 | 8.6365 | 6.3002 | 12.0576 | 24.3899 | 8.5167 | 6.2128 | 11.6572 | 24.8565 | 8.1171 | 5.9213 | 10.2967 | 25.2166 | 8.2074 | 5.9872 | 9.5683 | 25.4727 | 8.6851 | 6.3356 | 9.3157 | 25.6647 | 8.612 | 6.2823 | 9.312 | 23.6614 | 9.922 | 7.238 | 14.2826 | 23.7273 | 9.5868 | 6.9934 | 13.9149 | 23.7641 | 9.412 | 6.8659 | 13.8519 | 23.8285 | 9.2145 | 6.7219 | 13.5849 | 23.9197 | 8.9976 | 6.5636 | 13.3928 | 24.0392 | 8.7543 | 6.3861 | 13.0564 | 24.1836 | 8.648 | 6.3086 | 12.7984 | 24.3486 | 8.5299 | 6.2224 | 12.4415 | 24.5267 | 8.3281 | 6.0752 | 12.0304 | 24.7246 | 8.2467 | 6.0159 | 11.658 | 25.6067 | 7.4523 | 5.4364 | 9.4728 | 26.4657 | 6.4802 | 4.7272 | 4.4736 | 26.967 | 5.9408 | 4.3337 | 0.363 | 27.2449 | 5.3472 | 3.9007 | -2.4451 | 23.6491 | 9.9306 | 7.2442 | 14.3193 | 23.7084 | 9.6964 | 7.0734 | 13.965 | 23.7407 | 9.5971 | 7.001 | 13.921 | 23.7945 | 9.454 | 6.8965 | 13.7012 | 23.8748 | 9.1653 | 6.6859 | 13.5579 | 23.9811 | 9.0832 | 6.6261 | 13.2701 | 24.1159 | 8.9811 | 6.5516 | 13.0753 | 24.2682 | 8.8499 | 6.4559 | 12.7718 | 24.4582 | 8.6333 | 6.2979 | 12.2682 | 24.7631 | 8.3461 | 6.0883 | 11.0203 | 25.6918 | 7.7381 | 5.6449 | 5.4753 | 26.3186 | 6.3266 | 4.6152 | 0.95508 | 26.5769 | 5.6348 | 4.1105 | -1.8041 | 26.536 | 5.5977 | 4.0835 | -1.1871
FALLOWFIELD | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 31.7458 | 12.1086 | 8.8331 | 11.5712 | 31.812 | 12.0391 | 8.7823 | 11.3137 | 31.8406 | 11.9532 | 8.7197 | 11.0564 | 31.9028 | 11.8162 | 8.6197 | 10.7981 | 31.9886 | 11.6035 | 8.4646 | 10.4197 | 32.0949 | 11.5841 | 8.4504 | 9.9885 | 32.2075 | 11.5319 | 8.4123 | 9.4881 | 32.3227 | 11.4723 | 8.3689 | 9.0572 | 32.4451 | 11.3572 | 8.2849 | 8.6116 | 32.5844 | 11.2265 | 8.1896 | 8.0463 | 33.1051 | 10.4607 | 7.631 | 5.9558 | 33.4775 | 9.7807 | 7.1349 | 4.708 | 33.683 | 9.5601 | 6.9739 | 4.1969 | 33.8164 | 9.439 | 6.8857 | 4.1596 | 31.7158 | 12.2205 | 8.9147 | 11.6795 | 31.7656 | 12.1761 | 8.8823 | 11.4992 | 31.8459 | 12.0877 | 8.8178 | 11.149 | 31.9506 | 12.0166 | 8.766 | 10.8807 | 32.067 | 11.9414 | 8.7111 | 10.5081 | 32.1983 | 11.8454 | 8.6411 | 10.0796 | 32.3424 | 11.76 | 8.5788 | 9.5668 | 32.4981 | 11.6739 | 8.516 | 9.1132 | 32.6658 | 11.5758 | 8.4444 | 8.6361 | 32.846 | 11.4717 | 8.3685 | 8.1168 | 33.1526 | 11.1556 | 8.1378 | 6.5806 | 33.3922 | 10.8025 | 7.8803 | 5.3527 | 33.544 | 10.5699 | 7.7106 | 4.5653 | 33.647 | 10.2849 | 7.5027 | 3.996 | 31.7458 | 12.2234 | 8.9168 | 11.584 | 31.8121 | 12.1839 | 8.888 | 11.3434 | 31.8407 | 12.0824 | 8.8139 | 11.1047 | 31.9029 | 12.0328 | 8.7777 | 10.8616 | 31.9885 | 11.9457 | 8.7142 | 10.5017 | 32.0944 | 11.8407 | 8.6376 | 10.0895 | 32.2067 | 11.7263 | 8.5542 | 9.6087 | 32.3217 | 11.6026 | 8.464 | 9.1958 | 32.443 | 11.466 | 8.3643 | 8.7754 | 32.5775 | 11.3228 | 8.2598 | 8.2623 | 33.0728 | 10.7042 | 7.8085 | 6.331 | 33.4142 | 10.0642 | 7.3417 | 5.1934 | 33.6033 | 9.933 | 7.246 | 4.7228 | 33.7205 | 9.665 | 7.0505 | 4.6787 | 31.7415 | 12.1056 | 8.8309 | 11.5801 | 31.8082 | 12.023 | 8.7706 | 11.3252 | 31.8403 | 11.908 | 8.6867 | 11.0694 | 31.9179 | 11.7397 | 8.5639 | 10.8 | 32.0282 | 11.625 | 8.4803 | 10.42 | 32.1708 | 11.569 | 8.4394 | 9.9669 | 32.3364 | 11.4854 | 8.3784 | 9.3934 | 32.5196 | 11.3767 | 8.2991 | 8.8809 | 32.7166 | 11.2515 | 8.2078 | 8.4241 | 32.9315 | 11.0875 | 8.0882 | 7.9264 | 33.5075 | 9.9717 | 7.2742 | 5.0604 | 34.0378 | 8.5174 | 6.2133 | -0.52492 | 34.3211 | 7.4193 | 5.4123 | -4.7313 | 34.47 | 6.5958 | 4.8115 | -7.6481 | 31.7258 | 12.1073 | 8.8321 | 11.5855 | 31.7811 | 11.988 | 8.7451 | 11.3307 | 31.8061 | 11.8206 | 8.623 | 11.1053 | 31.8645 | 11.7038 | 8.5378 | 10.8848 | 31.9559 | 11.7541 | 8.5745 | 10.533 | 32.0734 | 11.6953 | 8.5316 | 10.1369 | 32.2143 | 11.575 | 8.4438 | 9.6465 | 32.3661 | 11.4424 | 8.3471 | 9.228 | 32.5193 | 11.2814 | 8.2296 | 8.7547 | 32.7102 | 10.9418 | 7.9819 | 7.3856 | 33.355 | 9.0336 | 6.5899 | 0.94694 | 33.7571 | 7.7834 | 5.6779 | -4.0871 | 33.8767 | 7.0314 | 5.1293 | -6.8829 | 33.7766 | 6.9102 | 5.0409 | -6.0866
FARNWORTH | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 31.1147 | 12.6815 | 9.1144 | 11.7158 | 31.1793 | 12.6362 | 9.0819 | 11.5732 | 31.2015 | 12.5474 | 9.0181 | 11.409 | 31.2546 | 12.4058 | 8.9163 | 11.1402 | 31.331 | 12.3064 | 8.8448 | 10.9097 | 31.4302 | 12.1398 | 8.7251 | 10.5552 | 31.5444 | 11.9727 | 8.605 | 10.1226 | 31.6701 | 11.7946 | 8.477 | 9.7514 | 31.8062 | 11.6939 | 8.4046 | 9.344 | 31.9591 | 11.6235 | 8.354 | 8.8394 | 32.7338 | 11.1887 | 8.0416 | 6.9387 | 33.5563 | 10.8661 | 7.8097 | 5.8216 | 34.1524 | 10.7426 | 7.7209 | 5.4343 | 34.657 | 10.7261 | 7.7091 | 5.4601 | 31.0713 | 12.6868 | 9.1183 | 11.8152 | 31.1029 | 12.6634 | 9.1014 | 11.7472 | 31.1634 | 12.5915 | 9.0497 | 11.4907 | 31.2385 | 12.5058 | 8.9882 | 11.1982 | 31.3267 | 12.4244 | 8.9296 | 10.9778 | 31.4279 | 12.3252 | 8.8584 | 10.6422 | 31.5431 | 12.2257 | 8.7868 | 10.2211 | 31.6685 | 12.1281 | 8.7167 | 9.8569 | 31.8037 | 12.0176 | 8.6373 | 9.4485 | 31.9474 | 11.9008 | 8.5533 | 9.0021 | 32.4076 | 11.4911 | 8.2589 | 7.7989 | 32.8655 | 11.3933 | 8.1886 | 6.8917 | 33.232 | 11.4575 | 8.2347 | 6.2861 | 33.5095 | 11.4721 | 8.2453 | 5.9327 | 31.1171 | 12.6842 | 9.1164 | 11.7307 | 31.1827 | 12.6364 | 9.082 | 11.5995 | 31.2049 | 12.5108 | 8.9918 | 11.4484 | 31.2585 | 12.3409 | 8.8696 | 11.1923 | 31.3351 | 12.1581 | 8.7382 | 10.995 | 31.4334 | 12.1252 | 8.7146 | 10.6343 | 31.5458 | 12.0535 | 8.6631 | 10.217 | 31.6691 | 11.9886 | 8.6165 | 9.9167 | 31.8008 | 11.9079 | 8.5585 | 9.5354 | 31.944 | 11.8085 | 8.487 | 9.0828 | 32.6354 | 11.4541 | 8.2323 | 7.3368 | 33.237 | 11.2096 | 8.0566 | 6.4521 | 33.6801 | 11.1277 | 7.9977 | 6.1874 | 34.0015 | 10.9894 | 7.8983 | 6.3126 | 31.1128 | 12.6814 | 9.1144 | 11.7182 | 31.1764 | 12.6338 | 9.0802 | 11.5747 | 31.2056 | 12.529 | 9.0048 | 11.4074 | 31.2745 | 12.38 | 8.8977 | 11.1292 | 31.3768 | 12.264 | 8.8144 | 10.9118 | 31.5215 | 12.0645 | 8.671 | 10.5127 | 31.7041 | 11.844 | 8.5125 | 10.0269 | 31.9178 | 11.7802 | 8.4666 | 9.6728 | 32.154 | 11.7325 | 8.4324 | 9.3276 | 32.419 | 11.66 | 8.3803 | 8.9504 | 33.7748 | 10.9744 | 7.8875 | 6.4318 | 35.1061 | 9.7459 | 7.0045 | 1.0278 | 35.8823 | 8.7803 | 6.3106 | -3.1369 | 36.2567 | 8.1699 | 5.8719 | -5.9575 | 31.1013 | 12.6897 | 9.1203 | 11.7612 | 31.1635 | 12.647 | 9.0897 | 11.6313 | 31.1934 | 12.5054 | 8.9879 | 11.4817 | 31.2578 | 12.2888 | 8.8322 | 11.2513 | 31.3569 | 12.1789 | 8.7532 | 11.077 | 31.5032 | 12.1834 | 8.7564 | 10.7381 | 31.6989 | 12.0751 | 8.6786 | 10.312 | 31.929 | 11.9629 | 8.598 | 10.0213 | 32.2018 | 11.8765 | 8.5359 | 9.6101 | 32.5902 | 11.607 | 8.3422 | 8.3643 | 34.0202 | 10.2394 | 7.3593 | 2.4633 | 35.0192 | 8.9581 | 6.4384 | -2.3517 | 35.4972 | 8.4042 | 6.0403 | -5.1439 | 35.5312 | 8.4289 | 6.058 | -4.3901
FENISCOWLES | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 18.0802 | 18.0802 | 18.0802 | 14.8874 | 18.1152 | 18.1152 | 18.1152 | 14.7722 | 18.1882 | 18.1882 | 18.1882 | 14.7569 | 18.2409 | 18.2409 | 18.2409 | 14.7104 | 18.2812 | 18.2812 | 18.2812 | 14.6129 | 18.3263 | 18.3263 | 18.3263 | 14.555 | 18.3778 | 18.3778 | 18.3778 | 14.512 | 18.434 | 18.434 | 18.434 | 14.4284 | 18.4944 | 18.4944 | 18.4944 | 14.3379 | 18.5603 | 18.5603 | 18.5603 | 14.2709 | 18.7342 | 18.7342 | 18.7342 | 13.9201 | 18.8202 | 18.8202 | 18.8202 | 13.7212 | 18.8682 | 18.8682 | 18.8682 | 13.7024 | 18.9012 | 18.9012 | 18.9012 | 13.8272 | 18.0895 | 18.0895 | 18.0895 | 14.9831 | 18.13 | 18.13 | 18.13 | 14.9473 | 18.1911 | 18.1911 | 18.1911 | 14.9093 | 18.2223 | 18.2223 | 18.2223 | 14.8513 | 18.2467 | 18.2467 | 18.2467 | 14.7541 | 18.2734 | 18.2734 | 18.2734 | 14.7028 | 18.3027 | 18.3027 | 18.3027 | 14.6636 | 18.3337 | 18.3337 | 18.3337 | 14.584 | 18.3661 | 18.3661 | 18.3661 | 14.4972 | 18.399 | 18.399 | 18.399 | 14.4419 | 18.5143 | 18.5143 | 18.5143 | 14.261 | 18.5987 | 18.5987 | 18.5987 | 14.0783 | 18.6596 | 18.6596 | 18.6596 | 13.935 | 18.7033 | 18.7033 | 18.7033 | 13.8957 | 18.0802 | 18.0802 | 18.0802 | 14.8884 | 18.1153 | 18.1153 | 18.1153 | 14.7744 | 18.1883 | 18.1883 | 18.1883 | 14.7601 | 18.241 | 18.241 | 18.241 | 14.7149 | 18.2811 | 18.2811 | 18.2811 | 14.6193 | 18.3259 | 18.3259 | 18.3259 | 14.563 | 18.3771 | 18.3771 | 18.3771 | 14.5216 | 18.4331 | 18.4331 | 18.4331 | 14.4397 | 18.4924 | 18.4924 | 18.4924 | 14.3522 | 18.554 | 18.554 | 18.554 | 14.2918 | 18.7212 | 18.7212 | 18.7212 | 14.0153 | 18.7908 | 18.7908 | 18.7908 | 13.8592 | 18.8311 | 18.8311 | 18.8311 | 13.8519 | 18.8532 | 18.8532 | 18.8532 | 13.9762 | 18.0808 | 18.0808 | 18.0808 | 14.8943 | 18.1159 | 18.1159 | 18.1159 | 14.787 | 18.1865 | 18.1865 | 18.1865 | 14.7814 | 18.258 | 18.258 | 18.258 | 14.7467 | 18.3272 | 18.3272 | 18.3272 | 14.6656 | 18.4004 | 18.4004 | 18.4004 | 14.6238 | 18.4892 | 18.4892 | 18.4892 | 14.594 | 18.5777 | 18.5777 | 18.5777 | 14.5273 | 18.6174 | 18.6174 | 18.6174 | 14.4623 | 18.6619 | 18.6619 | 18.6619 | 14.433 | 18.8286 | 18.8286 | 18.8286 | 13.9622 | 18.9958 | 18.9958 | 18.9958 | 12.7319 | 19.0994 | 19.0994 | 19.0994 | 11.764 | 19.1537 | 19.1537 | 19.1537 | 11.1962 | 18.0951 | 18.0951 | 18.0951 | 14.8877 | 18.1563 | 18.1563 | 18.1563 | 14.7671 | 18.2389 | 18.2389 | 18.2389 | 14.7565 | 18.2996 | 18.2996 | 18.2996 | 14.7209 | 18.3648 | 18.3648 | 18.3648 | 14.6361 | 18.4383 | 18.4383 | 18.4383 | 14.5961 | 18.5281 | 18.5281 | 18.5281 | 14.5718 | 18.5811 | 18.5811 | 18.5811 | 14.513 | 18.6206 | 18.6206 | 18.6206 | 14.4367 | 18.6755 | 18.6755 | 18.6755 | 14.2168 | 18.8734 | 18.8734 | 18.8734 | 12.8266 | 19.0055 | 19.0055 | 19.0055 | 11.7294 | 19.058 | 19.058 | 19.058 | 11.1121 | 19.0376 | 19.0376 | 19.0376 | 11.3984
FERODO | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 30.6587 | 17.778 | 12.7774 | 16.4972 | 30.7408 | 17.5838 | 12.6378 | 16.24 | 30.7785 | 17.4154 | 12.5168 | 16.1292 | 30.8381 | 17.2333 | 12.3859 | 15.932 | 30.9149 | 17.0714 | 12.2695 | 15.8043 | 31.0119 | 16.8867 | 12.1368 | 15.5098 | 31.1232 | 16.801 | 12.0752 | 15.2189 | 31.2436 | 16.7173 | 12.0151 | 14.9502 | 31.5214 | 16.612 | 11.9394 | 14.5348 | 31.6559 | 16.5071 | 11.864 | 14.1318 | 32.3177 | 16.0883 | 11.563 | 12.7428 | 32.9895 | 15.6968 | 11.2816 | 11.8561 | 33.4679 | 15.5796 | 11.1974 | 11.5457 | 33.9147 | 15.2182 | 10.9377 | 11.585 | 30.6093 | 17.8204 | 12.8079 | 16.7438 | 30.655 | 17.6496 | 12.6851 | 16.6141 | 30.7258 | 17.4821 | 12.5647 | 16.401 | 30.8043 | 17.3286 | 12.4544 | 16.1762 | 30.8877 | 17.2125 | 12.371 | 16.085 | 30.9647 | 17.0785 | 12.2747 | 15.8305 | 31.0504 | 17.0204 | 12.2329 | 15.5736 | 31.1409 | 16.9652 | 12.1932 | 15.3347 | 31.2364 | 16.9072 | 12.1515 | 15.071 | 31.335 | 16.844 | 12.1061 | 14.7598 | 31.7278 | 16.6631 | 11.9761 | 13.9489 | 32.0849 | 16.4813 | 11.8454 | 13.2285 | 32.4182 | 16.6323 | 11.9539 | 12.7342 | 32.656 | 17.1384 | 12.3177 | 12.4183 | 30.6589 | 17.8207 | 12.8081 | 16.5007 | 30.7411 | 17.6434 | 12.6807 | 16.2536 | 30.7792 | 17.464 | 12.5518 | 16.1557 | 30.8393 | 17.2966 | 12.4314 | 15.9702 | 30.9164 | 17.1669 | 12.3382 | 15.8556 | 31.0134 | 17.0193 | 12.2321 | 15.5759 | 31.1248 | 16.9505 | 12.1826 | 15.2995 | 31.2453 | 16.8518 | 12.1117 | 15.0449 | 31.522 | 16.7692 | 12.0524 | 14.6442 | 31.6504 | 16.6981 | 12.0012 | 14.2789 | 32.2433 | 16.2394 | 11.6716 | 13.0445 | 32.7485 | 16.1927 | 11.638 | 12.3292 | 33.1418 | 16.5945 | 11.9268 | 12.0868 | 33.4463 | 16.1613 | 11.6154 | 12.1912 | 30.6551 | 17.7801 | 12.7789 | 16.5161 | 30.7391 | 17.583 | 12.6373 | 16.2615 | 30.7875 | 17.4044 | 12.5089 | 16.1471 | 30.8641 | 17.217 | 12.3742 | 15.9529 | 30.9685 | 17.0477 | 12.2525 | 15.818 | 31.2816 | 16.8219 | 12.0902 | 15.3254 | 31.4514 | 16.7184 | 12.0158 | 14.9847 | 31.6505 | 16.6144 | 11.9411 | 14.6506 | 31.873 | 16.5179 | 11.8718 | 14.3618 | 32.1226 | 16.4103 | 11.7944 | 14.0091 | 36.1767 | 15.3164 | 11.0082 | 9.4589 | 37.3503 | 14.601 | 10.494 | 6.7551 | 37.6384 | 14.1974 | 10.2039 | 5.1006 | 37.6328 | 13.3281 | 9.5792 | 3.8619 | 30.657 | 17.7815 | 12.7799 | 16.523 | 30.7522 | 17.6693 | 12.6993 | 16.2691 | 30.8024 | 17.5548 | 12.617 | 16.163 | 30.8752 | 17.4132 | 12.5152 | 15.9795 | 31.1547 | 17.2508 | 12.3985 | 15.6869 | 31.2855 | 17.0874 | 12.281 | 15.4111 | 31.4615 | 16.9795 | 12.2035 | 15.1203 | 35.2069 | 16.2718 | 11.6949 | 11.3055 | 35.2657 | 16.1677 | 11.62 | 11.2349 | 35.3647 | 16.0178 | 11.5123 | 10.7614 | 36.2749 | 15.3306 | 11.0184 | 8.0893 | 37.1982 | 14.4502 | 10.3856 | 5.7603 | 37.4427 | 14.0277 | 10.082 | 4.7059 | 37.366 | 13.7126 | 9.8555 | 5.0457
FLAT LANE | NELSON | PADIHAM | 383248 | 456995 | 10.1718 | 10.1718 | 10.1718 | 5.495 | 10.2005 | 10.2005 | 10.2005 | 5.3085 | 10.2526 | 10.2526 | 10.2526 | 5.1786 | 10.3076 | 10.3076 | 10.3076 | 5.0451 | 10.3569 | 10.3569 | 10.3569 | 4.8996 | 10.3938 | 10.3938 | 10.3938 | 4.7397 | 10.4385 | 10.4385 | 10.4385 | 4.5662 | 10.4834 | 10.4834 | 10.4834 | 4.383 | 10.5312 | 10.5312 | 10.5312 | 4.1918 | 10.5866 | 10.5866 | 10.5866 | 3.9375 | 10.7799 | 10.7799 | 10.7799 | 3.0491 | 10.915 | 10.915 | 10.915 | 2.6186 | 10.9836 | 10.9836 | 10.9836 | 2.4935 | 11.0142 | 11.0142 | 11.0142 | 2.6623 | 10.1889 | 10.1889 | 10.1889 | 5.5754 | 10.2323 | 10.2323 | 10.2323 | 5.4628 | 10.2885 | 10.2885 | 10.2885 | 5.3232 | 10.3348 | 10.3348 | 10.3348 | 5.2075 | 10.3786 | 10.3786 | 10.3786 | 5.0823 | 10.4285 | 10.4285 | 10.4285 | 4.9416 | 10.4875 | 10.4875 | 10.4875 | 4.78 | 10.5384 | 10.5384 | 10.5384 | 4.6068 | 10.5818 | 10.5818 | 10.5818 | 4.426 | 10.6261 | 10.6261 | 10.6261 | 4.2377 | 10.7104 | 10.7104 | 10.7104 | 3.7234 | 10.7929 | 10.7929 | 10.7929 | 3.2219 | 10.8412 | 10.8412 | 10.8412 | 2.8662 | 10.8713 | 10.8713 | 10.8713 | 2.65 | 10.1718 | 10.1718 | 10.1718 | 5.4991 | 10.2005 | 10.2005 | 10.2005 | 5.3221 | 10.2526 | 10.2526 | 10.2526 | 5.1939 | 10.3076 | 10.3076 | 10.3076 | 5.0678 | 10.3568 | 10.3568 | 10.3568 | 4.931 | 10.3934 | 10.3934 | 10.3934 | 4.7794 | 10.4379 | 10.4379 | 10.4379 | 4.6137 | 10.4828 | 10.4828 | 10.4828 | 4.4382 | 10.5301 | 10.5301 | 10.5301 | 4.2595 | 10.5831 | 10.5831 | 10.5831 | 4.0335 | 10.7646 | 10.7646 | 10.7646 | 3.2383 | 10.8896 | 10.8896 | 10.8896 | 2.8656 | 10.9555 | 10.9555 | 10.9555 | 2.7862 | 10.985 | 10.985 | 10.985 | 2.9551 | 10.1741 | 10.1741 | 10.1741 | 5.4972 | 10.2058 | 10.2058 | 10.2058 | 5.3005 | 10.2604 | 10.2604 | 10.2604 | 5.159 | 10.3177 | 10.3177 | 10.3177 | 5.0169 | 10.3817 | 10.3817 | 10.3817 | 4.8506 | 10.4417 | 10.4417 | 10.4417 | 4.663 | 10.5036 | 10.5036 | 10.5036 | 4.4511 | 10.5747 | 10.5747 | 10.5747 | 4.2336 | 10.6535 | 10.6535 | 10.6535 | 4.0393 | 10.7416 | 10.7416 | 10.7416 | 3.8448 | 10.9832 | 10.9832 | 10.9832 | 2.9787 | 11.1485 | 11.1485 | 11.1485 | 1.8712 | 11.2216 | 11.2216 | 11.2216 | 1.25 | 11.2615 | 11.2615 | 11.2615 | 0.82113 | 10.1807 | 10.1807 | 10.1807 | 5.4849 | 10.2243 | 10.2243 | 10.2243 | 5.2672 | 10.2805 | 10.2805 | 10.2805 | 5.1166 | 10.3338 | 10.3338 | 10.3338 | 4.9703 | 10.3825 | 10.3825 | 10.3825 | 4.7945 | 10.4253 | 10.4253 | 10.4253 | 4.6116 | 10.4806 | 10.4806 | 10.4806 | 4.4175 | 10.5415 | 10.5415 | 10.5415 | 4.2271 | 10.6074 | 10.6074 | 10.6074 | 4.0565 | 10.6857 | 10.6857 | 10.6857 | 3.7178 | 10.9126 | 10.9126 | 10.9126 | 2.2072 | 11.0206 | 11.0206 | 11.0206 | 1.2639 | 11.0415 | 11.0415 | 11.0415 | 0.88663 | 11.0231 | 11.0231 | 11.0231 | 1.1543
FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 32.5643 | 9.297 | 6.782 | 12.1189 | 32.6682 | 9.0419 | 6.596 | 11.0424 | 32.6932 | 8.9252 | 6.5108 | 10.8451 | 32.7595 | 8.7632 | 6.3926 | 10.4756 | 32.8477 | 8.6605 | 6.3177 | 10.1571 | 32.9584 | 8.5256 | 6.2193 | 9.8047 | 33.077 | 8.4083 | 6.1337 | 9.4814 | 33.1962 | 8.2701 | 6.0329 | 9.0518 | 33.3213 | 8.0954 | 5.9055 | 8.6282 | 33.4598 | 8.0106 | 5.8436 | 8.1075 | 34.1634 | 7.2976 | 5.3235 | 6.063 | 34.9427 | 6.9697 | 5.0843 | 4.603 | 35.5161 | 6.6918 | 4.8816 | 3.7403 | 36.067 | 6.5661 | 4.7899 | 3.3415 | 32.4904 | 9.3378 | 6.8118 | 12.5147 | 32.5351 | 9.145 | 6.6711 | 11.828 | 32.612 | 9.0489 | 6.6011 | 11.6478 | 32.7196 | 8.9113 | 6.5007 | 11.244 | 32.8392 | 8.7824 | 6.4066 | 10.9037 | 32.9697 | 8.687 | 6.3371 | 10.5359 | 33.1091 | 8.6178 | 6.2866 | 10.2241 | 33.2439 | 8.5325 | 6.2243 | 9.815 | 33.3849 | 8.4336 | 6.1522 | 9.3663 | 33.5313 | 8.3312 | 6.0775 | 8.9195 | 33.9958 | 7.9107 | 5.7708 | 7.3648 | 34.4883 | 7.7072 | 5.6223 | 6.002 | 34.9391 | 7.4868 | 5.4615 | 4.9275 | 35.3165 | 7.4509 | 5.4353 | 4.148 | 32.5645 | 9.3343 | 6.8092 | 12.1279 | 32.6688 | 9.1307 | 6.6607 | 11.0615 | 32.6942 | 9.01 | 6.5726 | 10.8698 | 32.7613 | 8.8036 | 6.4221 | 10.5093 | 32.8501 | 8.6606 | 6.3178 | 10.1999 | 32.9612 | 8.5808 | 6.2596 | 9.8576 | 33.0803 | 8.5213 | 6.2162 | 9.5839 | 33.2001 | 8.4222 | 6.1439 | 9.2109 | 33.3248 | 8.3134 | 6.0645 | 8.814 | 33.4597 | 8.1921 | 5.976 | 8.3444 | 34.0898 | 7.6567 | 5.5854 | 6.5173 | 34.657 | 7.3434 | 5.3569 | 5.3125 | 35.1421 | 7.1795 | 5.2374 | 4.5731 | 35.5075 | 6.8084 | 4.9666 | 4.3075 | 32.5564 | 9.2986 | 6.7832 | 12.128 | 32.6556 | 9.0489 | 6.601 | 11.0654 | 32.6789 | 8.9068 | 6.4974 | 10.8849 | 32.7547 | 8.7398 | 6.3756 | 10.5206 | 32.8595 | 8.626 | 6.2925 | 10.2225 | 33.0047 | 8.5047 | 6.204 | 9.8833 | 33.1783 | 8.328 | 6.0752 | 9.4643 | 33.3731 | 8.1558 | 5.9495 | 8.9841 | 33.5797 | 8.0801 | 5.8943 | 8.5663 | 33.8067 | 7.9514 | 5.8004 | 8.1215 | 34.9822 | 7.1348 | 5.2047 | 5.5757 | 36.2311 | 6.0163 | 4.3888 | 1.1698 | 32.3488 | 5.2473 | 3.8278 | -2.1269 | 29.2204 | 4.7398 | 3.4576 | -4.4027 | 32.5488 | 9.3031 | 6.7865 | 12.1438 | 32.6462 | 9.0982 | 6.637 | 11.0794 | 32.6707 | 8.9759 | 6.5478 | 10.9158 | 32.7411 | 8.7847 | 6.4083 | 10.5781 | 32.8412 | 8.5479 | 6.2356 | 10.31 | 32.9864 | 8.562 | 6.2459 | 10.007 | 33.1658 | 8.4219 | 6.1437 | 9.588 | 33.3706 | 8.2487 | 6.0173 | 9.1584 | 33.6042 | 7.9583 | 5.8055 | 8.7337 | 33.9121 | 7.7959 | 5.687 | 7.7074 | 35.2252 | 6.6003 | 4.8148 | 2.7682 | 32.9084 | 5.3381 | 3.894 | -1.2034 | 30.7633 | 4.9901 | 3.6402 | -3.5412 | 30.1868 | 4.8966 | 3.572 | -3.2833
FUSEHILL | CARLISLE | HARKER / HUTTON | 341042 | 555452 | 34.1938 | 10.1852 | 7.3203 | 8.7351 | 34.358 | 9.8854 | 7.1048 | 7.9808 | 34.3682 | 9.7482 | 7.0062 | 8.0451 | 34.4306 | 9.4503 | 6.7921 | 7.7455 | 34.5288 | 9.2064 | 6.6168 | 7.7885 | 34.6529 | 8.7785 | 6.3093 | 7.3407 | 34.7803 | 8.4588 | 6.0795 | 6.9844 | 34.9074 | 8.2018 | 5.8948 | 6.9209 | 35.0335 | 7.9009 | 5.6785 | 6.505 | 35.1996 | 7.5959 | 5.4593 | 6.1126 | 35.9314 | 7.0606 | 5.0746 | 4.9521 | 36.499 | 6.8313 | 4.9098 | 4.3005 | 36.7887 | 7.3034 | 5.2491 | 4.1188 | 36.8815 | 7.274 | 5.228 | 4.3913 | 34.0285 | 10.2886 | 7.3946 | 9.1366 | 34.0564 | 10.0759 | 7.2418 | 8.7216 | 34.1383 | 9.9024 | 7.1171 | 8.6112 | 34.2275 | 9.6826 | 6.9591 | 8.2177 | 34.3395 | 9.5284 | 6.8483 | 8.1859 | 34.4596 | 9.1778 | 6.5963 | 7.7014 | 34.5883 | 8.9435 | 6.4279 | 7.2865 | 34.7214 | 8.779 | 6.3097 | 7.1485 | 34.8582 | 8.5578 | 6.1507 | 6.6376 | 34.9963 | 8.3571 | 6.0064 | 6.2118 | 35.4152 | 8.0785 | 5.8062 | 5.429 | 35.7974 | 7.9274 | 5.6976 | 4.7872 | 36.02 | 8.2698 | 5.9437 | 4.4174 | 36.1323 | 8.4873 | 6.1 | 4.377 | 34.1945 | 10.2859 | 7.3927 | 8.7456 | 34.359 | 10.0678 | 7.2359 | 8.0155 | 34.3694 | 9.8696 | 7.0934 | 8.0996 | 34.432 | 9.6177 | 6.9124 | 7.8216 | 34.53 | 9.4263 | 6.7749 | 7.8835 | 34.6535 | 8.9809 | 6.4547 | 7.4608 | 34.7804 | 8.6385 | 6.2087 | 7.1282 | 34.9068 | 8.5429 | 6.14 | 7.0837 | 35.0314 | 8.3357 | 5.9911 | 6.6977 | 35.1932 | 8.1324 | 5.8449 | 6.3502 | 35.8949 | 7.8353 | 5.6314 | 5.3274 | 36.3983 | 7.7279 | 5.5542 | 4.7914 | 36.6463 | 7.998 | 5.7483 | 4.6668 | 36.6904 | 7.8178 | 5.6188 | 4.969 | 34.1817 | 10.1872 | 7.3217 | 8.7626 | 34.3443 | 9.8039 | 7.0463 | 8.0281 | 34.3656 | 9.7002 | 6.9717 | 8.106 | 34.4472 | 9.386 | 6.7459 | 7.8157 | 34.571 | 9.1381 | 6.5677 | 7.8666 | 34.7458 | 8.6713 | 6.2322 | 7.4237 | 34.9527 | 8.277 | 5.9488 | 7.0494 | 35.1798 | 8.0447 | 5.7819 | 6.9578 | 35.3939 | 7.799 | 5.6053 | 6.5579 | 35.6243 | 7.5264 | 5.4094 | 6.2395 | 36.816 | 6.7507 | 4.8519 | 4.6871 | 35.5284 | 5.8495 | 4.2041 | 1.113 | 34.3794 | 5.6603 | 4.0682 | -1.5438 | 30.9457 | 5.095 | 3.6619 | -3.2068 | 34.167 | 10.1968 | 7.3287 | 8.8032 | 34.3212 | 9.9893 | 7.1795 | 8.096 | 34.3401 | 9.7268 | 6.9908 | 8.1977 | 34.4166 | 9.4324 | 6.7793 | 7.9444 | 34.5378 | 9.1974 | 6.6104 | 8.0341 | 34.706 | 8.9888 | 6.4604 | 7.6489 | 34.9033 | 8.6215 | 6.1964 | 7.3379 | 35.1144 | 8.6093 | 6.1877 | 7.3157 | 35.3575 | 8.3858 | 6.0271 | 6.9187 | 35.8851 | 8.0978 | 5.82 | 5.9923 | 37.0667 | 6.8848 | 4.9482 | 1.9237 | 35.4283 | 5.833 | 4.1923 | -1.2153 | 32.155 | 5.2941 | 3.805 | -2.9145 | 31.769 | 5.2305 | 3.7593 | -1.9875
GALE | BELFIELD | ROCHDALE | 389570 | 414943 | 30.2595 | 12.8774 | 9.3939 | 17.6206 | 30.3023 | 12.7255 | 9.2831 | 17.4109 | 30.3474 | 12.6795 | 9.2495 | 17.2753 | 30.4058 | 12.5812 | 9.1778 | 17.1639 | 30.4861 | 12.415 | 9.0566 | 16.963 | 30.5778 | 12.276 | 8.9552 | 16.603 | 30.6786 | 12.1734 | 8.8803 | 16.2469 | 30.7875 | 12.1212 | 8.8423 | 16.0508 | 30.905 | 12.0126 | 8.7631 | 15.6783 | 31.0192 | 11.8967 | 8.6785 | 15.3238 | 31.3807 | 11.4256 | 8.3348 | 14.1136 | 31.6428 | 11.1296 | 8.1189 | 13.3468 | 31.8014 | 11.2548 | 8.2102 | 13.0749 | 31.8976 | 11.1631 | 8.1433 | 12.957 | 30.2594 | 12.9115 | 9.4188 | 17.6357 | 30.3046 | 12.8071 | 9.3426 | 17.4675 | 30.3641 | 12.7049 | 9.2681 | 17.2794 | 30.4202 | 12.6153 | 9.2027 | 17.1645 | 30.494 | 12.5093 | 9.1253 | 16.9668 | 30.5762 | 12.3888 | 9.0375 | 16.6214 | 30.6664 | 12.2954 | 8.9693 | 16.2768 | 30.7623 | 12.2327 | 8.9236 | 16.0911 | 30.8639 | 12.1371 | 8.8538 | 15.7226 | 30.97 | 12.0461 | 8.7875 | 15.4191 | 31.1922 | 11.7077 | 8.5406 | 14.5796 | 31.3507 | 11.7464 | 8.5689 | 13.8573 | 31.4542 | 11.858 | 8.6502 | 13.4042 | 31.5224 | 11.8025 | 8.6097 | 12.973 | 30.2595 | 12.9186 | 9.4239 | 17.6211 | 30.3023 | 12.8056 | 9.3415 | 17.4324 | 30.3474 | 12.6503 | 9.2282 | 17.3101 | 30.4058 | 12.4873 | 9.1093 | 17.2084 | 30.4859 | 12.2815 | 8.9592 | 17.0298 | 30.5772 | 12.1609 | 8.8712 | 16.6864 | 30.6777 | 12.1198 | 8.8412 | 16.3466 | 30.7864 | 12.0764 | 8.8096 | 16.1633 | 30.9027 | 12.0019 | 8.7552 | 15.8114 | 31.0136 | 11.9258 | 8.6997 | 15.4911 | 31.3575 | 11.6629 | 8.5079 | 14.3605 | 31.6045 | 11.5777 | 8.4458 | 13.6676 | 31.7551 | 11.7428 | 8.5662 | 13.4194 | 31.8484 | 11.6057 | 8.4662 | 13.358 | 30.2607 | 12.8759 | 9.3928 | 17.6227 | 30.3105 | 12.7731 | 9.3178 | 17.4152 | 30.3668 | 12.6734 | 9.245 | 17.2795 | 30.4507 | 12.5421 | 9.1493 | 17.1646 | 30.5633 | 12.3795 | 9.0307 | 16.9751 | 30.7028 | 12.183 | 8.8873 | 16.6239 | 30.8451 | 12.1416 | 8.8572 | 16.2638 | 30.963 | 12.054 | 8.7933 | 16.0615 | 31.0887 | 11.9228 | 8.6975 | 15.7258 | 31.2268 | 11.8008 | 8.6085 | 15.4555 | 31.7625 | 11.0463 | 8.0581 | 13.6686 | 32.1594 | 10.1203 | 7.3826 | 9.358 | 32.3959 | 9.5441 | 6.9623 | 5.8854 | 32.5292 | 8.9986 | 6.5644 | 3.3189 | 30.2457 | 12.9202 | 9.4251 | 17.6589 | 30.2872 | 12.8527 | 9.3759 | 17.4619 | 30.3401 | 12.8362 | 9.3638 | 17.3405 | 30.4186 | 12.7392 | 9.293 | 17.2559 | 30.5257 | 12.5929 | 9.1863 | 17.0981 | 30.6536 | 12.4979 | 9.1171 | 16.7977 | 30.7879 | 12.3673 | 9.0218 | 16.4918 | 30.8921 | 12.2654 | 8.9475 | 16.3471 | 31.0176 | 12.11 | 8.8341 | 15.9322 | 31.2237 | 11.7961 | 8.6051 | 14.9174 | 31.7506 | 11.0587 | 8.0672 | 10.2962 | 32.0497 | 9.9045 | 7.2252 | 6.396 | 32.1577 | 9.425 | 6.8754 | 4.0648 | 32.0869 | 9.3357 | 6.8103 | 4.4001
GARSTANG | THORNTON | PENWORTHAM WEST / STANAH | 348319 | 445221 | 13.5267 | 13.5267 | 13.5267 | 0.79833 | 13.616 | 13.616 | 13.616 | 0.16544 | 13.7169 | 13.7169 | 13.7169 | -0.20251 | 13.7971 | 13.7971 | 13.7971 | -0.72275 | 13.8929 | 13.8929 | 13.8929 | -1.1251 | 14.0058 | 14.0058 | 14.0058 | -1.6899 | 14.1379 | 14.1379 | 14.1379 | -2.2749 | 14.2796 | 14.2796 | 14.2796 | -2.8622 | 14.43 | 14.43 | 14.43 | -3.4772 | 14.6035 | 14.6035 | 14.6035 | -4.2822 | 15.3315 | 15.3315 | 15.3315 | -7.0865 | 15.9669 | 15.9669 | 15.9669 | -8.5497 | 16.3882 | 16.3882 | 16.3882 | -8.8981 | 16.7321 | 16.7321 | 16.7321 | -8.459 | 13.5187 | 13.5187 | 13.5187 | 1.0436 | 13.6039 | 13.6039 | 13.6039 | 0.63441 | 13.7228 | 13.7228 | 13.7228 | 0.24972 | 13.8195 | 13.8195 | 13.8195 | -0.18019 | 13.9261 | 13.9261 | 13.9261 | -0.49376 | 14.0462 | 14.0462 | 14.0462 | -0.96832 | 14.1835 | 14.1835 | 14.1835 | -1.4662 | 14.3323 | 14.3323 | 14.3323 | -1.9787 | 14.4938 | 14.4938 | 14.4938 | -2.5329 | 14.6676 | 14.6676 | 14.6676 | -3.0986 | 14.9895 | 14.9895 | 14.9895 | -4.6977 | 15.2932 | 15.2932 | 15.2932 | -6.1989 | 15.557 | 15.557 | 15.557 | -7.2119 | 15.7636 | 15.7636 | 15.7636 | -7.8605 | 13.5267 | 13.5267 | 13.5267 | 0.80617 | 13.6162 | 13.6162 | 13.6162 | 0.19946 | 13.7174 | 13.7174 | 13.7174 | -0.14274 | 13.798 | 13.798 | 13.798 | -0.63603 | 13.8937 | 13.8937 | 13.8937 | -1.0164 | 14.0063 | 14.0063 | 14.0063 | -1.5578 | 14.1382 | 14.1382 | 14.1382 | -2.1215 | 14.2799 | 14.2799 | 14.2799 | -2.6889 | 14.4285 | 14.4285 | 14.4285 | -3.2694 | 14.5941 | 14.5941 | 14.5941 | -3.9927 | 15.2577 | 15.2577 | 15.2577 | -6.5459 | 15.7646 | 15.7646 | 15.7646 | -7.7755 | 16.1209 | 16.1209 | 16.1209 | -8.001 | 16.365 | 16.365 | 16.365 | -7.4896 | 13.528 | 13.528 | 13.528 | 0.81583 | 13.6298 | 13.6298 | 13.6298 | 0.16363 | 13.7356 | 13.7356 | 13.7356 | -0.22273 | 13.8351 | 13.8351 | 13.8351 | -0.74786 | 13.9659 | 13.9659 | 13.9659 | -1.1856 | 14.1325 | 14.1325 | 14.1325 | -1.8113 | 14.3418 | 14.3418 | 14.3418 | -2.4961 | 14.5786 | 14.5786 | 14.5786 | -3.1847 | 14.839 | 14.839 | 14.839 | -3.8106 | 15.13 | 15.13 | 15.13 | -4.4438 | 16.2279 | 16.2279 | 16.2279 | -7.0607 | 17.1233 | 17.1233 | 17.1233 | -10.1836 | 17.5489 | 17.5489 | 17.5489 | -11.6755 | 17.7533 | 17.7533 | 17.7533 | -12.8721 | 13.5533 | 13.5533 | 13.5533 | 0.72103 | 13.6834 | 13.6834 | 13.6834 | -0.014297 | 13.7562 | 13.7562 | 13.7562 | -0.39959 | 13.8524 | 13.8524 | 13.8524 | -0.91406 | 13.9803 | 13.9803 | 13.9803 | -1.3581 | 14.1406 | 14.1406 | 14.1406 | -1.9475 | 14.3488 | 14.3488 | 14.3488 | -2.5623 | 14.5776 | 14.5776 | 14.5776 | -3.1453 | 14.8238 | 14.8238 | 14.8238 | -3.6422 | 15.113 | 15.113 | 15.113 | -4.5557 | 16.1855 | 16.1855 | 16.1855 | -8.646 | 16.8676 | 16.8676 | 16.8676 | -11.1281 | 17.0506 | 17.0506 | 17.0506 | -11.9466 | 17.0018 | 17.0018 | 17.0018 | -11.2689
GATLEY | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 23.717 | 23.717 | 18.7401 | 11.927 | 23.7743 | 23.7743 | 18.7076 | 11.7312 | 23.7982 | 23.7982 | 18.6882 | 11.6487 | 23.8439 | 23.8439 | 18.6628 | 11.569 | 23.9036 | 23.9036 | 18.5968 | 11.3901 | 23.9739 | 23.9739 | 18.5347 | 11.1697 | 24.0498 | 24.0498 | 18.4356 | 10.8887 | 24.1307 | 24.1307 | 18.3917 | 10.7325 | 24.2164 | 24.2164 | 18.3296 | 10.5059 | 24.3162 | 24.3162 | 18.261 | 10.257 | 24.7612 | 24.6688 | 17.9956 | 9.4036 | 25.1274 | 24.438 | 17.8272 | 8.9852 | 25.364 | 24.4519 | 17.8373 | 8.9188 | 25.5342 | 24.2651 | 17.7011 | 8.9925 | 23.6756 | 23.6756 | 18.7415 | 12.0172 | 23.6986 | 23.6986 | 18.7247 | 11.8944 | 23.7425 | 23.7425 | 18.6892 | 11.7612 | 23.7895 | 23.7895 | 18.677 | 11.674 | 23.8486 | 23.8486 | 18.639 | 11.5053 | 23.9127 | 23.9127 | 18.611 | 11.3026 | 23.982 | 23.982 | 18.5665 | 11.0363 | 24.0529 | 24.0529 | 18.5391 | 10.8863 | 24.1271 | 24.1271 | 18.5014 | 10.6716 | 24.2037 | 24.2037 | 18.4559 | 10.452 | 24.448 | 24.448 | 18.3029 | 9.765 | 24.6544 | 24.6544 | 18.1149 | 9.3024 | 24.7981 | 24.7981 | 18.1315 | 9.0663 | 24.9056 | 24.8304 | 18.1134 | 8.9269 | 23.717 | 23.717 | 18.7408 | 11.9368 | 23.7743 | 23.7743 | 18.7208 | 11.7502 | 23.7983 | 23.7983 | 18.6863 | 11.6762 | 23.8441 | 23.8441 | 18.6534 | 11.6026 | 23.9038 | 23.9038 | 18.6057 | 11.4329 | 23.9738 | 23.9738 | 18.5496 | 11.2221 | 24.0495 | 24.0495 | 18.4954 | 10.951 | 24.1304 | 24.1304 | 18.4512 | 10.8026 | 24.2151 | 24.2151 | 18.3874 | 10.588 | 24.3112 | 24.3112 | 18.3289 | 10.3626 | 24.7323 | 24.7323 | 18.1591 | 9.593 | 25.0597 | 24.7148 | 18.0291 | 9.2367 | 25.2758 | 24.6543 | 17.9849 | 9.1891 | 25.4196 | 24.5577 | 17.9145 | 9.2749 | 23.7147 | 23.7147 | 18.7399 | 11.9357 | 23.7747 | 23.7747 | 18.7045 | 11.7503 | 23.8121 | 23.8121 | 18.68 | 11.6789 | 23.8754 | 23.8754 | 18.6518 | 11.6082 | 23.9571 | 23.9571 | 18.5758 | 11.449 | 24.0659 | 24.0659 | 18.5046 | 11.2495 | 24.1964 | 24.1964 | 18.4144 | 10.9836 | 24.3455 | 24.3455 | 18.3666 | 10.8399 | 24.4998 | 24.4998 | 18.2938 | 10.6579 | 24.6703 | 24.6703 | 18.2144 | 10.4748 | 25.4576 | 24.5606 | 17.9166 | 9.3792 | 25.7582 | 24.0004 | 17.5079 | 7.0921 | 25.8885 | 23.5514 | 17.1804 | 5.3331 | 25.9159 | 23.2025 | 16.9259 | 4.0706 | 23.7097 | 23.7097 | 18.7405 | 11.9408 | 23.773 | 23.773 | 18.6966 | 11.7453 | 23.8109 | 23.8109 | 18.6693 | 11.6812 | 23.8633 | 23.8633 | 18.6248 | 11.6365 | 23.94 | 23.94 | 18.5352 | 11.5082 | 24.0411 | 24.0411 | 18.4698 | 11.3485 | 24.1656 | 24.1656 | 18.3874 | 11.1186 | 24.3056 | 24.3056 | 18.3204 | 11.0146 | 24.4752 | 24.4752 | 18.2111 | 10.8154 | 24.81 | 24.7961 | 18.0884 | 10.2594 | 25.4507 | 24.2267 | 17.673 | 7.6481 | 25.6604 | 23.8195 | 17.376 | 5.5856 | 25.6883 | 23.4856 | 17.1325 | 4.4235 | 25.5764 | 23.4245 | 17.0879 | 4.7752
GIDLOW | WIGAN | WASHWAY FARM / KIRKBY | 357620 | 406662 | 32.251 | 13.7035 | 9.9965 | 11.1116 | 32.3476 | 12.9681 | 9.46 | 10.7689 | 32.4034 | 12.3048 | 8.9762 | 10.4511 | 32.4812 | 11.7341 | 8.5599 | 10.0526 | 32.5882 | 11.2141 | 8.1805 | 9.5514 | 32.7199 | 10.7047 | 7.8089 | 8.9811 | 32.8671 | 10.5468 | 7.6937 | 8.3853 | 33.0261 | 10.3745 | 7.5681 | 7.7565 | 33.1955 | 10.1761 | 7.4233 | 7.1231 | 33.3813 | 9.9275 | 7.242 | 6.3805 | 34.088 | 9.3843 | 6.8457 | 3.8814 | 34.5832 | 9.6184 | 7.0165 | 2.6396 | 34.8741 | 10.7507 | 7.8425 | 2.3461 | 35.048 | 11.0482 | 8.0595 | 2.5805 | 32.2204 | 13.7229 | 10.0107 | 11.191 | 32.2842 | 12.9174 | 9.4231 | 10.9104 | 32.3683 | 12.3877 | 9.0367 | 10.5302 | 32.472 | 11.7859 | 8.5977 | 10.1521 | 32.5905 | 11.1357 | 8.1234 | 9.7059 | 32.7228 | 10.6386 | 7.7607 | 9.192 | 32.8693 | 10.5268 | 7.6791 | 8.6503 | 33.0267 | 10.4022 | 7.5882 | 8.0744 | 33.1953 | 10.2747 | 7.4952 | 7.4842 | 33.373 | 10.1446 | 7.4003 | 6.872 | 33.6967 | 9.8262 | 7.1681 | 5.132 | 33.9395 | 9.9716 | 7.2741 | 3.8532 | 34.0924 | 10.605 | 7.7362 | 3.0841 | 34.1809 | 10.6473 | 7.7671 | 2.5845 | 32.251 | 13.7198 | 10.0084 | 11.1228 | 32.3476 | 12.9144 | 9.4209 | 10.805 | 32.4034 | 12.3674 | 9.0218 | 10.5078 | 32.4812 | 11.7335 | 8.5594 | 10.1249 | 32.5877 | 10.9271 | 7.9712 | 9.6433 | 32.7187 | 10.5864 | 7.7226 | 9.0941 | 32.8651 | 10.4419 | 7.6172 | 8.5186 | 33.0237 | 10.2884 | 7.5053 | 7.9097 | 33.1907 | 10.1261 | 7.3869 | 7.3064 | 33.367 | 9.9717 | 7.2742 | 6.634 | 34.0294 | 9.4999 | 6.93 | 4.3082 | 34.4872 | 9.8243 | 7.1667 | 3.2021 | 34.7581 | 11.1346 | 8.1226 | 3.0052 | 34.9252 | 11.348 | 8.2782 | 3.2073 | 32.2467 | 13.7017 | 9.9952 | 11.1141 | 32.3463 | 12.9624 | 9.4559 | 10.7747 | 32.4036 | 12.2879 | 8.9639 | 10.4703 | 32.5015 | 11.7275 | 8.5551 | 10.0893 | 32.6421 | 11.1875 | 8.1611 | 9.6314 | 32.8221 | 10.6791 | 7.7903 | 9.1081 | 33.0362 | 10.4956 | 7.6564 | 8.5368 | 33.2784 | 10.275 | 7.4955 | 7.9426 | 33.545 | 10.1006 | 7.3682 | 7.4237 | 33.8408 | 9.9671 | 7.2709 | 6.8935 | 34.804 | 9.092 | 6.6325 | 3.7218 | 35.5933 | 8.2004 | 5.9821 | -2.7747 | 36.031 | 8.2972 | 6.0527 | -7.7762 | 36.2722 | 7.8118 | 5.6986 | -11.1396 | 32.2336 | 13.7967 | 10.0645 | 11.1476 | 32.3395 | 13.7054 | 9.9979 | 10.7897 | 32.3848 | 13.5887 | 9.9128 | 10.4958 | 32.4691 | 13.4717 | 9.8274 | 10.1709 | 32.595 | 13.2943 | 9.698 | 9.7587 | 32.7506 | 13.0685 | 9.5333 | 9.3206 | 32.9415 | 12.8834 | 9.3983 | 8.8499 | 33.1497 | 12.7688 | 9.3147 | 8.3773 | 33.3852 | 12.5823 | 9.1786 | 7.79 | 33.6855 | 12.2397 | 8.9287 | 6.1819 | 34.6551 | 10.7895 | 7.8708 | -1.183 | 35.2027 | 9.1725 | 6.6912 | -6.9895 | 35.3668 | 8.2804 | 6.0405 | -10.2569 | 35.245 | 8.2392 | 6.0104 | -9.2259
GILLSROW | PENRITH & SHAP | HARKER / HUTTON | 337117 | 526444 | 8.1197 | 8.1197 | 8.1197 | 2.7313 | 8.1647 | 8.1647 | 8.1647 | 2.5827 | 8.2063 | 8.2063 | 8.2063 | 2.5018 | 8.2605 | 8.2605 | 8.2605 | 2.3983 | 8.3276 | 8.3276 | 8.3276 | 2.2299 | 8.4077 | 8.4077 | 8.4077 | 2.1105 | 8.5052 | 8.5052 | 8.5052 | 1.9829 | 8.5498 | 8.5498 | 8.5498 | 1.825 | 8.597 | 8.597 | 8.597 | 1.6513 | 8.6622 | 8.6622 | 8.6622 | 1.4635 | 8.8938 | 8.8938 | 8.8938 | 0.76993 | 9.0255 | 9.0255 | 9.0255 | 0.24229 | 9.0727 | 9.0727 | 9.0727 | -0.10293 | 9.0727 | 9.0727 | 9.0727 | 0.054604 | 8.1033 | 8.1033 | 8.1033 | 2.7905 | 8.1355 | 8.1355 | 8.1355 | 2.6911 | 8.1849 | 8.1849 | 8.1849 | 2.5929 | 8.2379 | 8.2379 | 8.2379 | 2.485 | 8.2971 | 8.2971 | 8.2971 | 2.3169 | 8.3647 | 8.3647 | 8.3647 | 2.1965 | 8.4456 | 8.4456 | 8.4456 | 2.0689 | 8.518 | 8.518 | 8.518 | 1.9068 | 8.5844 | 8.5844 | 8.5844 | 1.7308 | 8.6528 | 8.6528 | 8.6528 | 1.5709 | 8.784 | 8.784 | 8.784 | 1.1354 | 8.8944 | 8.8944 | 8.8944 | 0.72202 | 8.9778 | 8.9778 | 8.9778 | 0.0451 | 9.0114 | 9.0114 | 9.0114 | -0.38344 | 8.1197 | 8.1197 | 8.1197 | 2.7351 | 8.1647 | 8.1647 | 8.1647 | 2.5905 | 8.2063 | 8.2063 | 8.2063 | 2.5133 | 8.2605 | 8.2605 | 8.2605 | 2.414 | 8.3272 | 8.3272 | 8.3272 | 2.2518 | 8.4066 | 8.4066 | 8.4066 | 2.1378 | 8.5038 | 8.5038 | 8.5038 | 2.0151 | 8.5493 | 8.5493 | 8.5493 | 1.8628 | 8.5959 | 8.5959 | 8.5959 | 1.6974 | 8.6589 | 8.6589 | 8.6589 | 1.5263 | 8.8791 | 8.8791 | 8.8791 | 0.87592 | 9.0031 | 9.0031 | 9.0031 | 0.56065 | 9.0463 | 9.0463 | 9.0463 | 0.30738 | 9.0453 | 9.0453 | 9.0453 | 0.46118 | 8.1184 | 8.1184 | 8.1184 | 2.7381 | 8.1645 | 8.1645 | 8.1645 | 2.5964 | 8.2125 | 8.2125 | 8.2125 | 2.5284 | 8.2813 | 8.2813 | 8.2813 | 2.435 | 8.3723 | 8.3723 | 8.3723 | 2.2736 | 8.4862 | 8.4862 | 8.4862 | 2.1631 | 8.58 | 8.58 | 8.58 | 2.0459 | 8.6538 | 8.6538 | 8.6538 | 1.9074 | 8.7332 | 8.7332 | 8.7332 | 1.7744 | 8.8201 | 8.8201 | 8.8201 | 1.5861 | 9.0402 | 9.0402 | 9.0402 | 0.7986 | 9.1378 | 9.1378 | 9.1378 | 0.174 | 9.1369 | 9.1369 | 9.1369 | -0.095011 | 9.1033 | 9.1033 | 9.1033 | -0.17987 | 8.1372 | 8.1372 | 8.1372 | 2.7059 | 8.2016 | 8.2016 | 8.2016 | 2.5412 | 8.2533 | 8.2533 | 8.2533 | 2.4783 | 8.3204 | 8.3204 | 8.3204 | 2.3969 | 8.4105 | 8.4105 | 8.4105 | 2.2379 | 8.5039 | 8.5039 | 8.5039 | 2.1409 | 8.5707 | 8.5707 | 8.5707 | 2.0367 | 8.6364 | 8.6364 | 8.6364 | 1.9286 | 8.7 | 8.7 | 8.7 | 1.8021 | 8.7741 | 8.7741 | 8.7741 | 1.5567 | 8.9354 | 8.9354 | 8.9354 | 0.53831 | 8.9805 | 8.9805 | 8.9805 | 0.012629 | 8.9366 | 8.9366 | 8.9366 | -0.1421 | 8.8708 | 8.8708 | 8.8708 | 0.051005
GLAXO | ULVERSTON | HARKER / HUTTON | 330458 | 477825 | 15.7254 | 2.5891 | 1.8608 | 15.7254 | 15.3174 | 2.5219 | 1.8125 | 15.3174 | 14.5981 | 2.4035 | 1.7274 | 14.5981 | 14.366 | 2.3653 | 1.7 | 14.366 | 13.9189 | 2.2916 | 1.647 | 13.9189 | 13.1905 | 2.1717 | 1.5609 | 13.1905 | 12.5564 | 2.0673 | 1.4858 | 12.5564 | 12.0291 | 1.9805 | 1.4234 | 12.0291 | 11.6385 | 1.9162 | 1.3772 | 11.6385 | 11.0911 | 1.8261 | 1.3124 | 11.0911 | 7.1801 | 1.1821 | 0.84963 | 7.1801 | 4.297 | 0.70747 | 0.50848 | 4.297 | 19.6239 | 3.2309 | 2.3221 | 11.622 | 27.6419 | 6.362 | 4.5725 | 11.75 | 15.9527 | 2.6265 | 1.8877 | 15.9527 | 15.6735 | 2.5805 | 1.8547 | 15.6735 | 15.2053 | 2.5034 | 1.7993 | 15.2053 | 14.6522 | 2.4124 | 1.7338 | 14.6522 | 14.3597 | 2.3642 | 1.6992 | 14.3597 | 13.8828 | 2.2857 | 1.6428 | 13.8828 | 13.4219 | 2.2098 | 1.5882 | 13.4219 | 12.9803 | 2.1371 | 1.536 | 12.9803 | 12.5769 | 2.0707 | 1.4882 | 12.5769 | 12.096 | 1.9915 | 1.4313 | 12.096 | 11.2965 | 1.8599 | 1.3367 | 11.2965 | 10.1565 | 1.6722 | 1.2018 | 10.1565 | 21.1189 | 4.2057 | 3.0227 | 18.0671 | 21.1117 | 6.6616 | 4.7878 | 18.1516 | 15.9409 | 2.6246 | 1.8863 | 15.9409 | 15.53 | 2.5569 | 1.8377 | 15.53 | 14.912 | 2.4551 | 1.7646 | 14.912 | 14.2136 | 2.3402 | 1.6819 | 14.2136 | 13.589 | 2.2373 | 1.608 | 13.589 | 12.7416 | 2.0978 | 1.5077 | 12.7416 | 12.3736 | 2.0372 | 1.4642 | 12.3736 | 11.9374 | 1.9654 | 1.4126 | 11.9374 | 11.4763 | 1.8895 | 1.358 | 11.4763 | 10.6821 | 1.7587 | 1.264 | 10.6821 | 10.2105 | 1.6811 | 1.2082 | 10.2105 | 9.4325 | 1.553 | 1.1162 | 9.4325 | 27.6104 | 4.5969 | 3.3039 | 11.6649 | 27.5995 | 7.6246 | 5.48 | 11.8016 | 15.7362 | 2.5908 | 1.8621 | 15.7362 | 15.2553 | 2.5117 | 1.8052 | 15.2553 | 14.7548 | 2.4293 | 1.746 | 14.7548 | 14.2668 | 2.3489 | 1.6882 | 14.2668 | 13.6801 | 2.2523 | 1.6188 | 13.6801 | 12.8864 | 2.1216 | 1.5249 | 12.8864 | 12.3566 | 2.0344 | 1.4622 | 12.3566 | 11.7928 | 1.9416 | 1.3955 | 11.7928 | 11.1904 | 1.8424 | 1.3242 | 11.1904 | 10.6775 | 1.758 | 1.2635 | 10.6775 | 0.98824 | 0.16271 | 0.11694 | 0.98824 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 16.6177 | 2.736 | 1.9664 | 10.7953 | 28.5556 | 5.791 | 4.1621 | 10.9319 | 15.7394 | 2.5914 | 1.8625 | 15.7394 | 15.3325 | 2.5244 | 1.8143 | 15.3325 | 14.7035 | 2.4208 | 1.7399 | 14.7035 | 14.1296 | 2.3263 | 1.672 | 14.1296 | 13.5129 | 2.2248 | 1.599 | 13.5129 | 12.6898 | 2.0893 | 1.5016 | 12.6898 | 12.0673 | 1.9868 | 1.4279 | 12.0673 | 10.5319 | 1.734 | 1.2463 | 10.5319 | 8.1644 | 1.3442 | 0.96611 | 8.1644 | 2.8991 | 0.47732 | 0.34306 | 2.8991 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.2291 | 0.20237 | 0.14545 | 1.2291 | 28.5806 | 5.7735 | 4.1495 | 10.7198 | 28.5192 | 5.7612 | 4.1407 | 10.9622
GLOSSOP | HYDE | STALYBRIDGE | 402300 | 394074 | 31.0528 | 15.0795 | 10.8379 | 13.4709 | 31.1265 | 15.3353 | 11.0218 | 13.165 | 31.1653 | 15.3559 | 11.0366 | 12.9181 | 31.2293 | 15.212 | 10.9331 | 12.5868 | 31.3158 | 14.9067 | 10.7137 | 12.3467 | 31.4236 | 14.9776 | 10.7647 | 11.9961 | 31.5462 | 14.9729 | 10.7613 | 11.5312 | 31.6796 | 14.8358 | 10.6628 | 11.1539 | 31.8223 | 14.7822 | 10.6242 | 10.7279 | 31.9787 | 14.6012 | 10.4942 | 10.2195 | 32.6175 | 13.9906 | 10.0553 | 8.4812 | 33.1118 | 13.3784 | 9.6153 | 7.508 | 33.4573 | 13.5123 | 9.7116 | 7.1672 | 33.7595 | 13.2519 | 9.5244 | 7.2084 | 31.0082 | 15.1838 | 10.9129 | 13.5981 | 31.0462 | 15.6165 | 11.2239 | 13.3952 | 31.1124 | 15.5751 | 11.1941 | 13.0643 | 31.188 | 15.4551 | 11.1079 | 12.7216 | 31.2734 | 15.3142 | 11.0066 | 12.4929 | 31.3688 | 15.14 | 10.8814 | 12.1627 | 31.475 | 15.0435 | 10.8121 | 11.713 | 31.5882 | 14.9368 | 10.7354 | 11.3477 | 31.7083 | 14.8213 | 10.6523 | 10.9229 | 31.833 | 14.703 | 10.5674 | 10.4713 | 32.1595 | 13.9887 | 10.0539 | 9.1919 | 32.4401 | 13.7865 | 9.9086 | 8.2619 | 32.6713 | 13.816 | 9.9299 | 7.6928 | 32.8486 | 14.047 | 10.0959 | 7.3827 | 31.0529 | 15.2228 | 10.9409 | 13.4779 | 31.1267 | 15.6159 | 11.2235 | 13.1857 | 31.1656 | 15.5541 | 11.179 | 12.9532 | 31.2299 | 15.3962 | 11.0655 | 12.6361 | 31.3164 | 15.239 | 10.9526 | 12.4123 | 31.4239 | 14.9368 | 10.7354 | 12.0791 | 31.5462 | 14.7222 | 10.5811 | 11.6325 | 31.6794 | 14.4033 | 10.3519 | 11.2719 | 31.8204 | 14.385 | 10.3388 | 10.8693 | 31.9692 | 14.2795 | 10.2629 | 10.4083 | 32.5636 | 13.9865 | 10.0524 | 8.8406 | 32.9584 | 13.9669 | 10.0383 | 8.0174 | 33.2529 | 13.9524 | 10.0278 | 7.7369 | 33.4756 | 13.6301 | 9.7962 | 7.8191 | 31.0494 | 15.0932 | 10.8478 | 13.4807 | 31.1246 | 15.3522 | 11.0339 | 13.1825 | 31.1745 | 15.3531 | 11.0346 | 12.9471 | 31.2605 | 15.182 | 10.9116 | 12.6283 | 31.3818 | 14.5654 | 10.4685 | 12.416 | 31.5412 | 15.0215 | 10.7962 | 12.0956 | 31.7356 | 14.938 | 10.7362 | 11.6543 | 31.9594 | 14.7764 | 10.6201 | 11.3015 | 32.2027 | 14.7171 | 10.5775 | 10.951 | 32.4238 | 14.5739 | 10.4745 | 10.5747 | 33.3006 | 13.3517 | 9.5961 | 8.1046 | 34.1639 | 12.3534 | 8.8786 | 2.8526 | 34.7058 | 11.3502 | 8.1576 | -1.3153 | 34.9934 | 10.8329 | 7.7858 | -3.9746 | 31.0419 | 15.0997 | 10.8524 | 13.5098 | 31.1221 | 15.3056 | 11.0004 | 13.212 | 31.1749 | 15.3279 | 11.0165 | 12.9974 | 31.2551 | 15.2489 | 10.9597 | 12.7322 | 31.3695 | 15.0407 | 10.8101 | 12.5759 | 31.5186 | 14.9153 | 10.7199 | 12.3278 | 31.7089 | 14.9229 | 10.7254 | 11.9543 | 31.9173 | 14.8487 | 10.6721 | 11.6761 | 32.1132 | 14.7085 | 10.5713 | 11.2318 | 32.3684 | 14.4516 | 10.3867 | 9.9676 | 33.3556 | 13.0913 | 9.409 | 4.0997 | 34.0449 | 11.8744 | 8.5344 | -0.63396 | 34.3293 | 11.0074 | 7.9112 | -3.3775 | 34.2831 | 11.0327 | 7.9294 | -2.5391
GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 29.1559 | 4.8003 | 3.4501 | 8.6311 | 13.4052 | 2.2071 | 1.5863 | 6.9765 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.554 | 2.6844 | 0.44197 | 0.31765 | 0.54411 | 2.6844 | 0.44197 | 0.31765 | -0.98385 | 2.6844 | 0.44197 | 0.31765 | -2.4178 | 2.6844 | 0.44197 | 0.31765 | -6.1438 | 2.6844 | 0.44197 | 0.31765 | -8.5306 | 4.9945 | 0.8223 | 0.591 | -9.2911 | 13.242 | 2.1802 | 1.5669 | -9.4311 | 29.8247 | 4.9104 | 3.5292 | 9.4658 | 14.9521 | 2.4617 | 1.7693 | 8.5769 | 0.23818 | 0.039215 | 0.028184 | 0.23818 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.1995 | 2.6844 | 0.44197 | 0.31765 | -0.4932 | 2.6844 | 0.44197 | 0.31765 | -2.5595 | 2.6844 | 0.44197 | 0.31765 | -3.8495 | 2.6844 | 0.44197 | 0.31765 | -4.4894 | 29.8008 | 4.9065 | 3.5264 | 8.6404 | 14.8487 | 2.4447 | 1.7571 | 7.0082 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.7232 | 2.6844 | 0.44197 | 0.31765 | 0.67159 | 2.6844 | 0.44197 | 0.31765 | -0.817 | 2.6844 | 0.44197 | 0.31765 | -2.1558 | 2.6844 | 0.44197 | 0.31765 | -5.4681 | 2.6844 | 0.44197 | 0.31765 | -7.282 | 12.3408 | 2.0318 | 1.4603 | -7.8057 | 20.291 | 3.3408 | 2.4011 | -7.6036 | 29.1711 | 4.8028 | 3.4519 | 8.6665 | 13.3961 | 2.2056 | 1.5852 | 7.0597 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.1962 | 2.6844 | 0.44197 | 0.31765 | 1.3734 | 2.6844 | 0.44197 | 0.31765 | 0.18616 | 2.6844 | 0.44197 | 0.31765 | -0.85854 | 2.6844 | 0.44197 | 0.31765 | -5.7275 | 2.6844 | 0.44197 | 0.31765 | -14.3522 | 2.6844 | 0.44197 | 0.31765 | -20.672 | 2.6844 | 0.44197 | 0.31765 | -24.5623 | 29.1775 | 4.8039 | 3.4526 | 8.6707 | 25.555 | 4.2074 | 3.024 | 7.0086 | 23.3498 | 3.8444 | 2.763 | 6.4115 | 20.6212 | 3.3951 | 2.4401 | 5.5715 | 18.3764 | 3.0255 | 2.1745 | 5.1787 | 16.3972 | 2.6997 | 1.9403 | 3.7728 | 14.5355 | 2.3932 | 1.72 | 2.4367 | 13.5022 | 2.223 | 1.5977 | 1.7016 | 11.7885 | 1.9409 | 1.395 | 0.28398 | 9.1865 | 1.5125 | 1.0871 | -2.1119 | 14.0301 | 2.3099 | 1.6602 | -11.7288 | 1.5987 | 0.26321 | 0.18917 | -19.4964 | 2.6844 | 0.44197 | 0.31765 | -23.7365 | 2.6844 | 0.44197 | 0.31765 | -22.1408
GOWHOLE | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 30.6489 | 10.961 | 7.8779 | 9.8912 | 30.7615 | 10.8167 | 7.7742 | 9.3237 | 30.8419 | 10.5295 | 7.5678 | 8.7289 | 30.9565 | 10.392 | 7.4689 | 8.0399 | 31.0981 | 10.3191 | 7.4165 | 7.4071 | 31.2676 | 10.1112 | 7.2671 | 6.6376 | 31.4613 | 9.903 | 7.1175 | 5.7184 | 31.6709 | 9.6735 | 6.9526 | 4.8466 | 31.8922 | 9.5254 | 6.8461 | 3.9662 | 32.1516 | 9.3164 | 6.6959 | 2.8478 | 33.2611 | 8.3878 | 6.0284 | -0.99775 | 34.1647 | 7.7904 | 5.5991 | -2.833 | 34.7443 | 7.5471 | 5.4242 | -3.1189 | 35.1614 | 7.5482 | 5.4251 | -2.5512 | 30.6104 | 10.9753 | 7.8881 | 10.0247 | 30.6939 | 10.7954 | 7.7588 | 9.5831 | 30.8145 | 10.7183 | 7.7035 | 8.9771 | 30.9375 | 10.5687 | 7.596 | 8.4469 | 31.078 | 10.4001 | 7.4747 | 7.9953 | 31.2373 | 10.181 | 7.3173 | 7.4068 | 31.4169 | 10.0693 | 7.237 | 6.6808 | 31.6102 | 9.953 | 7.1534 | 5.999 | 31.8177 | 9.8288 | 7.0641 | 5.2529 | 32.0366 | 9.7001 | 6.9716 | 4.4799 | 32.552 | 9.3336 | 6.7083 | 2.1639 | 33.014 | 8.9671 | 6.4449 | 0.51027 | 33.3753 | 9.0203 | 6.483 | -0.47242 | 33.6465 | 8.98 | 6.4541 | -0.99916 | 30.6493 | 10.9848 | 7.895 | 9.8929 | 30.7621 | 10.7496 | 7.726 | 9.3487 | 30.8428 | 10.6976 | 7.6886 | 8.7805 | 30.9577 | 10.5549 | 7.586 | 8.122 | 31.099 | 10.4148 | 7.4853 | 7.5217 | 31.2677 | 10.25 | 7.3669 | 6.7864 | 31.4606 | 10.1113 | 7.2672 | 5.902 | 31.6695 | 9.9674 | 7.1638 | 5.0622 | 31.8877 | 9.8011 | 7.0442 | 4.2244 | 32.1354 | 9.6259 | 6.9183 | 3.2118 | 33.1672 | 9.0402 | 6.4974 | -0.2453 | 33.9357 | 8.7899 | 6.3175 | -1.8008 | 34.4392 | 8.689 | 6.245 | -2.0047 | 34.7625 | 8.4336 | 6.0614 | -1.4333 | 30.6458 | 10.9624 | 7.8789 | 9.9017 | 30.7686 | 10.8107 | 7.7698 | 9.3167 | 30.8763 | 10.4618 | 7.5191 | 8.7188 | 31.0334 | 10.3911 | 7.4683 | 8.0595 | 31.2402 | 10.2817 | 7.3896 | 7.4514 | 31.5054 | 10.0544 | 7.2263 | 6.6898 | 31.8339 | 9.8027 | 7.0454 | 5.7475 | 32.2093 | 9.6262 | 6.9186 | 4.8509 | 32.6072 | 9.4463 | 6.7892 | 4.0564 | 33.0389 | 9.2487 | 6.6472 | 3.2308 | 34.5095 | 8.1025 | 5.8234 | -0.67785 | 35.7555 | 6.6482 | 4.7782 | -6.9964 | 34.6432 | 5.7037 | 4.0994 | -10.9991 | 30.6603 | 5.048 | 3.6281 | -13.7899 | 30.6408 | 10.953 | 7.8721 | 9.8346 | 30.7734 | 10.7456 | 7.7231 | 9.1469 | 30.879 | 10.8455 | 7.7949 | 8.5619 | 31.0208 | 10.6852 | 7.6797 | 7.9628 | 31.2105 | 10.4637 | 7.5205 | 7.4238 | 31.4493 | 10.1561 | 7.2994 | 6.784 | 31.7522 | 9.8275 | 7.0632 | 5.9858 | 32.0886 | 9.5648 | 6.8744 | 5.2847 | 32.4607 | 9.4881 | 6.8193 | 4.5976 | 32.9067 | 9.1311 | 6.5627 | 2.9647 | 34.3776 | 7.3829 | 5.3063 | -4.4741 | 35.2977 | 5.9887 | 4.3042 | -9.5999 | 32.2459 | 5.309 | 3.8157 | -12.0169 | 32.7384 | 5.3901 | 3.874 | -10.752
GRANE RD & PRINNY HILL | ROSSENDALE | PADIHAM | 378312 | 422726 | 25.5536 | 8.5308 | 6.2231 | 14.3062 | 25.6309 | 8.4416 | 6.158 | 14.0753 | 25.6473 | 8.3441 | 6.0869 | 13.9769 | 25.6866 | 8.1367 | 5.9356 | 13.8203 | 25.7423 | 7.9727 | 5.816 | 13.6234 | 25.8136 | 7.6275 | 5.5642 | 13.3916 | 25.8922 | 7.7568 | 5.6585 | 13.1387 | 25.976 | 7.7878 | 5.6811 | 12.8814 | 26.0613 | 7.8189 | 5.7038 | 12.6122 | 26.1398 | 7.8057 | 5.6941 | 12.3222 | 26.44 | 7.5929 | 5.5389 | 11.4347 | 26.6367 | 7.3562 | 5.3663 | 11.1553 | 26.7342 | 7.644 | 5.5762 | 11.276 | 26.7751 | 7.5131 | 5.4807 | 11.5312 | 25.4811 | 8.5869 | 6.264 | 14.5005 | 25.4979 | 8.464 | 6.1744 | 14.4322 | 25.5417 | 8.2511 | 6.019 | 14.2722 | 25.5972 | 8.143 | 5.9402 | 14.088 | 25.6585 | 8.0658 | 5.8839 | 13.8968 | 25.7239 | 7.9928 | 5.8307 | 13.6849 | 25.7953 | 7.9645 | 5.81 | 13.4496 | 25.8702 | 7.91 | 5.7702 | 13.2072 | 25.9484 | 7.8609 | 5.7344 | 12.9583 | 26.0292 | 7.8075 | 5.6954 | 12.7124 | 26.189 | 7.6324 | 5.5678 | 12.0346 | 26.2963 | 7.5825 | 5.5313 | 11.6062 | 26.3484 | 7.8347 | 5.7153 | 11.4482 | 26.3531 | 8.0612 | 5.8805 | 11.4511 | 25.5536 | 8.5922 | 6.2679 | 14.3091 | 25.6309 | 8.4966 | 6.1981 | 14.082 | 25.6473 | 8.3154 | 6.0659 | 13.9876 | 25.6866 | 8.19 | 5.9745 | 13.8346 | 25.7421 | 8.1502 | 5.9454 | 13.6476 | 25.8129 | 7.9678 | 5.8124 | 13.4217 | 25.8912 | 7.966 | 5.8111 | 13.1745 | 25.9747 | 7.888 | 5.7542 | 12.9202 | 26.0592 | 7.7763 | 5.6727 | 12.6544 | 26.1335 | 7.6549 | 5.5841 | 12.3892 | 26.4138 | 7.3681 | 5.3749 | 11.58 | 26.5935 | 7.2317 | 5.2754 | 11.3418 | 26.682 | 7.6071 | 5.5492 | 11.4787 | 26.72 | 7.3847 | 5.387 | 11.7465 | 25.547 | 8.5287 | 6.2216 | 14.3233 | 25.6199 | 8.4302 | 6.1497 | 14.1159 | 25.6382 | 8.304 | 6.0577 | 14.0487 | 25.6855 | 8.1226 | 5.9253 | 13.9288 | 25.7565 | 7.8518 | 5.7278 | 13.7862 | 25.8512 | 7.8258 | 5.7088 | 13.6198 | 25.9544 | 7.8989 | 5.7621 | 13.4408 | 26.0572 | 7.9671 | 5.8119 | 13.2699 | 26.1694 | 7.9302 | 5.7849 | 13.1198 | 26.293 | 7.9337 | 5.7875 | 12.9791 | 26.6657 | 7.5251 | 5.4895 | 12.2856 | 26.8866 | 6.7624 | 4.9331 | 11.1655 | 26.9496 | 6.8549 | 5.0005 | 10.472 | 26.9345 | 6.5242 | 4.7593 | 10.0798 | 25.5489 | 8.5273 | 6.2205 | 14.306 | 25.6311 | 8.4134 | 6.1375 | 14.0643 | 25.6544 | 8.2558 | 6.0225 | 13.9888 | 25.7017 | 8.3251 | 6.073 | 13.8765 | 25.7718 | 8.4413 | 6.1578 | 13.7365 | 25.8607 | 8.414 | 6.1379 | 13.5941 | 25.9539 | 8.3788 | 6.1122 | 13.4383 | 26.047 | 8.3552 | 6.095 | 13.3007 | 26.1468 | 8.3517 | 6.0924 | 13.1627 | 26.2593 | 8.2768 | 6.0378 | 12.8422 | 26.5706 | 7.9876 | 5.8268 | 11.4485 | 26.6901 | 7.1778 | 5.2361 | 10.58 | 26.6563 | 6.7581 | 4.93 | 10.2451 | 26.5456 | 6.6278 | 4.8349 | 10.6275
GRANGE | ULVERSTON | HARKER / HUTTON | 340240 | 478314 | 21.2821 | 21.2821 | 19.7513 | 10.9337 | 21.3242 | 21.3242 | 19.7247 | 10.7952 | 21.3502 | 21.3502 | 19.6781 | 10.5957 | 21.3923 | 21.3923 | 19.6073 | 10.3237 | 21.4456 | 21.4456 | 19.5474 | 10.1363 | 21.5101 | 21.5101 | 19.4606 | 9.817 | 21.5843 | 21.5843 | 19.3667 | 9.4641 | 21.6643 | 21.6643 | 19.282 | 9.1913 | 21.7481 | 21.7481 | 19.1908 | 8.872 | 21.8423 | 21.8423 | 19.081 | 8.4157 | 22.1733 | 22.1733 | 18.4482 | 6.8764 | 22.3972 | 22.3972 | 18.4297 | 6.1272 | 22.5155 | 22.5155 | 18.5118 | 5.9646 | 22.5714 | 22.5714 | 18.4714 | 6.2308 | 21.2754 | 21.2754 | 20.5526 | 10.9382 | 21.3187 | 21.3187 | 20.6357 | 10.8029 | 21.3788 | 21.3788 | 20.6453 | 10.5758 | 21.4399 | 21.4399 | 20.5954 | 10.3535 | 21.5065 | 21.5065 | 20.5347 | 10.2133 | 21.5815 | 21.5815 | 20.4321 | 9.9348 | 21.6666 | 21.6666 | 20.2631 | 9.6228 | 21.7592 | 21.7592 | 20.0059 | 9.403 | 21.8568 | 21.8568 | 19.5525 | 9.1179 | 21.9385 | 21.9385 | 18.6915 | 8.7847 | 22.0904 | 22.0904 | 20.2126 | 7.9665 | 22.205 | 22.205 | 20.1728 | 7.2936 | 22.2665 | 22.2665 | 20.1733 | 6.8562 | 22.2984 | 22.2984 | 20.1692 | 6.5733 | 21.2821 | 21.2821 | 20.5649 | 10.9397 | 21.3242 | 21.3242 | 20.6042 | 10.8126 | 21.3502 | 21.3502 | 20.5633 | 10.627 | 21.3923 | 21.3923 | 20.2361 | 10.3723 | 21.4454 | 21.4454 | 19.6494 | 10.2002 | 21.5096 | 21.5096 | 20.3908 | 9.8989 | 21.5835 | 21.5835 | 20.4595 | 9.5532 | 21.6633 | 21.6633 | 20.4559 | 9.2845 | 21.7462 | 21.7462 | 20.4178 | 8.9828 | 21.8365 | 21.8365 | 20.3638 | 8.5698 | 22.1487 | 22.1487 | 20.1763 | 7.1715 | 22.3564 | 22.3564 | 19.9992 | 6.5045 | 22.4662 | 22.4662 | 19.9377 | 6.362 | 22.5192 | 22.5192 | 19.8048 | 6.5994 | 21.2794 | 21.2794 | 19.7503 | 10.9327 | 21.3206 | 21.3206 | 19.7157 | 10.7739 | 21.3495 | 21.3495 | 19.6549 | 10.5553 | 21.3999 | 21.3999 | 19.5726 | 10.2704 | 21.4683 | 21.4683 | 19.4972 | 10.055 | 21.5555 | 21.5555 | 19.3905 | 9.6913 | 21.6624 | 21.6624 | 19.2694 | 9.2692 | 21.7835 | 21.7835 | 19.155 | 8.9416 | 21.9155 | 21.9155 | 19.0353 | 8.6243 | 22.0602 | 22.0602 | 18.8971 | 8.2594 | 22.4903 | 22.4903 | 18.0744 | 6.6557 | 22.7833 | 22.7833 | 17.8956 | 3.7594 | 22.9159 | 22.9159 | 17.6143 | 1.8008 | 22.9892 | 22.9892 | 17.2967 | 0.26612 | 21.27 | 21.27 | 19.7504 | 10.9349 | 21.3064 | 21.3064 | 19.7142 | 10.7626 | 21.3286 | 21.3286 | 19.644 | 10.5513 | 21.3686 | 21.3686 | 19.5491 | 10.2838 | 21.4257 | 21.4257 | 19.4588 | 10.0861 | 21.4972 | 21.4972 | 19.3378 | 9.7648 | 21.5884 | 21.5884 | 19.2153 | 9.4048 | 21.6882 | 21.6882 | 19.0924 | 9.1586 | 21.795 | 21.795 | 18.9531 | 8.8957 | 21.9292 | 21.9292 | 18.7591 | 8.1518 | 22.3524 | 22.3524 | 18.2603 | 4.7814 | 22.5658 | 22.5658 | 17.7503 | 2.3433 | 22.6084 | 22.6084 | 17.5092 | 1.0437 | 22.551 | 22.551 | 17.4518 | 1.4571
GREAT HARWOOD | HUNCOAT | PADIHAM | 373765 | 431955 | 6.4706 | 6.4706 | 6.4706 | 6.4706 | 6.5068 | 6.5068 | 6.5068 | 6.5068 | 6.5232 | 6.5232 | 6.5232 | 6.5232 | 6.5592 | 6.5592 | 5.3632 | 6.5592 | 6.6088 | 4.7735 | 3.4822 | 6.6088 | 6.6715 | 2.2603 | 1.6489 | 6.6715 | 6.7432 | 2.1959 | 1.6019 | 6.7432 | 6.8222 | 2.1271 | 1.5517 | 6.8222 | 6.9088 | 2.0334 | 1.4833 | 6.9088 | 7.0091 | 1.9145 | 1.3966 | 7.0091 | 7.4533 | 1.9517 | 1.4237 | 7.4533 | 7.8741 | 5.7062 | 4.1626 | 7.8741 | 8.1185 | 8.1185 | 8.1185 | 8.1185 | 8.2881 | 8.2881 | 8.2881 | 8.2881 | 6.4529 | 6.4529 | 6.4529 | 6.4529 | 6.4785 | 6.4785 | 6.4785 | 6.4785 | 6.5237 | 6.5237 | 6.5237 | 6.5237 | 6.5784 | 6.5784 | 5.4832 | 6.5784 | 6.6421 | 4.9625 | 3.6201 | 6.6421 | 6.715 | 2.3319 | 1.7011 | 6.715 | 6.7978 | 2.2535 | 1.6439 | 6.7978 | 6.8887 | 2.1548 | 1.5719 | 6.8887 | 6.9703 | 2.0529 | 1.4976 | 6.9703 | 7.0532 | 1.9163 | 1.3979 | 7.0532 | 7.2848 | 2.0612 | 1.5036 | 7.2848 | 7.4961 | 4.5302 | 3.3047 | 7.4961 | 7.6517 | 7.6517 | 6.4999 | 7.6517 | 7.7574 | 7.7574 | 7.3879 | 7.7574 | 6.4715 | 6.4715 | 6.4715 | 6.4715 | 6.508 | 6.508 | 6.508 | 6.508 | 6.5247 | 6.5247 | 6.5247 | 6.5247 | 6.5609 | 6.5609 | 5.4703 | 6.5609 | 6.6104 | 4.8291 | 3.5228 | 6.6104 | 6.6725 | 2.1375 | 1.5593 | 6.6725 | 6.7432 | 2.0121 | 1.4678 | 6.7432 | 6.821 | 1.9012 | 1.3869 | 6.821 | 6.9052 | 1.7831 | 1.3007 | 6.9052 | 6.9999 | 1.6383 | 1.1951 | 6.9999 | 7.4051 | 1.8568 | 1.3545 | 7.4051 | 7.7371 | 5.7883 | 4.2225 | 7.7371 | 7.9406 | 7.9406 | 7.9406 | 7.9406 | 8.0509 | 8.0509 | 8.0509 | 8.0509 | 6.4688 | 6.4688 | 6.4688 | 6.4688 | 6.5051 | 6.5051 | 6.5051 | 6.5051 | 6.5265 | 6.5265 | 6.5265 | 6.5265 | 6.5731 | 6.5731 | 5.3757 | 6.5731 | 6.6403 | 4.767 | 3.4775 | 6.6403 | 6.7326 | 2.271 | 1.6567 | 6.7326 | 6.8495 | 2.1804 | 1.5906 | 6.8495 | 6.9851 | 2.0403 | 1.4884 | 6.9851 | 7.1331 | 1.9632 | 1.4321 | 7.1331 | 7.2987 | 1.7884 | 1.3046 | 7.2987 | 7.9706 | 1.5647 | 1.1414 | 7.9706 | 8.7703 | 4.5841 | 3.3441 | 8.7703 | 9.1447 | 9.1447 | 7.7277 | 7.1933 | 9.3184 | 9.3184 | 8.4203 | 5.2851 | 6.4577 | 6.4577 | 6.4577 | 6.4577 | 6.489 | 6.489 | 6.489 | 6.489 | 6.5069 | 6.5069 | 6.5069 | 6.5069 | 6.5459 | 6.5459 | 6.5459 | 6.5459 | 6.6085 | 6.6085 | 6.6085 | 6.6085 | 6.6951 | 6.6951 | 6.6951 | 6.6951 | 6.8077 | 6.8077 | 6.8077 | 6.8077 | 6.938 | 6.938 | 6.938 | 6.938 | 7.1018 | 7.1018 | 7.1018 | 7.1018 | 7.3629 | 7.3629 | 7.3629 | 7.3629 | 8.1683 | 8.1683 | 8.1683 | 8.1683 | 8.6519 | 8.6519 | 8.6519 | 7.4981 | 8.8606 | 8.8606 | 8.5708 | 5.5692 | 8.8287 | 8.8287 | 8.5051 | 6.3421
GREEN LANE (ALTRINCHAM) | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 31.7477 | 15.7802 | 11.3416 | 11.0171 | 31.8287 | 15.6613 | 11.256 | 10.6441 | 31.8841 | 15.4893 | 11.1325 | 10.0287 | 31.9772 | 15.4073 | 11.0735 | 9.5464 | 32.0805 | 15.2914 | 10.9902 | 9.3324 | 32.2062 | 15.1273 | 10.8723 | 8.7086 | 32.345 | 14.939 | 10.737 | 8.0102 | 32.495 | 14.7952 | 10.6336 | 7.3946 | 32.6548 | 14.6049 | 10.4969 | 6.6828 | 32.8296 | 14.4155 | 10.3607 | 6.0069 | 33.5121 | 13.6337 | 9.7988 | 3.7603 | 34.0051 | 13.1904 | 9.4802 | 2.6919 | 34.3148 | 13.279 | 9.5439 | 2.7398 | 34.5116 | 13.377 | 9.6143 | 2.9935 | 31.7071 | 15.7902 | 11.3487 | 11.1725 | 31.7576 | 15.701 | 11.2846 | 10.9276 | 31.8414 | 15.5033 | 11.1426 | 10.2737 | 31.932 | 15.4249 | 11.0861 | 9.8518 | 32.0296 | 15.3705 | 11.047 | 9.7312 | 32.139 | 15.2558 | 10.9646 | 9.2067 | 32.2583 | 15.1234 | 10.8695 | 8.6033 | 32.3854 | 15.0024 | 10.7825 | 8.0769 | 32.5201 | 14.8608 | 10.6807 | 7.4449 | 32.6599 | 14.7464 | 10.5986 | 6.9122 | 32.9899 | 14.3679 | 10.3265 | 5.2406 | 33.2432 | 14.0642 | 10.1082 | 4.0229 | 33.4071 | 14.0449 | 10.0943 | 3.5418 | 33.5016 | 14.0537 | 10.1007 | 3.1382 | 31.7477 | 15.7883 | 11.3473 | 11.0252 | 31.8287 | 15.6897 | 11.2765 | 10.6657 | 31.8841 | 15.491 | 11.1337 | 10.0665 | 31.9772 | 15.3723 | 11.0484 | 9.5956 | 32.08 | 15.3133 | 11.006 | 9.394 | 32.2048 | 15.1611 | 10.8966 | 8.7873 | 32.3429 | 15.0246 | 10.7985 | 8.1055 | 32.4924 | 14.8994 | 10.7085 | 7.5041 | 32.6499 | 14.7409 | 10.5946 | 6.8186 | 32.815 | 14.5995 | 10.493 | 6.2092 | 33.4535 | 14.0518 | 10.0993 | 4.1784 | 33.9088 | 13.6062 | 9.7791 | 3.2352 | 34.1974 | 13.5614 | 9.7468 | 3.2678 | 34.3863 | 13.7049 | 9.85 | 3.4862 | 31.7443 | 15.7827 | 11.3434 | 11.0369 | 31.8295 | 15.6631 | 11.2574 | 10.694 | 31.9059 | 15.5048 | 11.1436 | 10.1289 | 32.0149 | 15.422 | 11.0841 | 9.703 | 32.1574 | 15.3144 | 11.0068 | 9.574 | 32.3382 | 15.1584 | 10.8947 | 9.0511 | 32.5495 | 14.9959 | 10.7779 | 8.4544 | 32.7885 | 14.837 | 10.6636 | 7.954 | 33.0517 | 14.6622 | 10.538 | 7.4383 | 33.3429 | 14.5242 | 10.4388 | 7.0315 | 34.2908 | 13.5861 | 9.7646 | 4.1692 | 35.1146 | 12.1066 | 8.7012 | -2.177 | 35.5923 | 11.2703 | 8.1002 | -6.9323 | 35.8201 | 10.6535 | 7.6569 | -10.3884 | 31.7496 | 15.7693 | 11.3337 | 10.9448 | 31.8578 | 15.6589 | 11.2544 | 10.4765 | 31.9295 | 15.5081 | 11.146 | 9.9167 | 32.0221 | 15.3679 | 11.0452 | 9.558 | 32.1508 | 15.2863 | 10.9865 | 9.5014 | 32.3089 | 15.1058 | 10.8569 | 9.078 | 32.5003 | 14.9238 | 10.7261 | 8.5726 | 32.7085 | 14.7705 | 10.6158 | 8.1851 | 32.9443 | 14.5936 | 10.4887 | 7.5788 | 33.2494 | 14.2343 | 10.2304 | 6.0861 | 34.226 | 12.3685 | 8.8895 | -0.94105 | 34.8078 | 11.207 | 8.0547 | -6.6598 | 35.0051 | 10.7879 | 7.7535 | -9.676 | 34.8796 | 10.8618 | 7.8066 | -8.7089
GREEN LANE (HAZEL GROVE) | HAZEL GROVE | BREDBURY | 391570 | 387132 | 32.6689 | 9.4448 | 6.7882 | 8.7225 | 32.7379 | 9.3701 | 6.7345 | 8.5295 | 32.773 | 9.2302 | 6.6339 | 8.1196 | 32.8567 | 9.0297 | 6.4898 | 7.6796 | 32.9576 | 8.8906 | 6.3899 | 7.272 | 33.084 | 8.7011 | 6.2537 | 6.6956 | 33.2261 | 8.4713 | 6.0885 | 5.8688 | 33.38 | 8.2886 | 5.9572 | 5.3658 | 33.5452 | 8.1095 | 5.8285 | 4.8367 | 33.7259 | 7.9004 | 5.6782 | 4.0576 | 34.453 | 6.8146 | 4.8978 | 1.677 | 35.0358 | 6.4745 | 4.6533 | 0.67163 | 35.4208 | 7.4537 | 5.3571 | 0.47811 | 35.7162 | 8.5894 | 6.1733 | 0.88462 | 32.6292 | 9.4921 | 6.8222 | 8.8507 | 32.6723 | 9.3962 | 6.7532 | 8.7555 | 32.7543 | 9.2617 | 6.6566 | 8.2649 | 32.8568 | 9.1314 | 6.5629 | 7.848 | 32.9713 | 9.0146 | 6.4789 | 7.5097 | 33.0956 | 8.8897 | 6.3892 | 7.0109 | 33.2288 | 8.7373 | 6.2797 | 6.2627 | 33.3709 | 8.6309 | 6.2032 | 5.8319 | 33.5231 | 8.5052 | 6.1129 | 5.3588 | 33.6824 | 8.3515 | 6.0024 | 4.7027 | 34.049 | 7.9045 | 5.6811 | 2.9336 | 34.3511 | 7.5143 | 5.4007 | 1.8412 | 34.5811 | 8.2437 | 5.9249 | 1.1446 | 34.7454 | 9.0356 | 6.4941 | 0.88811 | 32.669 | 9.4873 | 6.8187 | 8.7332 | 32.738 | 9.4075 | 6.7613 | 8.5529 | 32.7733 | 9.2144 | 6.6226 | 8.1585 | 32.8572 | 9.0913 | 6.5341 | 7.7311 | 32.9578 | 8.9627 | 6.4416 | 7.338 | 33.0837 | 8.8096 | 6.3316 | 6.7786 | 33.2252 | 8.6272 | 6.2006 | 5.9707 | 33.3789 | 8.494 | 6.1048 | 5.4814 | 33.542 | 8.3465 | 5.9988 | 4.9765 | 33.7137 | 8.1577 | 5.8631 | 4.2633 | 34.3841 | 7.4681 | 5.3674 | 2.1001 | 34.879 | 6.8608 | 4.931 | 1.2448 | 35.2185 | 7.9311 | 5.7002 | 1.0924 | 35.4563 | 8.9272 | 6.4162 | 1.4946 | 32.6626 | 9.4447 | 6.7881 | 8.7377 | 32.7296 | 9.3742 | 6.7374 | 8.5639 | 32.7765 | 9.2209 | 6.6272 | 8.188 | 32.8727 | 9.006 | 6.4728 | 7.7896 | 33.0075 | 8.8713 | 6.376 | 7.45 | 33.1847 | 8.6832 | 6.2408 | 6.953 | 33.3973 | 8.4275 | 6.057 | 6.2077 | 33.6404 | 8.2469 | 5.9272 | 5.7921 | 33.9106 | 8.0846 | 5.8106 | 5.4309 | 34.2117 | 7.8662 | 5.6536 | 4.8941 | 35.2993 | 6.5201 | 4.6862 | 1.7351 | 29.125 | 4.7952 | 3.4464 | -4.9884 | 28.1286 | 4.6312 | 3.3285 | -10.3837 | 30.0595 | 4.9491 | 3.557 | -13.9061 | 32.6451 | 9.4513 | 6.7928 | 8.7664 | 32.7117 | 9.3999 | 6.7559 | 8.5541 | 32.7607 | 9.2244 | 6.6298 | 8.1657 | 32.8389 | 9.0466 | 6.502 | 7.8192 | 32.9599 | 8.9163 | 6.4083 | 7.5424 | 33.1166 | 8.7088 | 6.2592 | 7.1433 | 33.3136 | 8.4461 | 6.0704 | 6.4908 | 33.5332 | 8.2729 | 5.9459 | 6.185 | 33.7868 | 8.083 | 5.8094 | 5.7175 | 34.1176 | 7.6261 | 5.481 | 4.0042 | 34.5653 | 5.6909 | 4.0902 | -3.6884 | 25.7007 | 4.2314 | 3.0412 | -9.7055 | 34.1263 | 5.6186 | 4.0382 | -13.2853 | 33.7189 | 5.5516 | 3.99 | -11.9648
GREEN ST T11 | WIGAN | WASHWAY FARM / KIRKBY | 358235 | 404898 | 21.4807 | 21.4807 | 17.6069 | 5.6684 | 21.5544 | 21.5544 | 17.4235 | 5.3735 | 21.5577 | 21.5577 | 17.2749 | 5.3228 | 21.5856 | 21.5856 | 17.1335 | 5.2121 | 21.629 | 21.629 | 16.997 | 5.0459 | 21.6873 | 21.6873 | 16.8851 | 4.8456 | 21.7497 | 21.7497 | 16.8322 | 4.6329 | 21.8144 | 21.8144 | 16.7805 | 4.4253 | 21.8814 | 21.8814 | 16.7273 | 4.2205 | 21.9531 | 21.9531 | 16.6699 | 3.9973 | 22.2253 | 22.2253 | 16.5646 | 3.2077 | 22.4397 | 22.4397 | 17.3633 | 2.7579 | 22.5628 | 22.5628 | 18.7939 | 2.6167 | 22.6424 | 22.6424 | 19.1196 | 2.6654 | 21.4091 | 21.4091 | 17.6491 | 5.9539 | 21.4271 | 21.4271 | 17.4468 | 5.8914 | 21.4712 | 21.4712 | 17.2618 | 5.7318 | 21.5293 | 21.5293 | 17.1034 | 5.5516 | 21.5952 | 21.5952 | 16.9596 | 5.3431 | 21.6671 | 21.6671 | 16.8265 | 5.1282 | 21.746 | 21.746 | 16.793 | 4.8898 | 21.8296 | 21.8296 | 16.7545 | 4.6258 | 21.9183 | 21.9183 | 16.714 | 4.3536 | 22.0113 | 22.0113 | 16.6714 | 4.0682 | 22.1687 | 22.1687 | 16.6601 | 3.4154 | 22.3001 | 22.3001 | 17.1883 | 2.9451 | 22.3863 | 22.3863 | 18.0733 | 2.7002 | 22.4267 | 22.4267 | 18.2679 | 2.6069 | 21.4808 | 21.4808 | 17.6475 | 5.6758 | 21.5544 | 21.5544 | 17.4408 | 5.3902 | 21.5578 | 21.5578 | 17.2506 | 5.3493 | 21.5859 | 21.5859 | 17.0817 | 5.2475 | 21.6291 | 21.6291 | 16.929 | 5.0916 | 21.6873 | 21.6873 | 16.81 | 4.9018 | 21.7496 | 21.7496 | 16.7669 | 4.6997 | 21.8142 | 21.8142 | 16.7198 | 4.5026 | 21.8805 | 21.8805 | 16.67 | 4.3115 | 21.9492 | 21.9492 | 16.6173 | 4.1135 | 22.1998 | 22.1998 | 16.5762 | 3.4038 | 22.3765 | 22.3765 | 17.4346 | 3.0284 | 22.4805 | 22.4805 | 18.9107 | 2.9211 | 22.533 | 22.533 | 19.2291 | 2.9909 | 21.4737 | 21.4737 | 17.61 | 5.687 | 21.5415 | 21.5415 | 17.4253 | 5.4098 | 21.5426 | 21.5426 | 17.2762 | 5.3746 | 21.5724 | 21.5724 | 17.1304 | 5.276 | 21.6217 | 21.6217 | 16.999 | 5.1195 | 21.6928 | 21.6928 | 16.8815 | 4.9243 | 21.7762 | 21.7762 | 16.8243 | 4.7069 | 21.8688 | 21.8688 | 16.7636 | 4.4906 | 21.968 | 21.968 | 16.7066 | 4.2874 | 22.0764 | 22.0764 | 16.6471 | 4.0846 | 22.4754 | 22.4754 | 16.4889 | 3.0715 | 22.8939 | 22.8939 | 17.0553 | 1.1075 | 23.0719 | 23.0719 | 18.2389 | -0.53141 | 23.1098 | 23.1098 | 18.3839 | -1.5704 | 21.467 | 21.467 | 17.6445 | 5.6925 | 21.5322 | 21.5322 | 17.5915 | 5.4085 | 21.5304 | 21.5304 | 17.5425 | 5.3765 | 21.5538 | 21.5538 | 17.4863 | 5.2929 | 21.5967 | 21.5967 | 17.4219 | 5.152 | 21.6594 | 21.6594 | 17.3512 | 4.9816 | 21.7359 | 21.7359 | 17.2845 | 4.7894 | 21.8192 | 21.8192 | 17.2615 | 4.6052 | 21.9138 | 21.9138 | 17.2471 | 4.4036 | 22.047 | 22.047 | 17.2192 | 3.9096 | 22.5157 | 22.5157 | 19.0455 | 1.6207 | 22.7618 | 22.7618 | 18.5929 | -0.35922 | 22.7975 | 22.7975 | 18.3794 | -1.4042 | 22.6923 | 22.6923 | 18.3814 | -0.86699
GREEN ST T12 & T13 | WIGAN | WASHWAY FARM / KIRKBY | 358225 | 404888 | 30.9292 | 7.4441 | 5.4304 | 9.0048 | 27.9477 | 4.5334 | 3.307 | 8.6724 | 10.4728 | 1.6988 | 1.2392 | 8.5286 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 34.7906 | 8.8181 | 6.4327 | 2.8004 | 35.5433 | 10.668 | 7.7822 | 2.7142 | 30.9197 | 7.4726 | 5.4512 | 9.1719 | 27.4771 | 4.4571 | 3.2514 | 8.9397 | 9.5313 | 1.5461 | 1.1278 | 8.5547 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6809 | 23.2241 | 3.7672 | 2.7481 | 2.2784 | 31.7734 | 5.154 | 3.7597 | 2.0696 | 30.9306 | 7.468 | 5.4478 | 9.0403 | 27.4888 | 4.459 | 3.2527 | 8.7602 | 9.2705 | 1.5038 | 1.097 | 8.6619 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 34.1684 | 9.0359 | 6.5915 | 3.3605 | 34.6476 | 10.9197 | 7.9657 | 3.381 | 30.9268 | 7.4461 | 5.4318 | 9.0278 | 27.9431 | 4.5326 | 3.3065 | 8.7212 | 10.4139 | 1.6892 | 1.2323 | 8.6036 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -1.9397 | 36.9635 | 6.4028 | 4.6708 | -7.2943 | 37.433 | 7.479 | 5.4558 | -11.0671 | 30.9097 | 9.6282 | 7.0236 | 9.0625 | 30.9752 | 9.5568 | 6.9716 | 8.7745 | 31.018 | 9.4564 | 6.8983 | 8.6994 | 31.1013 | 9.3155 | 6.7956 | 8.5588 | 31.2203 | 9.1234 | 6.6554 | 8.3496 | 31.3968 | 8.8 | 6.4195 | 8.1114 | 31.6399 | 8.6622 | 6.3189 | 7.8116 | 31.927 | 8.6122 | 6.2825 | 7.4923 | 32.2618 | 8.5498 | 6.237 | 7.1155 | 32.6762 | 8.3563 | 6.0958 | 5.9985 | 34.4973 | 10.4905 | 7.6527 | -0.48916 | 35.9911 | 8.7379 | 6.3742 | -6.5901 | 36.6164 | 7.7696 | 5.6678 | -10.2494 | 36.6575 | 7.6524 | 5.5823 | -9.6423
GREENFIELD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 29.6844 | 11.4559 | 8.2336 | 16.8494 | 29.7311 | 11.3873 | 8.1843 | 16.5009 | 29.7883 | 11.2418 | 8.0797 | 16.1658 | 29.8695 | 11.0947 | 7.974 | 15.7647 | 29.9664 | 10.8923 | 7.8285 | 15.4444 | 30.0779 | 10.6119 | 7.627 | 14.9714 | 30.2047 | 10.4077 | 7.4802 | 14.4763 | 30.3426 | 10.1881 | 7.3224 | 13.9813 | 30.4834 | 9.9296 | 7.1366 | 13.4578 | 30.6396 | 9.6247 | 6.9174 | 12.8089 | 31.2246 | 9.4348 | 6.781 | 10.6457 | 31.6478 | 8.9464 | 6.4299 | 9.6949 | 31.8976 | 9.1743 | 6.5938 | 9.6031 | 32.0693 | 9.2544 | 6.6513 | 9.9781 | 29.6847 | 11.45 | 8.2293 | 16.9337 | 29.7312 | 11.2576 | 8.0911 | 16.6657 | 29.7976 | 10.9693 | 7.8839 | 16.3242 | 29.8636 | 10.5803 | 7.6043 | 16.0025 | 29.9389 | 10.4447 | 7.5068 | 15.7749 | 30.025 | 10.4857 | 7.5363 | 15.3956 | 30.122 | 10.413 | 7.484 | 14.996 | 30.2267 | 10.3385 | 7.4305 | 14.6001 | 30.3388 | 10.2565 | 7.3715 | 14.1752 | 30.4569 | 10.1724 | 7.3111 | 13.7198 | 30.7486 | 9.9092 | 7.1219 | 12.4437 | 30.9842 | 9.6069 | 6.9047 | 11.5268 | 31.1596 | 9.6909 | 6.965 | 11.0179 | 31.2927 | 9.6302 | 6.9214 | 10.7262 | 29.6845 | 11.4496 | 8.229 | 16.8551 | 29.7311 | 11.2419 | 8.0798 | 16.5183 | 29.7884 | 10.9129 | 7.8433 | 16.1967 | 29.8697 | 10.3909 | 7.4681 | 15.8129 | 29.9663 | 10.5524 | 7.5842 | 15.5092 | 30.0772 | 10.4822 | 7.5338 | 15.0554 | 30.2035 | 10.3699 | 7.4531 | 14.579 | 30.3411 | 10.2754 | 7.3851 | 14.08 | 30.4801 | 10.1551 | 7.2986 | 13.578 | 30.6289 | 10.0214 | 7.2026 | 12.9889 | 31.1724 | 9.3618 | 6.7285 | 11.0145 | 31.5468 | 9.2547 | 6.6515 | 10.1798 | 31.7725 | 9.1755 | 6.5946 | 10.1125 | 31.9196 | 9.2704 | 6.6628 | 10.4605 | 29.685 | 11.455 | 8.2329 | 16.854 | 29.7387 | 11.3875 | 8.1844 | 16.495 | 29.8093 | 11.2532 | 8.0879 | 16.1584 | 29.9066 | 11.0721 | 7.9577 | 15.7734 | 30.0321 | 10.8506 | 7.7985 | 15.465 | 30.186 | 10.5328 | 7.5702 | 14.9983 | 30.3565 | 10.2818 | 7.3897 | 14.4953 | 30.5433 | 9.9962 | 7.1845 | 13.9997 | 30.7483 | 9.7897 | 7.0361 | 13.5686 | 30.9775 | 9.8244 | 7.061 | 13.1082 | 31.7727 | 9.2851 | 6.6734 | 10.9217 | 32.47 | 8.2971 | 5.9633 | 7.1861 | 32.8213 | 8.0592 | 5.7923 | 4.7454 | 33.0288 | 7.5247 | 5.4082 | 2.9862 | 29.6822 | 11.4548 | 8.2328 | 16.8398 | 29.7432 | 11.4241 | 8.2107 | 16.4328 | 29.8178 | 11.3454 | 8.1541 | 16.091 | 29.9165 | 11.2486 | 8.0846 | 15.7321 | 30.0408 | 11.1049 | 7.9813 | 15.4583 | 30.1649 | 10.8692 | 7.8119 | 15.0575 | 30.317 | 10.6607 | 7.6621 | 14.6309 | 30.4845 | 10.4339 | 7.4991 | 14.239 | 30.6673 | 10.1813 | 7.3175 | 13.8539 | 30.9173 | 9.8649 | 7.0901 | 12.8637 | 31.713 | 9.0187 | 6.4819 | 8.4169 | 32.1668 | 8.0021 | 5.7513 | 5.2999 | 32.3146 | 7.7929 | 5.6009 | 3.7969 | 32.2766 | 7.8156 | 5.6172 | 4.5622
GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 26.2979 | 4.2658 | 3.1118 | 26.2979 | 8.8052 | 1.4283 | 1.0419 | 8.8052 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 27.0421 | 4.3865 | 3.1999 | 27.0421 | 9.7142 | 1.5757 | 1.1495 | 9.7142 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 27.0151 | 4.3821 | 3.1967 | 27.0151 | 8.659 | 1.4046 | 1.0246 | 8.659 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 26.3381 | 4.2723 | 3.1166 | 26.3381 | 8.8589 | 1.437 | 1.0483 | 8.8589 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 26.3946 | 4.2815 | 3.1233 | 26.3946 | 24.4034 | 3.9585 | 2.8877 | 24.4034 | 21.4767 | 3.4837 | 2.5413 | 21.4767 | 19.3406 | 3.1372 | 2.2886 | 19.3406 | 16.7867 | 2.723 | 1.9864 | 16.7867 | 13.8531 | 2.2471 | 1.6392 | 13.8531 | 12.4002 | 2.0114 | 1.4673 | 12.4002 | 11.0138 | 1.7866 | 1.3033 | 11.0138 | 9.4512 | 1.5331 | 1.1184 | 9.4512 | 6.3222 | 1.0255 | 0.7481 | 6.3222 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
GRIFFIN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 31.7568 | 16.6498 | 12.1458 | 13.0485 | 31.8205 | 15.3389 | 11.1895 | 12.2527 | 31.8602 | 14.078 | 10.2697 | 11.8635 | 31.9361 | 12.6869 | 9.2549 | 11.213 | 32.0378 | 11.5552 | 8.4293 | 11.2306 | 32.1623 | 10.4668 | 7.6354 | 10.6076 | 32.304 | 10.1708 | 7.4195 | 10.1909 | 32.4585 | 10.2229 | 7.4575 | 9.7008 | 32.6252 | 10.209 | 7.4473 | 9.1418 | 32.812 | 10.1009 | 7.3685 | 8.3926 | 33.5688 | 9.7341 | 7.1009 | 5.8069 | 34.2588 | 11.175 | 8.152 | 4.517 | 34.7355 | 13.5347 | 9.8733 | 4.004 | 35.1204 | 13.8459 | 10.1004 | 4.2679 | 31.7425 | 16.7161 | 12.1941 | 13.2453 | 31.8033 | 15.6293 | 11.4014 | 12.7357 | 31.8983 | 14.5025 | 10.5794 | 12.3136 | 32.0155 | 13.3329 | 9.7262 | 11.7525 | 32.1511 | 12.3263 | 8.9918 | 11.7808 | 32.3052 | 11.2287 | 8.1912 | 11.2125 | 32.4608 | 11.144 | 8.1294 | 10.8213 | 32.6261 | 11.0434 | 8.056 | 10.3507 | 32.8058 | 10.9379 | 7.9791 | 9.8935 | 32.998 | 10.8052 | 7.8822 | 9.3027 | 33.4303 | 10.6107 | 7.7403 | 7.6792 | 33.8257 | 11.5375 | 8.4165 | 6.4542 | 34.1132 | 13.1621 | 9.6016 | 5.5212 | 34.3231 | 13.1433 | 9.5879 | 5.0124 | 31.7576 | 16.709 | 12.189 | 13.0518 | 31.8216 | 15.5809 | 11.3661 | 12.2975 | 31.8617 | 14.5074 | 10.583 | 11.9044 | 31.938 | 13.3651 | 9.7497 | 11.3058 | 32.0397 | 12.3152 | 8.9838 | 11.3373 | 32.1634 | 11.0675 | 8.0736 | 10.7432 | 32.3042 | 10.9851 | 8.0135 | 10.3492 | 32.4575 | 10.8682 | 7.9282 | 9.8747 | 32.6212 | 10.7505 | 7.8423 | 9.3514 | 32.7985 | 10.6125 | 7.7417 | 8.6828 | 33.4851 | 10.3608 | 7.558 | 6.3877 | 34.0269 | 11.7043 | 8.5381 | 5.3121 | 34.4121 | 14.4304 | 10.5268 | 4.9134 | 34.6826 | 14.7049 | 10.727 | 5.2165 | 31.7539 | 16.6485 | 12.1448 | 13.0455 | 31.8179 | 15.3539 | 11.2004 | 12.242 | 31.8671 | 14.1119 | 10.2944 | 11.8435 | 31.9629 | 12.7691 | 9.3149 | 11.186 | 32.097 | 11.44 | 8.3453 | 11.2223 | 32.2716 | 10.2202 | 7.4555 | 10.5552 | 32.4844 | 10.2646 | 7.4879 | 10.1161 | 32.7283 | 10.2516 | 7.4784 | 9.6159 | 33 | 10.171 | 7.4196 | 9.1111 | 33.3036 | 10.0232 | 7.3118 | 8.5107 | 34.4858 | 9.2484 | 6.7466 | 5.2945 | 35.6311 | 9.4516 | 6.8948 | -0.93352 | 36.3233 | 10.7058 | 7.8097 | -5.6393 | 36.616 | 10.4605 | 7.6308 | -8.4512 | 31.7365 | 16.6582 | 12.1519 | 13.0804 | 31.795 | 16.5381 | 12.0643 | 12.2666 | 31.8369 | 16.4617 | 12.0086 | 11.9042 | 31.9154 | 16.2822 | 11.8777 | 11.2833 | 32.032 | 16.1821 | 11.8046 | 11.3555 | 32.1866 | 15.9996 | 11.6715 | 10.7447 | 32.3862 | 15.915 | 11.6098 | 10.3888 | 32.6128 | 15.7906 | 11.519 | 10.0494 | 32.874 | 15.6004 | 11.3803 | 9.4087 | 33.2036 | 15.206 | 11.0925 | 7.7896 | 34.455 | 14.1164 | 10.2977 | 0.66465 | 35.3504 | 12.3546 | 9.0125 | -4.7665 | 35.7212 | 11.2804 | 8.2289 | -7.7761 | 35.6686 | 11.1254 | 8.1158 | -6.5687
HADFIELD | HYDE | STALYBRIDGE | 401790 | 395876 | 6.2545 | 1.0298 | 0.74011 | 6.2545 | 6.8005 | 1.1196 | 0.80471 | 6.8005 | 6.8023 | 1.1199 | 0.80492 | 6.8023 | 6.4657 | 1.0645 | 0.76509 | 6.4657 | 5.755 | 0.94752 | 0.681 | 5.755 | 4.9522 | 0.81535 | 0.58601 | 4.9522 | 4.0227 | 0.66231 | 0.47601 | 4.0227 | 3.3181 | 0.54629 | 0.39263 | 3.3181 | 2.564 | 0.42214 | 0.3034 | 2.564 | 1.6654 | 0.27419 | 0.19707 | 1.6654 | 0.93119 | 0.15331 | 0.11019 | 0.93119 | 19.3629 | 4.2904 | 3.0836 | 7.7902 | 19.7627 | 10.9779 | 7.89 | 7.6205 | 20.064 | 12.4383 | 8.9397 | 7.8439 | 6.0996 | 1.0043 | 0.72178 | 6.0996 | 5.562 | 0.91574 | 0.65816 | 5.562 | 4.6693 | 0.76876 | 0.55253 | 4.6693 | 3.8005 | 0.62572 | 0.44972 | 3.8005 | 3.2428 | 0.53389 | 0.38372 | 3.2428 | 2.4464 | 0.40279 | 0.28949 | 2.4464 | 1.6593 | 0.27319 | 0.19635 | 1.6593 | 0.98986 | 0.16297 | 0.11713 | 0.98986 | 0.18921 | 0.031151 | 0.022389 | 0.18921 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.19426 | 0.031983 | 0.022987 | 0.19426 | 16.3586 | 2.6933 | 1.9357 | 9.9327 | 18.6153 | 7.0386 | 5.0588 | 9.4614 | 18.788 | 7.7768 | 5.5893 | 9.2749 | 6.1015 | 1.0046 | 0.722 | 6.1015 | 5.3973 | 0.88863 | 0.63868 | 5.3973 | 4.2516 | 0.7 | 0.5031 | 4.2516 | 3.787 | 0.62349 | 0.44812 | 3.787 | 2.4871 | 0.40949 | 0.29431 | 2.4871 | 1.5998 | 0.2634 | 0.18931 | 1.5998 | 1.285 | 0.21157 | 0.15206 | 1.285 | 0.68979 | 0.11357 | 0.081624 | 0.68979 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.22135 | 0.036444 | 0.026193 | 0.22135 | 19.1806 | 4.2451 | 3.051 | 8.3863 | 19.5407 | 11.0896 | 7.9703 | 8.2766 | 19.7716 | 12.554 | 9.0228 | 8.5403 | 6.3071 | 1.0384 | 0.74633 | 6.3071 | 6.8987 | 1.1358 | 0.81634 | 6.8987 | 6.8588 | 1.1292 | 0.81161 | 6.8588 | 6.5092 | 1.0717 | 0.77025 | 6.5092 | 5.635 | 0.92777 | 0.6668 | 5.635 | 4.6525 | 0.766 | 0.55054 | 4.6525 | 3.9621 | 0.65233 | 0.46884 | 3.9621 | 3.2195 | 0.53007 | 0.38097 | 3.2195 | 2.4158 | 0.39774 | 0.28586 | 2.4158 | 1.5007 | 0.24708 | 0.17758 | 1.5007 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 20.235 | 3.3315 | 2.3944 | 4.6154 | 21.8207 | 9.3286 | 6.7047 | 1.4296 | 22.2734 | 10.3822 | 7.4619 | -0.53214 | 6.297 | 1.0368 | 0.74513 | 6.297 | 6.7228 | 1.1069 | 0.79552 | 6.7228 | 6.599 | 1.0865 | 0.78088 | 6.599 | 6.4002 | 1.0537 | 0.75734 | 6.4002 | 5.6231 | 0.92579 | 0.66539 | 5.6231 | 4.7581 | 0.78339 | 0.56304 | 4.7581 | 4.1625 | 0.68533 | 0.49256 | 4.1625 | 4.8058 | 0.79124 | 0.56868 | 4.8058 | 5.7849 | 0.95244 | 0.68454 | 5.7849 | 6.7677 | 1.1143 | 0.80083 | 6.7677 | 20.1035 | 12.4137 | 8.922 | 5.957 | 21.0351 | 11.3672 | 8.1698 | 2.0552 | 21.3168 | 10.7789 | 7.747 | 0.1677 | 21.2527 | 10.7507 | 7.7268 | 1.1168
HALL CROSS | PEEL | PENWORTHAM WEST / STANAH | 342288 | 430650 | 20.0953 | 10.8169 | 7.8908 | 7.9934 | 20.3085 | 10.4872 | 7.6502 | 7.1774 | 20.3959 | 10.2546 | 7.4806 | 6.97 | 20.536 | 9.9248 | 7.24 | 6.3785 | 20.7218 | 9.4442 | 6.8894 | 5.9357 | 20.9487 | 9.1476 | 6.6731 | 5.2024 | 21.1986 | 9.0708 | 6.617 | 4.5331 | 21.4301 | 8.8743 | 6.4737 | 3.8256 | 21.6322 | 8.7302 | 6.3686 | 3.0521 | 21.8485 | 8.5469 | 6.2349 | 2.1672 | 22.6877 | 7.7325 | 5.6407 | -0.80816 | 23.3433 | 7.1144 | 5.1898 | -2.4624 | 23.7498 | 6.7141 | 4.8978 | -2.8733 | 24.0435 | 6.8314 | 4.9834 | -2.6825 | 19.9475 | 10.884 | 7.9397 | 8.3169 | 20.0324 | 10.7659 | 7.8536 | 7.7887 | 20.1815 | 10.6481 | 7.7677 | 7.4218 | 20.3496 | 10.5498 | 7.6959 | 6.8192 | 20.5352 | 10.3992 | 7.5861 | 6.402 | 20.7339 | 10.3248 | 7.5318 | 5.7224 | 20.9494 | 10.2029 | 7.4429 | 5.0938 | 21.173 | 10.0678 | 7.3444 | 4.4589 | 21.4055 | 9.8982 | 7.2206 | 3.72 | 21.6432 | 9.71 | 7.0833 | 2.9922 | 22.2535 | 9.3095 | 6.7911 | 0.96829 | 22.6968 | 8.9022 | 6.494 | -0.73484 | 22.9777 | 8.7733 | 6.4 | -1.7201 | 23.145 | 8.7602 | 6.3905 | -2.3885 | 20.0954 | 10.8826 | 7.9387 | 8.0018 | 20.3087 | 10.5594 | 7.7029 | 7.2092 | 20.3962 | 10.1544 | 7.4075 | 7.0318 | 20.5365 | 9.6956 | 7.0728 | 6.4563 | 20.7219 | 9.0277 | 6.5856 | 6.052 | 20.9479 | 8.8106 | 6.4272 | 5.3483 | 21.1969 | 8.6545 | 6.3133 | 4.6808 | 21.4294 | 8.493 | 6.1955 | 3.9935 | 21.6296 | 8.2936 | 6.05 | 3.2577 | 21.8374 | 8.103 | 5.911 | 2.4501 | 22.6188 | 7.4297 | 5.4199 | -0.29287 | 23.1769 | 6.8664 | 5.0089 | -1.731 | 23.5332 | 6.7023 | 4.8892 | -2.0469 | 23.7586 | 6.6734 | 4.8682 | -1.8044 | 20.0831 | 10.8206 | 7.8935 | 8.0212 | 20.2923 | 10.4864 | 7.6497 | 7.2268 | 20.3951 | 10.3064 | 7.5184 | 7.0468 | 20.5687 | 9.8822 | 7.2089 | 6.4942 | 20.8116 | 9.6515 | 7.0406 | 6.1091 | 21.0879 | 9.1781 | 6.6953 | 5.4319 | 21.3413 | 9.1131 | 6.6479 | 4.7839 | 21.6184 | 8.9211 | 6.5078 | 4.1417 | 21.9153 | 8.6719 | 6.326 | 3.4901 | 22.2366 | 8.4901 | 6.1934 | 2.8581 | 23.3477 | 7.4191 | 5.4121 | -0.19322 | 24.2336 | 6.143 | 4.4813 | -5.3014 | 24.6883 | 5.2999 | 3.8662 | -8.7568 | 24.8776 | 4.7311 | 3.4513 | -11.2478 | 20.0835 | 10.8229 | 7.8951 | 8.0276 | 20.3138 | 10.5078 | 7.6653 | 7.2081 | 20.4292 | 10.2594 | 7.4841 | 7.023 | 20.6024 | 9.8558 | 7.1896 | 6.5083 | 20.824 | 9.419 | 6.8711 | 6.1502 | 21.0243 | 9.2264 | 6.7305 | 5.5423 | 21.261 | 9.0877 | 6.6293 | 4.9929 | 21.5133 | 8.9265 | 6.5118 | 4.4535 | 21.7845 | 8.7061 | 6.351 | 3.8309 | 22.1034 | 8.418 | 6.1408 | 2.5264 | 23.2069 | 6.8189 | 4.9743 | -3.3303 | 23.8549 | 5.4623 | 3.9847 | -7.718 | 24.0254 | 5.1683 | 3.7702 | -9.9147 | 23.8854 | 5.0905 | 3.7135 | -9.203
HANDFORTH | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 31.4968 | 9.8834 | 7.1034 | 14.7963 | 31.5942 | 9.7721 | 7.0234 | 14.2374 | 31.6411 | 9.6761 | 6.9544 | 13.7941 | 31.7272 | 9.5478 | 6.8622 | 13.5151 | 31.8407 | 9.3215 | 6.6996 | 13.0866 | 31.9536 | 9.1038 | 6.543 | 12.6156 | 32.0743 | 8.827 | 6.3441 | 12.045 | 32.201 | 8.6933 | 6.248 | 11.6022 | 32.3336 | 8.6872 | 6.2437 | 11.107 | 32.4756 | 8.5998 | 6.1809 | 10.5346 | 33.0972 | 7.8934 | 5.6731 | 8.4631 | 33.6517 | 7.917 | 5.6901 | 7.4162 | 34.0042 | 7.9785 | 5.7343 | 7.1414 | 34.2995 | 8.1594 | 5.8643 | 7.1773 | 31.4316 | 9.9612 | 7.1593 | 15.0576 | 31.4739 | 9.85 | 7.0794 | 14.7418 | 31.5504 | 9.7283 | 6.9919 | 14.3093 | 31.6472 | 9.6549 | 6.9391 | 14.0574 | 31.7554 | 9.583 | 6.8875 | 13.6879 | 31.8743 | 9.5047 | 6.8312 | 13.2794 | 31.9917 | 9.4526 | 6.7938 | 12.7703 | 32.112 | 9.4023 | 6.7576 | 12.3794 | 32.2385 | 9.3473 | 6.7181 | 11.9317 | 32.369 | 9.2873 | 6.675 | 11.4666 | 32.7084 | 9.0295 | 6.4897 | 9.9206 | 33.013 | 8.7225 | 6.2691 | 8.8297 | 33.2696 | 8.8768 | 6.3799 | 8.1689 | 33.4614 | 9.2591 | 6.6547 | 7.7253 | 31.4969 | 9.9693 | 7.1651 | 14.8048 | 31.5945 | 9.8931 | 7.1103 | 14.2597 | 31.6416 | 9.7856 | 7.0331 | 13.8311 | 31.728 | 9.7537 | 7.0101 | 13.5619 | 31.8414 | 9.6812 | 6.9581 | 13.148 | 31.9542 | 9.6155 | 6.9109 | 12.6922 | 32.0747 | 9.5225 | 6.844 | 12.1371 | 32.2013 | 9.4345 | 6.7808 | 11.7073 | 32.3325 | 9.3231 | 6.7007 | 11.2339 | 32.4676 | 9.2069 | 6.6172 | 10.714 | 33.0328 | 8.6567 | 6.2218 | 8.8054 | 33.4763 | 8.6224 | 6.1971 | 7.918 | 33.7746 | 9.0291 | 6.4894 | 7.7039 | 33.9835 | 8.6819 | 6.2399 | 7.8373 | 31.4925 | 9.8834 | 7.1034 | 14.8116 | 31.5913 | 9.7597 | 7.0145 | 14.2731 | 31.6537 | 9.6334 | 6.9237 | 13.8579 | 31.7614 | 9.5002 | 6.828 | 13.6008 | 31.8711 | 9.275 | 6.6661 | 13.2227 | 32.0148 | 9.0331 | 6.4923 | 12.8018 | 32.1835 | 8.7083 | 6.2588 | 12.2678 | 32.3722 | 8.7057 | 6.2569 | 11.8654 | 32.58 | 8.6561 | 6.2213 | 11.4662 | 32.8105 | 8.5399 | 6.1378 | 11.0521 | 33.688 | 7.8229 | 5.6225 | 8.7573 | 34.4822 | 7.0367 | 5.0574 | 5.0356 | 34.9207 | 6.8059 | 4.8915 | 2.3609 | 35.1174 | 6.3304 | 4.5497 | 0.45831 | 31.5026 | 9.8735 | 7.0963 | 14.751 | 31.6236 | 9.7056 | 6.9756 | 14.1424 | 31.6944 | 9.5381 | 6.8552 | 13.7306 | 31.7714 | 9.3321 | 6.7071 | 13.5076 | 31.8749 | 9.0361 | 6.4945 | 13.162 | 32.0106 | 9.0695 | 6.5185 | 12.7961 | 32.1772 | 8.9841 | 6.457 | 12.3188 | 32.3601 | 8.8917 | 6.3906 | 11.9873 | 32.565 | 8.7398 | 6.2815 | 11.5768 | 32.8147 | 8.4992 | 6.1085 | 10.6363 | 33.7262 | 8.1532 | 5.8599 | 6.2263 | 34.3447 | 7.1477 | 5.1372 | 2.953 | 34.5441 | 6.6848 | 4.8045 | 1.2353 | 34.4652 | 6.6321 | 4.7666 | 1.7721
HANGING BRIDGE | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 346186 | 417486 | 10.4984 | 10.4984 | 10.4984 | 5.8397 | 10.5487 | 10.5487 | 10.5487 | 5.5624 | 10.6285 | 10.6285 | 10.6285 | 5.4732 | 10.7263 | 10.7263 | 10.7263 | 5.2381 | 10.8217 | 10.8217 | 10.8217 | 5.0568 | 10.9141 | 10.9141 | 10.9141 | 4.7578 | 11.0243 | 11.0243 | 11.0243 | 4.4434 | 11.1477 | 11.1477 | 11.1477 | 4.1226 | 11.2739 | 11.2739 | 11.2739 | 3.7822 | 11.3834 | 11.3834 | 11.3834 | 3.3905 | 12.0801 | 12.0801 | 12.0801 | 1.9315 | 12.8582 | 12.8582 | 12.8582 | 0.80554 | 13.4225 | 13.4225 | 13.4225 | 0.32702 | 13.9826 | 13.9826 | 13.9826 | 0.085603 | 10.5074 | 10.5074 | 10.5074 | 5.9866 | 10.5588 | 10.5588 | 10.5588 | 5.8337 | 10.6282 | 10.6282 | 10.6282 | 5.6932 | 10.6889 | 10.6889 | 10.6889 | 5.466 | 10.7628 | 10.7628 | 10.7628 | 5.341 | 10.833 | 10.833 | 10.833 | 5.0912 | 10.9075 | 10.9075 | 10.9075 | 4.8276 | 10.9898 | 10.9898 | 10.9898 | 4.5569 | 11.0791 | 11.0791 | 11.0791 | 4.2591 | 11.1726 | 11.1726 | 11.1726 | 3.9681 | 11.7181 | 11.7181 | 11.7181 | 2.9554 | 12.2713 | 12.2713 | 12.2713 | 2.1079 | 12.6598 | 12.6598 | 12.6598 | 1.5665 | 12.9955 | 12.9955 | 12.9955 | 1.2125 | 10.5024 | 10.5024 | 10.5024 | 5.8416 | 10.5542 | 10.5542 | 10.5542 | 5.5734 | 10.6354 | 10.6354 | 10.6354 | 5.4928 | 10.7342 | 10.7342 | 10.7342 | 5.2519 | 10.828 | 10.828 | 10.828 | 5.0755 | 10.9197 | 10.9197 | 10.9197 | 4.7856 | 11.0283 | 11.0283 | 11.0283 | 4.4801 | 11.1492 | 11.1492 | 11.1492 | 4.1683 | 11.2732 | 11.2732 | 11.2732 | 3.8432 | 11.3756 | 11.3756 | 11.3756 | 3.4863 | 11.9706 | 11.9706 | 11.9706 | 2.1964 | 12.5147 | 12.5147 | 12.5147 | 1.3945 | 12.9313 | 12.9313 | 12.9313 | 1.0959 | 13.2795 | 13.2795 | 13.2795 | 1.0682 | 10.5058 | 10.5058 | 10.5058 | 5.8545 | 10.5728 | 10.5728 | 10.5728 | 5.5861 | 10.6834 | 10.6834 | 10.6834 | 5.509 | 10.8098 | 10.8098 | 10.8098 | 5.2917 | 10.9267 | 10.9267 | 10.9267 | 5.1439 | 11.0828 | 11.0828 | 11.0828 | 4.8675 | 11.2299 | 11.2299 | 11.2299 | 4.5679 | 11.3962 | 11.3962 | 11.3962 | 4.265 | 11.5879 | 11.5879 | 11.5879 | 3.9733 | 11.806 | 11.806 | 11.806 | 3.6869 | 12.9457 | 12.9457 | 12.9457 | 1.9025 | 14.065 | 14.065 | 14.065 | -0.13627 | 14.6175 | 14.6175 | 14.6175 | -1.2656 | 14.6871 | 14.6871 | 14.6871 | -1.9842 | 10.5181 | 10.5181 | 10.5181 | 5.835 | 10.6128 | 10.6128 | 10.6128 | 5.5294 | 10.7467 | 10.7467 | 10.7467 | 5.4418 | 10.8642 | 10.8642 | 10.8642 | 5.2032 | 11.0037 | 11.0037 | 11.0037 | 5.0457 | 11.155 | 11.155 | 11.155 | 4.7771 | 11.3315 | 11.3315 | 11.3315 | 4.482 | 11.5466 | 11.5466 | 11.5466 | 4.1909 | 11.7962 | 11.7962 | 11.7962 | 3.8988 | 12.0866 | 12.0866 | 12.0866 | 3.451 | 13.2816 | 13.2816 | 13.2816 | 1.1518 | 14.2401 | 14.2401 | 14.2401 | -0.49505 | 14.4048 | 14.4048 | 14.4048 | -1.1262 | 14.3134 | 14.3134 | 14.3134 | -1.0707
HAREHOLME | ROSSENDALE | PADIHAM | 382535 | 422283 | 29.0502 | 14.3148 | 10.4424 | 9.9452 | 29.1922 | 14.0741 | 10.2669 | 9.2905 | 29.4 | 13.8862 | 10.1298 | 9.058 | 29.6422 | 13.6879 | 9.9852 | 8.7773 | 29.9081 | 13.5075 | 9.8535 | 8.4391 | 30.0941 | 13.2893 | 9.6943 | 7.9931 | 30.3115 | 13.1414 | 9.5865 | 7.5073 | 30.5523 | 12.9762 | 9.4659 | 6.993 | 30.8132 | 12.7785 | 9.3217 | 6.4726 | 31.0806 | 12.5493 | 9.1546 | 5.8559 | 31.9297 | 11.7774 | 8.5915 | 3.1085 | 32.5637 | 11.0697 | 8.0752 | 1.0628 | 32.9419 | 10.6028 | 7.7346 | -0.12168 | 33.2104 | 10.2841 | 7.5021 | -0.83729 | 29.0312 | 14.4001 | 10.5046 | 10.4228 | 29.1477 | 14.2194 | 10.3728 | 10.18 | 29.3281 | 14.0347 | 10.2381 | 9.901 | 29.4947 | 13.8551 | 10.1071 | 9.6017 | 29.6832 | 13.6769 | 9.9771 | 9.303 | 29.8919 | 13.437 | 9.8021 | 8.9567 | 30.1264 | 13.3745 | 9.7565 | 8.5831 | 30.3732 | 13.2885 | 9.6938 | 8.1957 | 30.6287 | 13.1843 | 9.6178 | 7.8144 | 30.8373 | 13.0938 | 9.5517 | 7.2649 | 31.2516 | 12.8254 | 9.356 | 5.4344 | 31.5691 | 12.4817 | 9.1052 | 4.2052 | 31.7904 | 12.311 | 8.9807 | 3.6106 | 31.9394 | 12.105 | 8.8304 | 3.2938 | 29.0502 | 14.4003 | 10.5048 | 9.9529 | 29.1924 | 14.2037 | 10.3614 | 9.3323 | 29.4002 | 13.9723 | 10.1926 | 9.0884 | 29.6425 | 13.8321 | 10.0903 | 8.8179 | 29.9081 | 13.6055 | 9.925 | 8.4934 | 30.093 | 13.4058 | 9.7793 | 8.0621 | 30.3094 | 13.3075 | 9.7076 | 7.5909 | 30.5496 | 13.1849 | 9.6182 | 7.0908 | 30.8069 | 13.0818 | 9.543 | 6.5917 | 31.0657 | 12.8987 | 9.4094 | 6.027 | 31.8521 | 12.2609 | 8.9441 | 3.5179 | 32.398 | 11.7952 | 8.6044 | 1.7131 | 32.7321 | 11.3909 | 8.3095 | 0.66384 | 32.9484 | 11.2061 | 8.1747 | 0.034218 | 29.0522 | 14.3161 | 10.4434 | 9.9782 | 29.2142 | 14.0758 | 10.2681 | 9.3426 | 29.4783 | 13.8854 | 10.1292 | 9.0718 | 29.8111 | 13.6774 | 9.9775 | 8.7196 | 30.0637 | 13.4675 | 9.8244 | 8.2692 | 30.3531 | 13.1678 | 9.6057 | 7.6519 | 30.6891 | 12.9639 | 9.457 | 6.9163 | 30.9608 | 12.7027 | 9.2665 | 6.0853 | 31.2606 | 12.4198 | 9.0601 | 5.2175 | 31.5979 | 12.1025 | 8.8286 | 4.2185 | 32.8689 | 10.7792 | 7.8633 | -0.10344 | 33.9326 | 9.2358 | 6.7374 | -5.4034 | 34.4582 | 8.1625 | 5.9544 | -9.0194 | 34.715 | 7.4484 | 5.4335 | -11.2474 | 29.0935 | 14.3156 | 10.443 | 9.9462 | 29.3454 | 14.171 | 10.3375 | 9.2457 | 29.6615 | 14.1072 | 10.291 | 8.9134 | 29.8771 | 13.9281 | 10.1603 | 8.5442 | 30.103 | 13.7996 | 10.0666 | 8.0848 | 30.3762 | 13.6121 | 9.9299 | 7.4868 | 30.691 | 13.3012 | 9.7031 | 6.7647 | 30.9473 | 13.1137 | 9.5663 | 5.9822 | 31.2478 | 12.8261 | 9.3565 | 5.0694 | 31.6427 | 12.3963 | 9.043 | 3.5385 | 32.9041 | 10.5764 | 7.7153 | -2.5057 | 33.6317 | 8.9475 | 6.527 | -7.4957 | 33.8448 | 7.9036 | 5.7656 | -10.8599 | 33.7213 | 7.819 | 5.7039 | -9.9012
HARPURHEY | RED BANK | WHITEGATE | 385907 | 402469 | 31.8205 | 13.0616 | 9.5282 | 13.908 | 31.8861 | 13.0216 | 9.4991 | 13.6323 | 31.9124 | 12.9399 | 9.4395 | 13.4618 | 31.9757 | 12.7708 | 9.3161 | 13.1267 | 32.0682 | 12.6994 | 9.264 | 12.7967 | 32.1847 | 12.57 | 9.1697 | 12.3621 | 32.3134 | 12.4428 | 9.0768 | 11.9415 | 32.4535 | 12.2874 | 8.9635 | 11.4549 | 32.6029 | 12.1346 | 8.852 | 10.9394 | 32.7686 | 11.9569 | 8.7224 | 10.3755 | 33.3813 | 11.1764 | 8.1531 | 8.2512 | 33.8122 | 10.3265 | 7.533 | 7.0592 | 34.0707 | 10.3553 | 7.554 | 6.6665 | 34.2261 | 10.3012 | 7.5146 | 6.6684 | 31.7751 | 13.1283 | 9.5769 | 13.961 | 31.8064 | 13.0513 | 9.5208 | 13.7628 | 31.8706 | 12.9722 | 9.4631 | 13.5069 | 31.9541 | 12.8806 | 9.3962 | 13.1861 | 32.0531 | 12.816 | 9.3491 | 12.9332 | 32.1647 | 12.7157 | 9.2759 | 12.5387 | 32.2869 | 12.6158 | 9.2031 | 12.1727 | 32.4184 | 12.5 | 9.1186 | 11.7305 | 32.5587 | 12.3907 | 9.0388 | 11.2544 | 32.7073 | 12.2727 | 8.9528 | 10.7994 | 33.035 | 11.9202 | 8.6956 | 9.215 | 33.2848 | 11.6082 | 8.468 | 8.0689 | 33.4363 | 11.5311 | 8.4118 | 7.4125 | 33.5321 | 11.5235 | 8.4063 | 6.9406 | 31.8205 | 13.1242 | 9.5739 | 13.901 | 31.8861 | 13.011 | 9.4913 | 13.6416 | 31.9124 | 12.9121 | 9.4192 | 13.4884 | 31.9758 | 12.8132 | 9.347 | 13.177 | 32.0681 | 12.7086 | 9.2708 | 12.8592 | 32.1839 | 12.6036 | 9.1941 | 12.4466 | 32.3122 | 12.4646 | 9.0928 | 12.0471 | 32.4519 | 12.3413 | 9.0028 | 11.582 | 32.5995 | 12.1979 | 8.8982 | 11.0958 | 32.7574 | 12.0629 | 8.7997 | 10.5883 | 33.3435 | 11.4962 | 8.3863 | 8.6775 | 33.7372 | 10.9858 | 8.014 | 7.6395 | 33.9761 | 10.8633 | 7.9247 | 7.2961 | 34.1182 | 10.9003 | 7.9516 | 7.294 | 31.8156 | 13.0564 | 9.5245 | 13.9078 | 31.8799 | 13.0056 | 9.4874 | 13.6316 | 31.9161 | 12.9207 | 9.4255 | 13.4517 | 32.0022 | 12.7231 | 9.2814 | 13.0894 | 32.131 | 12.6696 | 9.2423 | 12.7846 | 32.2993 | 12.5331 | 9.1427 | 12.3527 | 32.4984 | 12.3207 | 8.9878 | 11.9051 | 32.726 | 12.1997 | 8.8995 | 11.3853 | 32.9417 | 12.0214 | 8.7694 | 10.9106 | 33.1623 | 11.8194 | 8.6221 | 10.4541 | 34.0062 | 10.7464 | 7.8394 | 7.6779 | 34.7155 | 9.0905 | 6.6314 | 2.1391 | 35.1195 | 8.3353 | 6.0805 | -2.1779 | 35.3474 | 7.6719 | 5.5965 | -5.3033 | 31.7999 | 13.0655 | 9.5311 | 13.953 | 31.8612 | 13.023 | 9.5001 | 13.6735 | 31.8976 | 12.9212 | 9.4258 | 13.5021 | 31.9745 | 12.7496 | 9.3006 | 13.1964 | 32.0926 | 12.5758 | 9.1739 | 12.9111 | 32.2424 | 12.4186 | 9.0592 | 12.5472 | 32.4253 | 12.3022 | 8.9743 | 12.1731 | 32.6281 | 12.1505 | 8.8636 | 11.7397 | 32.8256 | 11.9619 | 8.7261 | 11.2182 | 33.1051 | 11.6153 | 8.4732 | 9.9042 | 33.9795 | 9.9663 | 7.2703 | 3.6431 | 34.5049 | 8.792 | 6.4137 | -1.352 | 34.6822 | 8.3435 | 6.0865 | -4.241 | 34.5874 | 8.1571 | 5.9505 | -3.6633
HARWOOD | BOLTON | KEARSLEY | 374043 | 410941 | 24.8718 | 11.4285 | 8.2139 | 6.6022 | 24.947 | 11.3368 | 8.148 | 6.2127 | 25.0079 | 11.2559 | 8.0898 | 6.0398 | 25.1027 | 11.0836 | 7.966 | 5.4929 | 25.2291 | 10.9748 | 7.8878 | 5.3196 | 25.3825 | 10.7637 | 7.7361 | 4.5435 | 25.5589 | 10.6042 | 7.6215 | 4.096 | 25.753 | 10.3947 | 7.4709 | 3.551 | 25.9632 | 10.0886 | 7.2509 | 2.8962 | 26.1868 | 10.0585 | 7.2292 | 2.1554 | 26.8958 | 9.5925 | 6.8944 | -0.38531 | 27.3772 | 9.2695 | 6.6622 | -1.4078 | 27.6484 | 9.1048 | 6.5438 | -1.4951 | 27.8009 | 8.918 | 6.4095 | -0.95151 | 24.8383 | 11.4187 | 8.2068 | 6.7118 | 24.8886 | 11.3174 | 8.1341 | 6.4131 | 24.9756 | 11.2277 | 8.0696 | 6.1894 | 25.0752 | 11.0768 | 7.9611 | 5.6914 | 25.1889 | 10.9982 | 7.9046 | 5.596 | 25.3177 | 10.8167 | 7.7742 | 4.9128 | 25.4624 | 10.7228 | 7.7067 | 4.5522 | 25.6191 | 10.5988 | 7.6176 | 4.0984 | 25.7858 | 10.4723 | 7.5267 | 3.7205 | 25.9219 | 10.3083 | 7.4088 | 3.1265 | 26.2578 | 9.9535 | 7.1538 | 1.5164 | 26.5047 | 9.8454 | 7.0761 | 0.38444 | 26.6407 | 9.7755 | 7.0259 | -0.36052 | 26.7132 | 9.7298 | 6.993 | -0.61567 | 24.8718 | 11.4163 | 8.2051 | 6.6157 | 24.947 | 11.3011 | 8.1223 | 6.2381 | 25.0079 | 11.1809 | 8.0359 | 6.0756 | 25.1027 | 10.9598 | 7.877 | 5.5417 | 25.2284 | 10.8186 | 7.7755 | 5.3793 | 25.3808 | 10.5495 | 7.5822 | 4.6211 | 25.5562 | 10.4857 | 7.5363 | 4.1866 | 25.7497 | 10.4528 | 7.5126 | 3.6544 | 25.9566 | 10.4077 | 7.4802 | 3.083 | 26.1712 | 10.2976 | 7.4011 | 2.4184 | 26.8329 | 9.8978 | 7.1137 | 0.12885 | 27.2755 | 9.6477 | 6.934 | -0.72515 | 27.5265 | 9.4761 | 6.8106 | -0.78366 | 27.673 | 9.2586 | 6.6543 | -0.26885 | 24.8692 | 11.4301 | 8.215 | 6.609 | 24.9493 | 11.3427 | 8.1522 | 6.2269 | 25.0327 | 11.2471 | 8.0835 | 6.0686 | 25.1671 | 11.0629 | 7.9511 | 5.5421 | 25.3546 | 10.9524 | 7.8717 | 5.407 | 25.5919 | 10.7289 | 7.7111 | 4.6676 | 25.8555 | 10.5342 | 7.5712 | 4.2194 | 26.0951 | 10.262 | 7.3755 | 3.6758 | 26.3602 | 10.194 | 7.3266 | 3.2975 | 26.6578 | 10.1416 | 7.2889 | 2.7413 | 27.6232 | 9.3536 | 6.7226 | -0.27137 | 28.4277 | 7.9059 | 5.6822 | -6.5079 | 28.885 | 6.6806 | 4.8015 | -11.4621 | 29.1486 | 5.7943 | 4.1645 | -14.6514 | 24.8669 | 11.43 | 8.2149 | 6.5979 | 24.963 | 11.3806 | 8.1795 | 6.1673 | 25.0541 | 11.3048 | 8.125 | 6.0135 | 25.1825 | 11.0987 | 7.9769 | 5.5312 | 25.3622 | 10.9221 | 7.8499 | 5.4235 | 25.5788 | 10.739 | 7.7183 | 4.7487 | 25.8137 | 10.7244 | 7.7078 | 4.3813 | 26.0262 | 10.6433 | 7.6495 | 3.9385 | 26.266 | 10.5648 | 7.5931 | 3.424 | 26.5792 | 10.2373 | 7.3578 | 1.8442 | 27.5709 | 8.6285 | 6.2015 | -5.4187 | 28.1316 | 7.183 | 5.1625 | -10.9371 | 28.3106 | 6.2918 | 4.522 | -14.1961 | 28.1872 | 6.2977 | 4.5263 | -12.9327
HATTERSLEY | HYDE | STALYBRIDGE | 398419 | 395120 | 14.0685 | 5.348 | 3.8437 | 9.4807 | 14.1651 | 5.3944 | 3.877 | 9.1733 | 14.3244 | 5.2911 | 3.8028 | 8.8825 | 14.5105 | 4.6969 | 3.3757 | 6.5256 | 14.7324 | 4.0983 | 2.9455 | 2.2051 | 14.8575 | 3.998 | 2.8734 | 1.726 | 14.9727 | 3.835 | 2.7563 | 1.2569 | 15.0991 | 3.7234 | 2.6761 | 0.80018 | 15.2352 | 3.5827 | 2.575 | 0.31523 | 15.3864 | 3.4515 | 2.4807 | -0.27027 | 16.0281 | 3.1911 | 2.2935 | -2.2501 | 16.5112 | 5.2691 | 3.787 | -3.2211 | 16.8088 | 9.3501 | 6.7201 | -3.377 | 17.0145 | 10.1574 | 7.3003 | -3.1275 | 14.0773 | 5.4778 | 3.937 | 9.6229 | 14.1813 | 5.348 | 3.8437 | 9.4371 | 14.3436 | 5.305 | 3.8128 | 9.1241 | 14.5045 | 4.9668 | 3.5697 | 7.3238 | 14.671 | 4.4234 | 3.1792 | 4.0859 | 14.746 | 4.3303 | 3.1122 | 3.707 | 14.8294 | 4.2378 | 3.0458 | 3.3372 | 14.9181 | 4.1376 | 2.9738 | 2.9777 | 15.0119 | 4.0398 | 2.9034 | 2.5867 | 15.1085 | 3.9203 | 2.8176 | 2.1645 | 15.3787 | 3.8758 | 2.7856 | 0.8932 | 15.5883 | 5.2317 | 3.7601 | 0.029875 | 15.7316 | 7.7593 | 5.5768 | -0.3892 | 15.8214 | 8.5272 | 6.1286 | -0.56094 | 14.0685 | 5.4751 | 3.935 | 9.4849 | 14.1652 | 5.3685 | 3.8584 | 9.1813 | 14.3244 | 5.2743 | 3.7907 | 8.8949 | 14.5106 | 4.9121 | 3.5304 | 6.5431 | 14.7313 | 4.3385 | 3.1181 | 2.2293 | 14.8567 | 4.1916 | 3.0126 | 1.759 | 14.9714 | 4.1448 | 2.979 | 1.2981 | 15.0975 | 4.0604 | 2.9183 | 0.84851 | 15.2315 | 3.952 | 2.8404 | 0.37791 | 15.3744 | 3.8322 | 2.7543 | -0.16189 | 15.9705 | 3.6313 | 2.6099 | -1.9765 | 16.3989 | 5.8948 | 4.2367 | -2.8361 | 16.6673 | 9.9563 | 7.1558 | -2.963 | 16.8466 | 10.8308 | 7.7843 | -2.7265 | 14.068 | 5.3256 | 3.8276 | 9.4921 | 14.1627 | 5.3986 | 3.8801 | 9.1933 | 14.313 | 5.2215 | 3.7528 | 8.9143 | 14.4831 | 4.799 | 3.4492 | 6.5735 | 14.6792 | 4.106 | 2.9511 | 2.2798 | 14.8886 | 3.9245 | 2.8206 | 1.8265 | 15.1188 | 3.7711 | 2.7104 | 1.3681 | 15.3524 | 3.6465 | 2.6208 | 0.9225 | 15.5737 | 3.4986 | 2.5145 | 0.5059 | 15.7911 | 3.3428 | 2.4025 | 0.04813 | 16.6451 | 2.7891 | 2.0046 | -2.2976 | 17.499 | 4.1417 | 2.9767 | -6.196 | 17.9474 | 7.6429 | 5.4931 | -8.9431 | 18.1555 | 7.9636 | 5.7236 | -10.7585 | 14.0844 | 5.3219 | 3.825 | 9.4617 | 14.2196 | 5.3927 | 3.8759 | 9.0865 | 14.3839 | 5.2759 | 3.7919 | 8.7743 | 14.5437 | 4.7718 | 3.4296 | 6.4401 | 14.7242 | 4.1436 | 2.9781 | 2.1587 | 14.9026 | 3.975 | 2.8569 | 1.7482 | 15.1052 | 3.8349 | 2.7562 | 1.3359 | 15.2984 | 3.8679 | 2.7799 | 0.95986 | 15.4922 | 3.9178 | 2.8158 | 0.52434 | 15.7977 | 3.9236 | 2.82 | -0.49855 | 16.8046 | 10.2522 | 7.3684 | -5.0485 | 17.325 | 9.2384 | 6.6398 | -8.3771 | 17.484 | 8.7035 | 6.2554 | -10.0359 | 17.398 | 8.6232 | 6.1977 | -9.2887
HAVERTHWAITE | ULVERSTON | HARKER / HUTTON | 334234 | 483827 | 12.4712 | 12.4712 | 12.4712 | 5.8214 | 12.4946 | 12.4946 | 12.4946 | 5.5136 | 12.5151 | 12.5151 | 12.5151 | 5.4189 | 12.5397 | 12.5397 | 12.5397 | 5.2074 | 12.5689 | 12.5689 | 12.5689 | 5.1913 | 12.6038 | 12.6038 | 12.6038 | 5.0503 | 12.647 | 12.647 | 12.647 | 4.8429 | 12.6924 | 12.6924 | 12.6924 | 4.6716 | 12.7369 | 12.7369 | 12.7369 | 4.4941 | 12.8057 | 12.8057 | 12.8057 | 4.2795 | 13.0715 | 13.0715 | 13.0715 | 3.4816 | 13.2603 | 13.2603 | 13.2603 | 3.0964 | 13.365 | 13.365 | 13.365 | 2.9812 | 13.4464 | 13.4464 | 13.4464 | 3.1807 | 12.4679 | 12.4679 | 12.4679 | 6.0221 | 12.4878 | 12.4878 | 12.4878 | 5.8863 | 12.5144 | 12.5144 | 12.5144 | 5.7271 | 12.5379 | 12.5379 | 12.5379 | 5.4837 | 12.5613 | 12.5613 | 12.5613 | 5.4356 | 12.5879 | 12.5879 | 12.5879 | 5.2752 | 12.6187 | 12.6187 | 12.6187 | 5.0416 | 12.652 | 12.652 | 12.652 | 4.8324 | 12.6879 | 12.6879 | 12.6879 | 4.6104 | 12.7263 | 12.7263 | 12.7263 | 4.3946 | 12.8423 | 12.8423 | 12.8423 | 3.9089 | 12.9994 | 12.9994 | 12.9994 | 3.4659 | 13.0911 | 13.0911 | 13.0911 | 3.1391 | 13.1626 | 13.1626 | 13.1626 | 3.0053 | 12.4712 | 12.4712 | 12.4712 | 5.8271 | 12.4947 | 12.4947 | 12.4947 | 5.5259 | 12.5152 | 12.5152 | 12.5152 | 5.4375 | 12.54 | 12.54 | 12.54 | 5.2344 | 12.5692 | 12.5692 | 12.5692 | 5.2233 | 12.6039 | 12.6039 | 12.6039 | 5.0901 | 12.647 | 12.647 | 12.647 | 4.8916 | 12.6926 | 12.6926 | 12.6926 | 4.7287 | 12.7367 | 12.7367 | 12.7367 | 4.562 | 12.803 | 12.803 | 12.803 | 4.3661 | 13.0455 | 13.0455 | 13.0455 | 3.611 | 13.2065 | 13.2065 | 13.2065 | 3.2536 | 13.294 | 13.294 | 13.294 | 3.1412 | 13.3476 | 13.3476 | 13.3476 | 3.3484 | 12.4721 | 12.4721 | 12.4721 | 5.8362 | 12.4981 | 12.4981 | 12.4981 | 5.5375 | 12.5257 | 12.5257 | 12.5257 | 5.4531 | 12.5603 | 12.5603 | 12.5603 | 5.2575 | 12.6045 | 12.6045 | 12.6045 | 5.247 | 12.6617 | 12.6617 | 12.6617 | 5.1122 | 12.7373 | 12.7373 | 12.7373 | 4.9045 | 12.8161 | 12.8161 | 12.8161 | 4.7362 | 12.8956 | 12.8956 | 12.8956 | 4.5825 | 12.9828 | 12.9828 | 12.9828 | 4.4436 | 13.3124 | 13.3124 | 13.3124 | 3.6928 | 13.5485 | 13.5485 | 13.5485 | 2.5718 | 13.6708 | 13.6708 | 13.6708 | 1.8741 | 13.7236 | 13.7236 | 13.7236 | 1.5133 | 12.4753 | 12.4753 | 12.4753 | 5.8007 | 12.5097 | 12.5097 | 12.5097 | 5.4758 | 12.5403 | 12.5403 | 12.5403 | 5.4018 | 12.5745 | 12.5745 | 12.5745 | 5.2168 | 12.619 | 12.619 | 12.619 | 5.2085 | 12.6754 | 12.6754 | 12.6754 | 5.0851 | 12.7497 | 12.7497 | 12.7497 | 4.8961 | 12.8224 | 12.8224 | 12.8224 | 4.7547 | 12.9009 | 12.9009 | 12.9009 | 4.6217 | 13.0032 | 13.0032 | 13.0032 | 4.3188 | 13.2856 | 13.2856 | 13.2856 | 2.8159 | 13.4686 | 13.4686 | 13.4686 | 1.827 | 13.5234 | 13.5234 | 13.5234 | 1.3983 | 13.5067 | 13.5067 | 13.5067 | 1.7989
HAWK GREEN | HAZEL GROVE | BREDBURY | 395915 | 387138 | 29.7541 | 16.7273 | 12.0223 | 15.9144 | 29.8119 | 16.6508 | 11.9672 | 15.6668 | 29.862 | 16.529 | 11.8797 | 15.307 | 29.9321 | 16.3962 | 11.7842 | 15.0158 | 30.0206 | 16.2371 | 11.6699 | 14.7082 | 30.1255 | 16.0829 | 11.5591 | 14.3008 | 30.2445 | 16.02 | 11.5139 | 13.7139 | 30.374 | 15.9589 | 11.47 | 13.3114 | 30.5121 | 15.8917 | 11.4217 | 12.9525 | 30.6694 | 15.7432 | 11.315 | 12.3211 | 31.2627 | 15.1808 | 10.9108 | 10.2761 | 31.6929 | 14.7484 | 10.5999 | 9.2582 | 31.9559 | 14.4821 | 10.4086 | 9.0036 | 32.1183 | 14.3486 | 10.3126 | 9.4542 | 29.7455 | 16.7501 | 12.0386 | 16.0805 | 29.7999 | 16.6378 | 11.9579 | 15.9795 | 29.8765 | 16.5231 | 11.8754 | 15.5454 | 29.9609 | 16.4367 | 11.8134 | 15.3008 | 30.0567 | 16.3587 | 11.7573 | 15.0709 | 30.1648 | 16.2557 | 11.6833 | 14.7392 | 30.2862 | 16.0841 | 11.56 | 14.2292 | 30.4187 | 16.0216 | 11.515 | 13.892 | 30.5634 | 15.9871 | 11.4902 | 13.574 | 30.7195 | 15.9249 | 11.4456 | 13.1165 | 30.952 | 15.7554 | 11.3237 | 11.8938 | 31.1333 | 15.5398 | 11.1688 | 10.8917 | 31.2582 | 15.3996 | 11.068 | 10.1906 | 31.3416 | 15.2781 | 10.9807 | 9.8905 | 29.7541 | 16.7454 | 12.0352 | 15.9218 | 29.8119 | 16.6796 | 11.9879 | 15.6714 | 29.862 | 16.5404 | 11.8879 | 15.3257 | 29.9321 | 16.4017 | 11.7883 | 15.0496 | 30.0202 | 16.2626 | 11.6883 | 14.7589 | 30.1244 | 16.1815 | 11.63 | 14.37 | 30.2429 | 16.1317 | 11.5941 | 13.8037 | 30.3721 | 16.087 | 11.562 | 13.4183 | 30.5083 | 16.0275 | 11.5193 | 13.0807 | 30.658 | 15.9325 | 11.451 | 12.5089 | 31.2154 | 15.5554 | 11.1799 | 10.6364 | 31.6144 | 15.236 | 10.9504 | 9.7369 | 31.8598 | 14.9513 | 10.7458 | 9.5399 | 32.0155 | 14.7619 | 10.6096 | 9.9759 | 29.7531 | 16.7286 | 12.0232 | 15.9311 | 29.8154 | 16.6459 | 11.9637 | 15.6929 | 29.8802 | 16.504 | 11.8618 | 15.3481 | 29.9733 | 16.3539 | 11.7539 | 15.0908 | 30.0971 | 16.1732 | 11.624 | 14.8233 | 30.2515 | 16.1063 | 11.5759 | 14.4431 | 30.4383 | 16.0133 | 11.5091 | 13.8396 | 30.6509 | 15.9317 | 11.4505 | 13.4155 | 30.8854 | 15.8217 | 11.3714 | 13.1011 | 31.1465 | 15.7217 | 11.2995 | 12.6394 | 31.9631 | 14.8731 | 10.6896 | 10.4204 | 32.6101 | 13.6757 | 9.829 | 6.1627 | 32.9712 | 12.7521 | 9.1652 | 3.1265 | 33.1935 | 12.0764 | 8.6796 | 1.1796 | 29.7504 | 16.7263 | 12.0215 | 15.9089 | 29.82 | 16.6144 | 11.9411 | 15.6072 | 29.8842 | 16.4366 | 11.8133 | 15.2636 | 29.9698 | 16.186 | 11.6332 | 15.0201 | 30.0854 | 16.2285 | 11.6638 | 14.7489 | 30.2231 | 16.2398 | 11.6718 | 14.4032 | 30.3928 | 16.0875 | 11.5624 | 13.8755 | 30.5779 | 16.0193 | 11.5134 | 13.5542 | 30.7816 | 15.9218 | 11.4433 | 13.2374 | 31.0347 | 15.6291 | 11.233 | 12.1407 | 31.8268 | 14.3053 | 10.2815 | 7.3121 | 32.2682 | 13.2105 | 9.4946 | 3.7406 | 32.4125 | 12.5921 | 9.0502 | 1.8224 | 32.3596 | 12.4794 | 8.9692 | 2.7168
HAYDOCK | GOLBORNE | BOLD | 357489 | 397336 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 4.821 | 0.79374 | 0.57048 | 3.1572 | 11.349 | 1.8685 | 1.3429 | 1.5671 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 9.5373 | 1.5702 | 1.1286 | 4.7639 | 16.508 | 2.7179 | 1.9534 | 3.9301 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -2.3756 | 2.6844 | 0.44197 | 0.31765 | -9.6166 | 2.6844 | 0.44197 | 0.31765 | -14.1223 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 10.9323 | 1.7999 | 1.2936 | 0.2993 | 2.6844 | 0.44197 | 0.31765 | -7.9913 | 2.6844 | 0.44197 | 0.31765 | -12.9496 | 2.6844 | 0.44197 | 0.31765 | -12.6203
HDA NO1 & HDA NO2 | STAINBURN & SIDDICK | HARKER / HUTTON | 301743 | 524532 | 9.5042 | 1.5648 | 1.1247 | 9.5042 | 8.8403 | 1.4555 | 1.0461 | 8.8403 | 8.3675 | 1.3776 | 0.99014 | 8.3675 | 7.4387 | 1.2247 | 0.88023 | 7.4387 | 7.2281 | 1.19 | 0.85531 | 7.2281 | 6.1688 | 1.0156 | 0.72996 | 6.1688 | 5.3076 | 0.87385 | 0.62806 | 5.3076 | 4.3013 | 0.70817 | 0.50898 | 4.3013 | 3.1965 | 0.52628 | 0.37825 | 3.1965 | 2.0389 | 0.33569 | 0.24127 | 2.0389 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 10.1505 | 1.6712 | 1.2011 | 10.1505 | 10.0757 | 1.6589 | 1.1923 | 10.0757 | 9.54 | 1.5707 | 1.1289 | 9.54 | 8.6915 | 1.431 | 1.0285 | 8.6915 | 8.6075 | 1.4172 | 1.0185 | 8.6075 | 7.7859 | 1.2819 | 0.92132 | 7.7859 | 7.2977 | 1.2015 | 0.86355 | 7.2977 | 6.5985 | 1.0864 | 0.78081 | 6.5985 | 5.7953 | 0.95416 | 0.68577 | 5.7953 | 4.9987 | 0.823 | 0.59151 | 4.9987 | 2.5415 | 0.41843 | 0.30073 | 2.5415 | 0.14449 | 0.023789 | 0.017098 | 0.14449 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 10.1444 | 1.6702 | 1.2004 | 10.1444 | 10.0346 | 1.6521 | 1.1874 | 10.0346 | 9.3761 | 1.5437 | 1.1095 | 9.3761 | 8.3087 | 1.368 | 0.98318 | 8.3087 | 7.9908 | 1.3156 | 0.94556 | 7.9908 | 6.7669 | 1.1141 | 0.80074 | 6.7669 | 5.8493 | 0.96304 | 0.69216 | 5.8493 | 4.6334 | 0.76285 | 0.54827 | 4.6334 | 3.4192 | 0.56295 | 0.4046 | 3.4192 | 2.2503 | 0.37049 | 0.26628 | 2.2503 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 9.5348 | 1.5698 | 1.1283 | 9.5348 | 8.8195 | 1.4521 | 1.0436 | 8.8195 | 8.3246 | 1.3706 | 0.98507 | 8.3246 | 7.332 | 1.2072 | 0.86761 | 7.332 | 7.0624 | 1.1628 | 0.83571 | 7.0624 | 5.8663 | 0.96584 | 0.69417 | 5.8663 | 5.0051 | 0.82406 | 0.59227 | 5.0051 | 3.9637 | 0.65259 | 0.46903 | 3.9637 | 2.9123 | 0.47948 | 0.34461 | 2.9123 | 1.968 | 0.32401 | 0.23287 | 1.968 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 9.5207 | 1.5675 | 1.1266 | 9.5207 | 8.914 | 1.4676 | 1.0548 | 8.914 | 8.3395 | 1.373 | 0.98682 | 8.3395 | 7.3278 | 1.2065 | 0.86712 | 7.3278 | 7.061 | 1.1625 | 0.83554 | 7.061 | 5.8848 | 0.96889 | 0.69636 | 5.8848 | 5.0255 | 0.82741 | 0.59467 | 5.0255 | 4.0208 | 0.66199 | 0.47578 | 4.0208 | 3.0235 | 0.49779 | 0.35777 | 3.0235 | 1.8748 | 0.30868 | 0.22185 | 1.8748 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
HDA NO1 & HDA NO2 | STAINBURN & SIDDICK | HARKER / HUTTON | 301429 | 525527 | -2.381 | -0.39201 | -0.28175 | -2.381 | -3.045 | -0.50134 | -0.36032 | -3.045 | -3.5177 | -0.57917 | -0.41626 | -3.5177 | -4.4465 | -0.73209 | -0.52617 | -4.4465 | -4.6572 | -0.76677 | -0.55109 | -4.6572 | -5.7164 | -0.94117 | -0.67644 | -5.7164 | -6.5777 | -1.083 | -0.77835 | -6.5777 | -7.584 | -1.2486 | -0.89742 | -7.584 | -8.6887 | -1.4305 | -1.0282 | -8.6887 | -9.8463 | -1.6211 | -1.1651 | -9.8463 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -1.7348 | -0.28562 | -0.20528 | -1.7348 | -1.8096 | -0.29793 | -0.21413 | -1.8096 | -2.3453 | -0.38613 | -0.27752 | -2.3453 | -3.1937 | -0.52582 | -0.37792 | -3.1937 | -3.2778 | -0.53966 | -0.38786 | -3.2778 | -4.0993 | -0.67492 | -0.48508 | -4.0993 | -4.5876 | -0.75531 | -0.54286 | -4.5876 | -5.2868 | -0.87043 | -0.62559 | -5.2868 | -6.0899 | -1.0027 | -0.72063 | -6.0899 | -6.8865 | -1.1338 | -0.8149 | -6.8865 | -9.3438 | -1.5384 | -1.1057 | -9.3438 | -11.7408 | -1.933 | -1.3893 | -11.7408 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -1.7408 | -0.28661 | -0.206 | -1.7408 | -1.8507 | -0.3047 | -0.21899 | -1.8507 | -2.5092 | -0.41311 | -0.29691 | -2.5092 | -3.5766 | -0.58886 | -0.42322 | -3.5766 | -3.8945 | -0.64119 | -0.46084 | -3.8945 | -5.1184 | -0.8427 | -0.60567 | -5.1184 | -6.036 | -0.99378 | -0.71425 | -6.036 | -7.2519 | -1.194 | -0.85813 | -7.2519 | -8.466 | -1.3939 | -1.0018 | -8.466 | -9.635 | -1.5863 | -1.1401 | -9.635 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.3505 | -0.38699 | -0.27814 | -2.3505 | -3.0658 | -0.50476 | -0.36278 | -3.0658 | -3.5606 | -0.58623 | -0.42133 | -3.5606 | -4.5533 | -0.74966 | -0.5388 | -4.5533 | -4.8228 | -0.79404 | -0.57069 | -4.8228 | -6.019 | -0.99098 | -0.71223 | -6.019 | -6.8801 | -1.1328 | -0.81414 | -6.8801 | -7.9215 | -1.3042 | -0.93737 | -7.9215 | -8.973 | -1.4773 | -1.0618 | -8.973 | -9.9173 | -1.6328 | -1.1735 | -9.9173 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.3645 | -0.3893 | -0.2798 | -2.3645 | -2.9713 | -0.4892 | -0.3516 | -2.9713 | -3.5458 | -0.58379 | -0.41958 | -3.5458 | -4.5574 | -0.75034 | -0.53929 | -4.5574 | -4.8243 | -0.79428 | -0.57087 | -4.8243 | -6.0004 | -0.98792 | -0.71004 | -6.0004 | -6.8598 | -1.1294 | -0.81173 | -6.8598 | -7.8645 | -1.2948 | -0.93062 | -7.8645 | -8.8618 | -1.459 | -1.0486 | -8.8618 | -10.0104 | -1.6481 | -1.1845 | -10.0104 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
HEADY HILL | CASTLETON | ROCHDALE | 384370 | 410583 | 24.526 | 11.0251 | 8.0427 | 8.9245 | 24.6086 | 9.4653 | 6.9048 | 8.5729 | 24.6402 | 7.8889 | 5.7548 | 8.2454 | 24.6963 | 6.2412 | 4.5529 | 8.1788 | 24.7725 | 4.4086 | 3.216 | 7.9551 | 20.1692 | 3.2716 | 2.3866 | 7.6058 | 19.9055 | 3.2289 | 2.3554 | 7.2076 | 19.312 | 3.1326 | 2.2852 | 6.9129 | 18.5056 | 3.0018 | 2.1898 | 6.128 | 17.6966 | 2.8706 | 2.094 | 5.7084 | 16.0278 | 2.5999 | 1.8966 | 4.133 | 24.1747 | 3.9214 | 2.8606 | 2.1044 | 30.7764 | 6.9121 | 5.0423 | 1.1686 | 32.2993 | 7.4463 | 5.432 | 0.1664 | 24.4766 | 11.2165 | 8.1823 | 9.1668 | 24.5212 | 9.7134 | 7.0858 | 9.0343 | 24.5942 | 8.0842 | 5.8973 | 8.6574 | 24.6805 | 6.5055 | 4.7457 | 8.5651 | 24.7789 | 5.4183 | 3.9526 | 8.3463 | 24.8921 | 4.0601 | 2.9618 | 8.005 | 24.6484 | 3.9982 | 2.9166 | 7.6099 | 24.213 | 3.9276 | 2.8651 | 7.313 | 23.8083 | 3.8619 | 2.8172 | 7.0277 | 23.1318 | 3.7522 | 2.7372 | 6.6152 | 22.4156 | 3.636 | 2.6524 | 5.3909 | 27.249 | 4.793 | 3.4964 | 4.2009 | 28.3761 | 6.5877 | 4.8056 | 3.1838 | 29.3998 | 6.6938 | 4.883 | 2.313 | 24.5281 | 11.21 | 8.1775 | 8.9329 | 24.6124 | 9.5856 | 6.9926 | 8.5838 | 24.6462 | 7.6886 | 5.6087 | 8.2672 | 24.7048 | 6.7045 | 4.8909 | 8.2021 | 24.7837 | 5.2209 | 3.8086 | 7.986 | 24.8858 | 4.0573 | 2.9597 | 7.6459 | 24.2791 | 3.9383 | 2.8729 | 7.2573 | 23.5148 | 3.8143 | 2.7825 | 6.9713 | 22.8607 | 3.7082 | 2.7051 | 6.1993 | 21.7177 | 3.5228 | 2.5699 | 5.8109 | 21.1121 | 3.4246 | 2.4982 | 4.4412 | 28.4734 | 4.6976 | 3.4268 | 2.8777 | 29.5802 | 7.8055 | 5.694 | 2.1742 | 30.4781 | 8.7486 | 6.382 | 1.6226 | 24.5242 | 11.0235 | 8.0415 | 8.9311 | 24.6076 | 9.3701 | 6.8354 | 8.5866 | 24.648 | 7.672 | 5.5966 | 8.2604 | 24.7208 | 5.9252 | 4.3223 | 8.1997 | 24.8231 | 4.8147 | 3.5123 | 7.9888 | 21.0644 | 3.4168 | 2.4925 | 7.6372 | 19.7746 | 3.2076 | 2.3399 | 7.2062 | 18.6784 | 3.0298 | 2.2102 | 6.8612 | 18.4732 | 2.9965 | 2.1859 | 6.0911 | 17.6797 | 2.8678 | 2.092 | 5.6786 | 11.4888 | 1.8636 | 1.3595 | 2.4761 | 19.0084 | 3.0833 | 2.2493 | -3.228 | 31.735 | 5.1477 | 3.7552 | -7.2746 | 31.1211 | 5.0481 | 3.6826 | -10.1501 | 24.524 | 11.0275 | 8.0444 | 8.9567 | 24.6171 | 10.6778 | 7.7893 | 8.6041 | 24.673 | 10.206 | 7.4451 | 8.3078 | 24.7608 | 9.8727 | 7.202 | 8.2408 | 24.8823 | 9.5789 | 6.9877 | 8.0464 | 25.6798 | 9.4607 | 6.9015 | 7.1256 | 26.5433 | 9.122 | 6.6544 | 6.132 | 27.3782 | 8.8075 | 6.425 | 5.3295 | 27.7594 | 8.7171 | 6.359 | 5.0024 | 28.2305 | 8.3114 | 6.0631 | 3.9089 | 31.1351 | 7.5916 | 5.5379 | -1.5343 | 33.4827 | 6.275 | 4.5775 | -6.5975 | 33.2411 | 5.392 | 3.9334 | -9.5674 | 33.0677 | 5.3639 | 3.9129 | -9.4563
HEAP BRIDGE | BURY | KEARSLEY | 382793 | 410428 | 1.4434 | 1.4434 | 1.4434 | 1.4434 | 1.5697 | 1.5697 | 1.5697 | 1.5697 | 1.6578 | 1.6578 | 1.6578 | 1.6578 | 1.6948 | 1.6948 | 1.6948 | 1.6948 | 1.7475 | 1.7475 | 1.7475 | 1.7475 | 1.8194 | 1.8194 | 1.8194 | 1.8194 | 1.8967 | 1.8967 | 1.8967 | 1.8967 | 1.9776 | 1.9776 | 1.9776 | 1.9776 | 2.0625 | 2.0625 | 2.0625 | 2.0625 | 2.1557 | 2.1557 | 2.1557 | 2.1557 | 2.7656 | 2.7656 | 2.7656 | 1.7593 | 3.4025 | 3.4025 | 3.4025 | 0.92799 | 3.9145 | 3.9145 | 3.9145 | 0.29701 | 4.3454 | 4.3454 | 4.3454 | -0.16202 | 1.3746 | 1.3746 | 1.3746 | 1.3746 | 1.4461 | 1.4461 | 1.4461 | 1.4461 | 1.5035 | 1.5035 | 1.5035 | 1.5035 | 1.5602 | 1.5602 | 1.5602 | 1.5602 | 1.6238 | 1.6238 | 1.6238 | 1.6238 | 1.6921 | 1.6921 | 1.6921 | 1.6921 | 1.7661 | 1.7661 | 1.7661 | 1.7661 | 1.8431 | 1.8431 | 1.8431 | 1.8431 | 1.9229 | 1.9229 | 1.9229 | 1.9229 | 2.0036 | 2.0036 | 2.0036 | 2.0036 | 2.3861 | 2.3861 | 2.3861 | 2.3861 | 2.8489 | 2.8489 | 2.8489 | 2.0449 | 3.3322 | 3.3322 | 3.3322 | 1.4715 | 3.6606 | 3.6606 | 3.6606 | 1.1292 | 1.4436 | 1.4436 | 1.4436 | 1.4436 | 1.5701 | 1.5701 | 1.5701 | 1.5701 | 1.6586 | 1.6586 | 1.6586 | 1.6586 | 1.6973 | 1.6973 | 1.6973 | 1.6973 | 1.7511 | 1.7511 | 1.7511 | 1.7511 | 1.8239 | 1.8239 | 1.8239 | 1.8239 | 1.9019 | 1.9019 | 1.9019 | 1.9019 | 1.9837 | 1.9837 | 1.9837 | 1.9837 | 2.0686 | 2.0686 | 2.0686 | 2.0686 | 2.1588 | 2.1588 | 2.1588 | 2.1588 | 2.6785 | 2.6785 | 2.6785 | 1.9271 | 3.0797 | 3.0797 | 3.0797 | 1.3579 | 3.4682 | 3.4682 | 3.4682 | 0.85772 | 3.795 | 3.795 | 3.795 | 0.61465 | 1.4362 | 1.4362 | 1.4362 | 1.4362 | 1.5531 | 1.5531 | 1.5531 | 1.5531 | 1.6264 | 1.6264 | 1.6264 | 1.6264 | 1.6919 | 1.6919 | 1.6919 | 1.6919 | 1.7592 | 1.7592 | 1.7592 | 1.7592 | 1.8666 | 1.8666 | 1.8666 | 1.8666 | 2.0029 | 2.0029 | 2.0029 | 2.0029 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 2.3203 | 2.3203 | 2.3203 | 2.3203 | 2.459 | 2.459 | 2.459 | 2.459 | 3.3509 | 3.3509 | 3.3509 | 1.0208 | 4.263 | 4.263 | 4.263 | -1.396 | 4.7994 | 4.7994 | 4.7994 | -3.2502 | 4.924 | 4.924 | 4.924 | -4.3639 | 1.4597 | 1.4597 | 1.4597 | 1.4597 | 1.5984 | 1.5984 | 1.5984 | 1.5984 | 1.6708 | 1.6708 | 1.6708 | 1.6708 | 1.721 | 1.721 | 1.721 | 1.721 | 1.7997 | 1.7997 | 1.7997 | 1.7997 | 1.9295 | 1.9295 | 1.9295 | 1.9295 | 2.1022 | 2.1022 | 2.1022 | 2.1022 | 2.2878 | 2.2878 | 2.2878 | 2.2878 | 2.4414 | 2.4414 | 2.4414 | 2.4414 | 2.6574 | 2.6574 | 2.6574 | 2.0713 | 3.7372 | 3.7372 | 3.7372 | -0.62451 | 4.5147 | 4.5147 | 4.5147 | -2.8456 | 4.7572 | 4.7572 | 4.7572 | -4.0818 | 4.594 | 4.594 | 4.594 | -3.8542
HEASANDFORD | BURNLEY | ROCHDALE | 385349 | 433821 | -47.8167 | -7.7563 | -5.6581 | -47.8167 | -50.3452 | -8.1665 | -5.9573 | -50.3452 | -51.6478 | -8.3778 | -6.1115 | -51.6478 | -52.3939 | -8.4988 | -6.1998 | -52.3939 | -54.3085 | -8.8094 | -6.4263 | -54.3085 | -56.2103 | -9.1179 | -6.6514 | -56.2103 | -56.4095 | -9.1502 | -6.6749 | -56.4095 | -56.5685 | -9.176 | -6.6937 | -56.5685 | -57 | -9.246 | -6.7448 | -57 | -57.3073 | -9.2958 | -6.7812 | -57.3073 | -58.2071 | -9.4418 | -6.8876 | -58.2071 | -56.8964 | -9.2292 | -6.7325 | -56.8964 | -48.2196 | -7.8217 | -5.7058 | -48.2196 | -46.4321 | -7.5317 | -5.4943 | -46.4321 | -47.0993 | -7.64 | -5.5733 | -47.0993 | -48.8965 | -7.9315 | -5.7859 | -48.8965 | -50.6957 | -8.2233 | -5.9988 | -50.6957 | -52.2428 | -8.4743 | -6.1819 | -52.2428 | -53.9292 | -8.7478 | -6.3814 | -53.9292 | -55.5784 | -9.0154 | -6.5766 | -55.5784 | -55.8275 | -9.0558 | -6.6061 | -55.8275 | -55.9356 | -9.0733 | -6.6189 | -55.9356 | -56.2477 | -9.1239 | -6.6558 | -56.2477 | -56.5223 | -9.1685 | -6.6883 | -56.5223 | -56.6887 | -9.1955 | -6.708 | -56.6887 | -55.9465 | -9.0751 | -6.6201 | -55.9465 | -50.1001 | -8.1267 | -5.9283 | -50.1001 | -45.0914 | -7.3143 | -5.3357 | -45.0914 | -47.1122 | -7.6421 | -5.5748 | -47.1122 | -49.038 | -7.9544 | -5.8027 | -49.038 | -50.9288 | -8.2611 | -6.0264 | -50.9288 | -52.8692 | -8.5759 | -6.256 | -52.8692 | -54.6513 | -8.865 | -6.4669 | -54.6513 | -56.4327 | -9.1539 | -6.6777 | -56.4327 | -56.7981 | -9.2132 | -6.7209 | -56.7981 | -56.9409 | -9.2364 | -6.7378 | -56.9409 | -57.3319 | -9.2998 | -6.7841 | -57.3319 | -57.6798 | -9.3562 | -6.8252 | -57.6798 | -58.1634 | -9.4347 | -6.8825 | -58.1634 | -56.231 | -9.1212 | -6.6538 | -56.231 | -44.768 | -7.2618 | -5.2974 | -44.768 | -43.1317 | -6.9964 | -5.1038 | -43.1317 | -47.8214 | -7.7571 | -5.6587 | -47.8214 | -50.4619 | -8.1854 | -5.9711 | -50.4619 | -51.3479 | -8.3291 | -6.076 | -51.3479 | -52.3133 | -8.4857 | -6.1902 | -52.3133 | -54.4066 | -8.8253 | -6.4379 | -54.4066 | -56.1515 | -9.1083 | -6.6444 | -56.1515 | -56.3473 | -9.1401 | -6.6676 | -56.3473 | -56.6447 | -9.1883 | -6.7028 | -56.6447 | -57.0203 | -9.2493 | -6.7472 | -57.0203 | -57.3232 | -9.2984 | -6.783 | -57.3232 | -58.5153 | -9.4918 | -6.9241 | -58.5153 | -58.5542 | -9.4981 | -6.9287 | -58.5542 | -52.2401 | -8.4738 | -6.1816 | -52.2401 | -51.5204 | -8.3571 | -6.0964 | -51.5204 | -47.8185 | -7.7566 | -5.6584 | -47.8185 | -48.5235 | -7.871 | -5.7418 | -48.5235 | -47.7171 | -7.7402 | -5.6464 | -47.7171 | -47.9438 | -7.777 | -5.6732 | -47.9438 | -49.0192 | -7.9514 | -5.8004 | -49.0192 | -50.3822 | -8.1725 | -5.9617 | -50.3822 | -50.9442 | -8.2636 | -6.0282 | -50.9442 | -50.8951 | -8.2557 | -6.0224 | -50.8951 | -50.9882 | -8.2708 | -6.0334 | -50.9882 | -51.2995 | -8.3213 | -6.0703 | -51.2995 | -47.4632 | -7.699 | -5.6163 | -47.4632 | -50.5252 | -8.1957 | -5.9786 | -50.5252 | -51.4594 | -8.3472 | -6.0892 | -51.4594 | -51.1329 | -8.2943 | -6.0505 | -51.1329
HEATON MOOR | VERNON PARK | BREDBURY | 387623 | 391345 | 30.5018 | 9.9229 | 7.2386 | 14.7909 | 30.5518 | 9.9417 | 7.2523 | 14.3492 | 30.5936 | 9.8976 | 7.2202 | 13.9936 | 30.6648 | 9.7994 | 7.1485 | 13.5714 | 30.7569 | 9.721 | 7.0913 | 13.4169 | 30.869 | 9.6186 | 7.0166 | 12.9758 | 30.9978 | 9.4776 | 6.9138 | 12.4119 | 31.1405 | 9.3402 | 6.8136 | 12.0214 | 31.2971 | 9.2145 | 6.7219 | 11.5369 | 31.4715 | 9.0349 | 6.5908 | 10.973 | 32.3544 | 8.318 | 6.0679 | 8.9541 | 33.0962 | 7.8835 | 5.7509 | 7.8118 | 33.6048 | 7.3923 | 5.3926 | 7.26 | 34.0068 | 7.2993 | 5.3247 | 7.2517 | 30.4914 | 9.9162 | 7.2337 | 14.9404 | 30.5347 | 9.8777 | 7.2057 | 14.654 | 30.6017 | 9.7594 | 7.1194 | 14.2797 | 30.6818 | 9.6271 | 7.0228 | 13.904 | 30.7753 | 9.5546 | 6.97 | 13.7808 | 30.8837 | 9.4397 | 6.8861 | 13.4339 | 31.007 | 9.344 | 6.8163 | 12.9012 | 31.1425 | 9.2872 | 6.7749 | 12.6124 | 31.2904 | 9.2056 | 6.7153 | 12.2349 | 31.4309 | 9.1074 | 6.6437 | 11.7746 | 31.8793 | 8.812 | 6.4282 | 10.3333 | 32.2906 | 8.5567 | 6.242 | 9.3237 | 32.6092 | 8.3803 | 6.1133 | 8.6342 | 32.851 | 8.3114 | 6.063 | 8.3501 | 30.5044 | 9.9194 | 7.2361 | 14.7919 | 30.5553 | 9.8386 | 7.1771 | 14.3866 | 30.5979 | 9.7229 | 7.0928 | 14.036 | 30.6698 | 9.6033 | 7.0055 | 13.659 | 30.7619 | 9.5231 | 6.947 | 13.4869 | 30.8723 | 9.4082 | 6.8631 | 13.054 | 30.9983 | 9.2933 | 6.7793 | 12.4687 | 31.1374 | 9.2086 | 6.7175 | 12.091 | 31.2878 | 9.1088 | 6.6447 | 11.675 | 31.4495 | 8.9826 | 6.5527 | 11.1587 | 32.2428 | 8.5202 | 6.2154 | 9.2868 | 32.8345 | 8.1785 | 5.9661 | 8.3846 | 33.2254 | 7.944 | 5.795 | 8.092 | 33.4923 | 7.6949 | 5.6133 | 8.2768 | 30.5026 | 9.9276 | 7.2421 | 14.8006 | 30.5558 | 9.9532 | 7.2607 | 14.3717 | 30.6103 | 9.9037 | 7.2246 | 14.0389 | 30.7053 | 9.7825 | 7.1362 | 13.6445 | 30.8329 | 9.6976 | 7.0743 | 13.5248 | 31.003 | 9.5955 | 6.9998 | 13.1588 | 31.2145 | 9.4377 | 6.8847 | 12.6214 | 31.461 | 9.2969 | 6.782 | 12.2991 | 31.7358 | 9.1341 | 6.6632 | 11.8755 | 31.9925 | 8.9541 | 6.5319 | 11.4852 | 33.2617 | 7.9451 | 5.7958 | 8.7166 | 34.6131 | 6.63 | 4.8365 | 3.7873 | 33.5466 | 5.4416 | 3.9696 | -0.1158 | 29.9319 | 4.8552 | 3.5418 | -2.3675 | 30.5022 | 9.9252 | 7.2403 | 14.778 | 30.5668 | 10.0303 | 7.317 | 14.293 | 30.6276 | 10.0057 | 7.299 | 13.965 | 30.7221 | 9.9215 | 7.2376 | 13.6011 | 30.8498 | 9.8698 | 7.1999 | 13.5251 | 31.0244 | 9.6759 | 7.0584 | 13.1502 | 31.2518 | 9.4423 | 6.888 | 12.6435 | 31.5161 | 9.2756 | 6.7664 | 12.3505 | 31.8202 | 9.1819 | 6.6981 | 11.8717 | 32.1922 | 8.8919 | 6.4865 | 10.7252 | 33.472 | 7.4182 | 5.4115 | 5.0297 | 34.5203 | 6.0793 | 4.4348 | 0.55722 | 32.2939 | 5.2384 | 3.8213 | -2.0586 | 32.4631 | 5.2658 | 3.8414 | -1.1545
HEATON NORRIS | VERNON PARK | BREDBURY | 388860 | 391967 | 27.562 | 10.9045 | 7.9547 | 9.87 | 27.6607 | 9.7772 | 7.1324 | 9.0417 | 27.6896 | 8.5279 | 6.221 | 8.9956 | 27.7574 | 7.6814 | 5.6035 | 8.5249 | 27.8493 | 6.7849 | 4.9495 | 8.6542 | 27.9613 | 5.7822 | 4.2181 | 8.2515 | 28.0824 | 5.6386 | 4.1132 | 7.6988 | 30.8325 | 5.1305 | 3.7426 | 4.8646 | 30.8841 | 5.0264 | 3.6667 | 4.4985 | 30.0051 | 4.8671 | 3.5505 | 4.037 | 23.8238 | 3.8644 | 2.8191 | -1.3311 | 30.852 | 5.0045 | 3.6507 | -2.3464 | 36.7447 | 8.2068 | 5.9868 | -2.7454 | 36.5658 | 9.9066 | 7.2267 | -2.2998 | 27.4792 | 10.9468 | 7.9855 | 10.2458 | 27.5136 | 9.8654 | 7.1967 | 9.7421 | 27.5832 | 8.8566 | 6.4608 | 9.6504 | 27.6547 | 7.7746 | 5.6714 | 9.1326 | 27.7395 | 6.7837 | 4.9486 | 9.1306 | 27.8342 | 5.7395 | 4.1869 | 8.7329 | 27.9387 | 5.5703 | 4.0635 | 8.2185 | 28.0471 | 5.4719 | 3.9917 | 7.9938 | 28.1607 | 5.3308 | 3.8887 | 7.5582 | 28.2762 | 5.2213 | 3.8089 | 7.0932 | 28.7052 | 5.2816 | 3.8529 | 5.9514 | 29.1673 | 6.1131 | 4.4594 | 5.0294 | 29.5535 | 8.4701 | 6.1788 | 4.3114 | 29.8493 | 9.6762 | 7.0587 | 4.0043 | 27.5621 | 10.9437 | 7.9833 | 9.8768 | 27.6609 | 9.8792 | 7.2068 | 9.0517 | 27.69 | 8.8483 | 6.4547 | 9.0109 | 27.7581 | 7.7472 | 5.6515 | 8.5537 | 27.8501 | 6.7151 | 4.8985 | 8.6925 | 27.9619 | 5.602 | 4.0866 | 8.3028 | 28.0829 | 5.4228 | 3.9558 | 7.7492 | 30.8329 | 5.4289 | 3.9603 | 4.989 | 30.8833 | 5.3763 | 3.922 | 4.6444 | 30.9663 | 5.3002 | 3.8664 | 4.2318 | 31.9939 | 5.1897 | 3.7858 | -0.96435 | 36.2817 | 6.4372 | 4.6958 | -1.8313 | 36.5347 | 9.7318 | 7.0992 | -2.2241 | 36.277 | 11.3601 | 8.287 | -1.7259 | 27.5538 | 10.9084 | 7.9575 | 9.8941 | 27.6534 | 9.7715 | 7.1282 | 9.0879 | 27.6962 | 8.522 | 6.2167 | 9.0573 | 27.7882 | 7.7056 | 5.6211 | 8.5949 | 27.9217 | 6.7856 | 4.95 | 8.7205 | 28.1064 | 5.7424 | 4.189 | 8.2956 | 28.3429 | 5.5692 | 4.0627 | 7.6711 | 31.1639 | 5.0777 | 3.7041 | 5.0584 | 30.3129 | 4.917 | 3.5869 | 4.6075 | 29.2628 | 4.7467 | 3.4627 | 4.1971 | 21.2664 | 3.4496 | 2.5164 | -2.1294 | 23.4793 | 3.8086 | 2.7783 | -6.4115 | 37.2983 | 6.2062 | 4.5273 | -10.1907 | 36.9949 | 7.5563 | 5.5122 | -11.9173 | 27.5415 | 10.9117 | 7.9599 | 9.904 | 27.6396 | 10.6815 | 7.792 | 9.0711 | 27.681 | 10.4998 | 7.6594 | 9.0265 | 27.7714 | 10.5653 | 7.7072 | 8.5831 | 27.9171 | 10.5408 | 7.6893 | 8.7175 | 28.1073 | 10.4095 | 7.5936 | 8.3207 | 28.3401 | 10.2083 | 7.4468 | 7.7056 | 31.1548 | 9.6786 | 7.0604 | 5.1401 | 31.3967 | 9.5089 | 6.9366 | 4.6552 | 34.462 | 8.8353 | 6.4452 | 0.73538 | 36.55 | 7.3161 | 5.337 | -5.606 | 36.8007 | 6.3763 | 4.6515 | -9.4334 | 36.9198 | 7.8839 | 5.7512 | -11.9222 | 36.3454 | 7.9404 | 5.7924 | -10.5536
HELWITH BRIDGE | PADIHAM | PADIHAM | 381025 | 469428 | 12.0289 | 12.0289 | 12.0289 | 8.8209 | 12.0411 | 12.0411 | 12.0411 | 8.7032 | 12.056 | 12.056 | 12.056 | 8.6402 | 12.0727 | 12.0727 | 12.0727 | 8.5855 | 12.0924 | 12.0924 | 12.0924 | 8.5241 | 12.1149 | 12.1149 | 12.1149 | 8.4521 | 12.1431 | 12.1431 | 12.1431 | 8.3735 | 12.1748 | 12.1748 | 12.1748 | 8.2917 | 12.2101 | 12.2101 | 12.2101 | 8.2044 | 12.2522 | 12.2522 | 12.2522 | 8.0897 | 12.4293 | 12.4293 | 12.4293 | 7.5683 | 12.5569 | 12.5569 | 12.5569 | 7.3411 | 12.634 | 12.634 | 12.634 | 7.2225 | 12.6921 | 12.6921 | 12.6921 | 7.2168 | 12.0317 | 12.0317 | 12.0317 | 8.8969 | 12.0456 | 12.0456 | 12.0456 | 8.8468 | 12.0591 | 12.0591 | 12.0591 | 8.786 | 12.0716 | 12.0716 | 12.0716 | 8.7401 | 12.0857 | 12.0857 | 12.0857 | 8.6907 | 12.102 | 12.102 | 12.102 | 8.6345 | 12.1214 | 12.1214 | 12.1214 | 8.5726 | 12.1427 | 12.1427 | 12.1427 | 8.5081 | 12.1658 | 12.1658 | 12.1658 | 8.4424 | 12.1903 | 12.1903 | 12.1903 | 8.3757 | 12.2632 | 12.2632 | 12.2632 | 8.0933 | 12.3295 | 12.3295 | 12.3295 | 7.8763 | 12.3818 | 12.3818 | 12.3818 | 7.7269 | 12.422 | 12.422 | 12.422 | 7.616 | 12.0289 | 12.0289 | 12.0289 | 8.8214 | 12.0412 | 12.0412 | 12.0412 | 8.7062 | 12.056 | 12.056 | 12.056 | 8.6458 | 12.0728 | 12.0728 | 12.0728 | 8.5936 | 12.0924 | 12.0924 | 12.0924 | 8.5345 | 12.1149 | 12.1149 | 12.1149 | 8.4646 | 12.1429 | 12.1429 | 12.1429 | 8.388 | 12.1745 | 12.1745 | 12.1745 | 8.308 | 12.2094 | 12.2094 | 12.2094 | 8.2244 | 12.2493 | 12.2493 | 12.2493 | 8.1203 | 12.4128 | 12.4128 | 12.4128 | 7.6607 | 12.5199 | 12.5199 | 12.5199 | 7.4672 | 12.5868 | 12.5868 | 12.5868 | 7.3667 | 12.632 | 12.632 | 12.632 | 7.3708 | 12.0299 | 12.0299 | 12.0299 | 8.8218 | 12.0435 | 12.0435 | 12.0435 | 8.6998 | 12.0624 | 12.0624 | 12.0624 | 8.6303 | 12.0849 | 12.0849 | 12.0849 | 8.568 | 12.1137 | 12.1137 | 12.1137 | 8.4918 | 12.1493 | 12.1493 | 12.1493 | 8.3995 | 12.1959 | 12.1959 | 12.1959 | 8.2916 | 12.2504 | 12.2504 | 12.2504 | 8.1777 | 12.3117 | 12.3117 | 12.3117 | 8.0649 | 12.3817 | 12.3817 | 12.3817 | 7.9454 | 12.6248 | 12.6248 | 12.6248 | 7.412 | 12.8009 | 12.8009 | 12.8009 | 6.7304 | 12.8874 | 12.8874 | 12.8874 | 6.2901 | 12.8481 | 12.8481 | 12.8481 | 6.0007 | 12.0349 | 12.0349 | 12.0349 | 8.8136 | 12.0494 | 12.0494 | 12.0494 | 8.6787 | 12.0716 | 12.0716 | 12.0716 | 8.6035 | 12.0962 | 12.0962 | 12.0962 | 8.5363 | 12.1274 | 12.1274 | 12.1274 | 8.4513 | 12.1636 | 12.1636 | 12.1636 | 8.356 | 12.2088 | 12.2088 | 12.2088 | 8.2499 | 12.26 | 12.26 | 12.26 | 8.142 | 12.3167 | 12.3167 | 12.3167 | 8.0334 | 12.3823 | 12.3823 | 12.3823 | 7.8297 | 12.6001 | 12.6001 | 12.6001 | 6.9729 | 12.7231 | 12.7231 | 12.7231 | 6.3912 | 12.756 | 12.756 | 12.756 | 6.1141 | 12.7389 | 12.7389 | 12.7389 | 6.2196
HENSINGHAM | EGREMONT | HARKER / HUTTON | 298465 | 517239 | 25.97 | 12.9698 | 9.3217 | 17.1071 | 26.0082 | 12.9181 | 9.2845 | 16.8893 | 26.0058 | 12.8815 | 9.2582 | 16.9067 | 26.0308 | 12.7658 | 9.175 | 16.6925 | 26.0739 | 12.699 | 9.127 | 16.663 | 26.1339 | 12.5624 | 9.0289 | 16.3565 | 26.2012 | 12.3853 | 8.9015 | 16.0468 | 26.2748 | 12.1357 | 8.7222 | 15.8428 | 26.3537 | 12.0201 | 8.6391 | 15.5323 | 26.445 | 12.0404 | 8.6537 | 15.1661 | 26.8205 | 11.8212 | 8.4961 | 13.9239 | 27.1072 | 12.1099 | 8.7036 | 13.3392 | 27.2713 | 15.4717 | 11.1198 | 13.2914 | 27.3611 | 15.4094 | 11.075 | 13.6807 | 25.919 | 12.9873 | 9.3342 | 17.143 | 25.9177 | 12.9514 | 9.3084 | 16.9948 | 25.9446 | 12.9369 | 9.298 | 16.957 | 25.9814 | 12.9331 | 9.2953 | 16.744 | 26.0259 | 12.9616 | 9.3158 | 16.7231 | 26.0781 | 12.9472 | 9.3054 | 16.4566 | 26.1364 | 12.9266 | 9.2906 | 16.1805 | 26.1993 | 12.9108 | 9.2792 | 15.9949 | 26.2649 | 12.8789 | 9.2563 | 15.7353 | 26.333 | 12.8426 | 9.2302 | 15.4699 | 26.4801 | 12.7429 | 9.1586 | 14.7783 | 26.6085 | 12.6548 | 9.0953 | 14.1731 | 26.6893 | 14.592 | 10.4876 | 13.7997 | 26.7197 | 16.5159 | 11.8703 | 13.6683 | 25.97 | 12.9881 | 9.3348 | 17.1112 | 26.0082 | 12.9617 | 9.3158 | 16.9143 | 26.006 | 12.963 | 9.3168 | 16.942 | 26.031 | 12.9904 | 9.3364 | 16.7372 | 26.074 | 13.0355 | 9.3688 | 16.7094 | 26.1336 | 13.0685 | 9.3926 | 16.4332 | 26.2006 | 13.0149 | 9.3541 | 16.1369 | 26.2741 | 13.0235 | 9.3602 | 15.909 | 26.3518 | 12.9053 | 9.2753 | 15.653 | 26.438 | 12.7508 | 9.1642 | 15.3165 | 26.7834 | 12.578 | 9.04 | 14.2228 | 27.0268 | 12.6685 | 9.1051 | 13.7615 | 27.1682 | 15.9008 | 11.4282 | 13.7646 | 27.2314 | 15.6827 | 11.2715 | 14.0928 | 25.9657 | 12.9681 | 9.3204 | 17.1097 | 26.0021 | 12.9112 | 9.2795 | 16.8989 | 26.0052 | 12.852 | 9.237 | 16.9234 | 26.0433 | 12.7305 | 9.1496 | 16.7146 | 26.1073 | 12.6622 | 9.1006 | 16.7097 | 26.1998 | 12.5051 | 8.9876 | 16.4203 | 26.3156 | 12.2675 | 8.8169 | 16.0907 | 26.4487 | 11.9269 | 8.5721 | 15.8614 | 26.5925 | 11.9898 | 8.6173 | 15.5935 | 26.7527 | 11.9614 | 8.5969 | 15.329 | 27.3621 | 11.589 | 8.3292 | 13.7826 | 27.8067 | 11.0857 | 7.9675 | 10.2998 | 28.0043 | 13.7613 | 9.8905 | 7.6553 | 28.0719 | 13.2563 | 9.5276 | 5.9457 | 25.9586 | 12.9739 | 9.3246 | 17.1351 | 25.9947 | 12.9221 | 9.2873 | 16.9225 | 25.9987 | 12.8641 | 9.2457 | 16.9517 | 26.0337 | 12.7493 | 9.1632 | 16.7645 | 26.0977 | 12.6977 | 9.1261 | 16.7505 | 26.1849 | 12.5228 | 9.0004 | 16.4857 | 26.2938 | 12.2596 | 8.8112 | 16.2065 | 26.4156 | 12.081 | 8.6828 | 16.0483 | 26.5581 | 12.2202 | 8.7829 | 15.7237 | 26.7731 | 12.1986 | 8.7674 | 14.8696 | 27.3485 | 15.107 | 10.8577 | 11.0224 | 27.6378 | 14.2393 | 10.2341 | 7.9217 | 27.681 | 13.7194 | 9.8604 | 6.2058 | 27.5434 | 13.6687 | 9.8239 | 6.9326
HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 31.5893 | 8.9912 | 6.559 | 14.2771 | 31.642 | 8.7157 | 6.358 | 13.9872 | 31.6525 | 8.524 | 6.2182 | 13.9612 | 31.695 | 8.3074 | 6.0601 | 13.7207 | 31.7542 | 8.1192 | 5.9229 | 13.6284 | 31.8286 | 7.6961 | 5.6142 | 13.2831 | 31.9108 | 7.773 | 5.6703 | 12.9729 | 31.9993 | 7.747 | 5.6514 | 12.6941 | 32.0949 | 7.6528 | 5.5826 | 12.306 | 32.2034 | 7.5174 | 5.4838 | 11.8798 | 32.6876 | 6.9674 | 5.0826 | 10.3624 | 33.1652 | 6.528 | 4.7621 | 9.3998 | 33.5099 | 6.4881 | 4.733 | 9.0466 | 33.8032 | 6.3255 | 4.6144 | 9.0324 | 31.55 | 9.0384 | 6.5934 | 14.3504 | 31.5771 | 8.7954 | 6.4161 | 14.0929 | 31.6297 | 8.4708 | 6.1793 | 13.9872 | 31.7012 | 8.5501 | 6.2371 | 13.7264 | 31.7786 | 8.4565 | 6.1689 | 13.6164 | 31.8667 | 8.2902 | 6.0476 | 13.2673 | 31.9475 | 8.2048 | 5.9853 | 12.9533 | 32.0319 | 8.1291 | 5.9301 | 12.6964 | 32.1219 | 8.0253 | 5.8543 | 12.296 | 32.2156 | 7.9329 | 5.7869 | 11.9317 | 32.4723 | 7.6587 | 5.5869 | 10.937 | 32.7319 | 7.3886 | 5.3899 | 10.0376 | 32.9628 | 7.4187 | 5.4119 | 9.4414 | 33.144 | 7.5061 | 5.4756 | 9.0273 | 31.5894 | 9.0352 | 6.591 | 14.2534 | 31.6422 | 8.764 | 6.3932 | 13.9839 | 31.653 | 8.5607 | 6.2449 | 13.959 | 31.6958 | 8.5461 | 6.2342 | 13.7852 | 31.7552 | 8.409 | 6.1343 | 13.6322 | 31.8296 | 8.2161 | 5.9936 | 13.3571 | 31.9118 | 8.1105 | 5.9165 | 13.078 | 32.0004 | 8.0177 | 5.8488 | 12.8129 | 32.0952 | 7.8996 | 5.7626 | 12.4465 | 32.1995 | 7.776 | 5.6725 | 12.0593 | 32.6383 | 7.308 | 5.3311 | 10.6635 | 33.0073 | 6.9068 | 5.0384 | 9.8436 | 33.2968 | 7.0766 | 5.1623 | 9.5463 | 33.4972 | 6.6452 | 4.8476 | 9.5819 | 31.5836 | 8.9897 | 6.5579 | 14.2861 | 31.6331 | 8.691 | 6.34 | 13.9967 | 31.6473 | 8.5045 | 6.2039 | 13.9741 | 31.7017 | 8.2783 | 6.0389 | 13.7325 | 31.7845 | 8.0333 | 5.8602 | 13.6479 | 31.8951 | 7.7796 | 5.6751 | 13.2958 | 32.0323 | 7.763 | 5.663 | 12.9525 | 32.1898 | 7.6767 | 5.6 | 12.6439 | 32.3599 | 7.5275 | 5.4912 | 12.2736 | 32.5489 | 7.3734 | 5.3788 | 11.9244 | 33.3073 | 6.5058 | 4.7459 | 9.8332 | 31.9635 | 5.1848 | 3.7822 | 5.2577 | 27.7286 | 4.4978 | 3.2811 | 1.7566 | 23.247 | 3.7709 | 2.7508 | -0.67297 | 31.571 | 8.9967 | 6.563 | 14.3209 | 31.6155 | 8.8671 | 6.4684 | 14.058 | 31.6266 | 8.586 | 6.2634 | 14.0585 | 31.6717 | 8.6124 | 6.2827 | 13.8605 | 31.7432 | 8.4824 | 6.1878 | 13.8045 | 31.8455 | 8.2071 | 5.9869 | 13.5024 | 31.9775 | 8.0657 | 5.8838 | 13.212 | 32.1293 | 8.0814 | 5.8953 | 12.9594 | 32.3113 | 7.9848 | 5.8248 | 12.549 | 32.5203 | 7.7263 | 5.6362 | 11.4802 | 33.3452 | 6.4294 | 4.6901 | 6.5082 | 31.7699 | 5.1534 | 3.7593 | 2.3835 | 27.2459 | 4.4196 | 3.224 | 0.055559 | 26.3336 | 4.2716 | 3.116 | 0.6459
HEYSIDE | ROYTON | WHITEGATE | 393433 | 407129 | 23.2849 | 12.2604 | 8.9438 | 16.8478 | 23.3435 | 11.8004 | 8.6083 | 16.44 | 23.3643 | 11.3892 | 8.3082 | 16.3767 | 23.4062 | 10.9516 | 7.9891 | 16.1692 | 23.4651 | 10.521 | 7.675 | 16.0214 | 23.5418 | 10.0777 | 7.3515 | 15.7648 | 23.6299 | 9.9676 | 7.2713 | 15.6125 | 23.7273 | 9.8808 | 7.2079 | 15.3606 | 23.8324 | 9.8691 | 7.1994 | 15.032 | 23.941 | 9.8185 | 7.1624 | 14.7093 | 24.6812 | 9.3777 | 6.8409 | 13.3321 | 25.7469 | 9.5978 | 7.0015 | 12.1551 | 26.6087 | 10.674 | 7.7865 | 11.498 | 27.5363 | 10.5457 | 7.6929 | 10.8015 | 23.2403 | 12.2929 | 8.9675 | 17.0539 | 23.2636 | 12.0876 | 8.8177 | 16.8112 | 23.3097 | 11.8534 | 8.6469 | 16.6927 | 23.3654 | 11.6579 | 8.5043 | 16.4571 | 23.4289 | 11.4515 | 8.3537 | 16.3187 | 23.501 | 11.2066 | 8.175 | 16.0779 | 23.5827 | 11.1581 | 8.1397 | 15.9315 | 23.6714 | 11.1031 | 8.0995 | 15.6887 | 23.7536 | 11.0291 | 8.0456 | 15.3717 | 23.8385 | 10.9702 | 8.0026 | 15.099 | 24.3194 | 10.7751 | 7.8603 | 14.2057 | 24.8952 | 10.7502 | 7.8421 | 13.2977 | 25.5183 | 11.329 | 8.2644 | 12.5625 | 26.0761 | 11.7294 | 8.5564 | 11.9907 | 23.2858 | 12.2925 | 8.9672 | 16.8419 | 23.3453 | 11.8814 | 8.6673 | 16.4571 | 23.3673 | 11.4483 | 8.3513 | 16.3981 | 23.4108 | 10.9958 | 8.0213 | 16.2028 | 23.4712 | 10.5662 | 7.7079 | 16.0635 | 23.549 | 10.1048 | 7.3713 | 15.8161 | 23.6378 | 10.0428 | 7.3261 | 15.6712 | 23.7358 | 9.9759 | 7.2773 | 15.4235 | 23.8403 | 9.8962 | 7.2191 | 15.1078 | 23.9458 | 9.8161 | 7.1607 | 14.8113 | 24.5598 | 9.5766 | 6.986 | 13.6079 | 25.213 | 9.7012 | 7.0769 | 12.7715 | 25.8926 | 10.9101 | 7.9588 | 12.2764 | 26.4903 | 10.8581 | 7.9209 | 11.9946 | 23.2821 | 12.2609 | 8.9441 | 16.8582 | 23.3406 | 11.7954 | 8.6046 | 16.4518 | 23.368 | 11.373 | 8.2964 | 16.3907 | 23.4234 | 10.9303 | 7.9735 | 16.1837 | 23.5043 | 10.4818 | 7.6463 | 16.0365 | 23.6302 | 10.0249 | 7.313 | 15.7612 | 23.7838 | 9.888 | 7.2131 | 15.5638 | 23.9551 | 9.893 | 7.2168 | 15.2569 | 24.1507 | 9.8415 | 7.1792 | 14.9072 | 24.3731 | 9.7625 | 7.1216 | 14.5848 | 25.9713 | 9.1877 | 6.7023 | 12.3776 | 27.9711 | 8.7109 | 6.3544 | 8.0633 | 29.1795 | 9.048 | 6.6004 | 4.3885 | 29.747 | 8.5483 | 6.2359 | 1.9949 | 23.2811 | 12.2635 | 8.9461 | 16.8661 | 23.3478 | 11.969 | 8.7312 | 16.466 | 23.3877 | 11.6798 | 8.5203 | 16.4054 | 23.4536 | 11.2621 | 8.2155 | 16.2119 | 23.5473 | 11.1232 | 8.1142 | 16.0735 | 23.7053 | 10.8637 | 7.9249 | 15.8061 | 23.897 | 10.7886 | 7.8701 | 15.6073 | 24.1333 | 10.6866 | 7.7957 | 15.294 | 24.4193 | 10.5273 | 7.6795 | 14.8425 | 24.7961 | 10.3446 | 7.5462 | 13.8974 | 26.7995 | 10.5004 | 7.6599 | 9.3529 | 28.4343 | 9.4896 | 6.9225 | 5.1994 | 29.2083 | 8.8794 | 6.4774 | 2.7233 | 29.3557 | 8.7847 | 6.4083 | 2.9047
HEYWOOD | CASTLETON | ROCHDALE | 385429 | 410369 | 19.247 | 8.3075 | 6.0602 | 7.4937 | 19.3236 | 7.2926 | 5.3199 | 6.3036 | 19.3828 | 5.8455 | 4.2642 | 3.7049 | 19.4739 | 3.9023 | 2.8467 | -1.4136 | 11.2226 | 1.8204 | 1.328 | -6.5879 | -6.1803 | -1.0025 | -0.73131 | -17.1046 | -9.0179 | -1.4628 | -1.0671 | -19.7503 | -10.4742 | -1.699 | -1.2394 | -20.9009 | -11.0507 | -1.7925 | -1.3076 | -20.9969 | -12.4426 | -2.0183 | -1.4723 | -21.6626 | -13.7506 | -2.2305 | -1.6271 | -22.8746 | -6.1017 | -0.98975 | -0.72201 | -24.0336 | 10.3052 | 1.6716 | 1.2194 | -24.7757 | 14.7169 | 2.3872 | 1.7414 | -25.4654 | 19.2132 | 8.5668 | 6.2494 | 8.0554 | 19.2633 | 7.3732 | 5.3786 | 7.4791 | 19.3442 | 5.9226 | 4.3205 | 5.4408 | 19.4393 | 4.1256 | 3.0096 | 1.5345 | 14.2441 | 2.3105 | 1.6855 | -2.418 | -0.55871 | -0.090629 | -0.066112 | -10.4091 | -2.8761 | -0.46653 | -0.34033 | -12.5165 | -4.0679 | -0.65986 | -0.48136 | -13.4766 | -4.5366 | -0.73588 | -0.53682 | -13.653 | -5.4129 | -0.87803 | -0.64051 | -14.2646 | -5.6398 | -0.91483 | -0.66736 | -15.1617 | -0.26142 | -0.042405 | -0.030934 | -16.1172 | 10.9541 | 1.7769 | 1.2962 | -16.9246 | 14.0067 | 2.272 | 1.6574 | -17.6516 | 19.2473 | 8.5676 | 6.25 | 7.5021 | 19.3244 | 7.3846 | 5.387 | 6.3482 | 19.3845 | 5.9073 | 4.3093 | 3.7357 | 19.4768 | 4.0669 | 2.9667 | -1.3739 | 13.8519 | 2.2469 | 1.6391 | -6.5371 | -1.1238 | -0.18229 | -0.13298 | -17.0403 | -3.5258 | -0.57192 | -0.41721 | -19.672 | -4.7629 | -0.7726 | -0.5636 | -20.8112 | -5.2697 | -0.85479 | -0.62356 | -20.891 | -6.4 | -1.0381 | -0.75731 | -21.5187 | -7.2388 | -1.1742 | -0.85656 | -22.5729 | 1.6808 | 0.27264 | 0.19889 | -23.4615 | 19.7432 | 3.2025 | 2.3362 | -24.0806 | 22.725 | 3.9163 | 2.8569 | -24.5256 | 19.246 | 8.304 | 6.0576 | 7.499 | 19.3272 | 7.5376 | 5.4986 | 6.3169 | 19.4045 | 6.0584 | 4.4196 | 3.7265 | 19.5276 | 4.0289 | 2.939 | -1.387 | 12.2248 | 1.983 | 1.4466 | -6.5433 | -5.3652 | -0.87029 | -0.63487 | -17.0685 | -8.7782 | -1.4239 | -1.0387 | -19.6976 | -10.2383 | -1.6607 | -1.2115 | -20.8624 | -10.7932 | -1.7508 | -1.2772 | -20.974 | -11.725 | -1.9019 | -1.3874 | -21.5411 | -15.2301 | -2.4705 | -1.8022 | -23.6647 | -12.7398 | -2.0665 | -1.5075 | -28.7037 | -1.4887 | -0.24148 | -0.17616 | -32.8035 | -0.17104 | -0.027744 | -0.020239 | -35.7522 | 19.2699 | 8.305 | 6.0584 | 7.498 | 19.3739 | 8.4455 | 6.1609 | 6.3265 | 19.4573 | 8.1067 | 5.9138 | 3.7753 | 19.579 | 7.2715 | 5.3045 | -1.2908 | 19.6859 | 6.2704 | 4.5742 | -6.4066 | 19.8279 | 4.4246 | 3.2277 | -16.944 | 20.0242 | 3.852 | 2.8099 | -19.4937 | 20.2587 | 3.6401 | 2.6554 | -20.6162 | 20.5507 | 3.488 | 2.5444 | -20.9354 | 19.5329 | 3.1684 | 2.3113 | -22.2101 | 10.2482 | 1.6624 | 1.2127 | -27.3216 | 2.3401 | 0.37958 | 0.2769 | -32.0261 | 1.7364 | 0.28166 | 0.20547 | -34.828 | 0.59026 | 0.095746 | 0.069845 | -34.7399
HIGHER MILL | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 31.4315 | 13.5501 | 9.8846 | 14.1354 | 31.5113 | 13.4725 | 9.828 | 13.8702 | 31.5518 | 13.3714 | 9.7543 | 13.605 | 31.6327 | 13.309 | 9.7087 | 13.312 | 31.7423 | 13.1574 | 9.5981 | 12.8989 | 31.8815 | 13.0401 | 9.5126 | 12.4393 | 32.0315 | 12.8697 | 9.3883 | 11.8779 | 32.1864 | 12.7273 | 9.2844 | 11.3688 | 32.3559 | 12.5608 | 9.163 | 10.8271 | 32.5474 | 12.3615 | 9.0175 | 10.1783 | 33.4684 | 11.4717 | 8.3684 | 7.861 | 34.308 | 10.8041 | 7.8814 | 6.5922 | 34.7303 | 10.7005 | 7.8059 | 6.1392 | 34.982 | 10.6423 | 7.7634 | 6.1909 | 31.3829 | 13.5315 | 9.871 | 14.2225 | 31.4238 | 13.4686 | 9.8251 | 14.0439 | 31.4995 | 13.3943 | 9.771 | 13.7183 | 31.5988 | 13.2858 | 9.6918 | 13.4423 | 31.7128 | 13.2121 | 9.6381 | 13.076 | 31.8433 | 13.112 | 9.565 | 12.6635 | 31.9911 | 12.9982 | 9.482 | 12.1577 | 32.1529 | 12.8966 | 9.4079 | 11.7375 | 32.3288 | 12.774 | 9.3184 | 11.2573 | 32.5161 | 12.6349 | 9.217 | 10.7559 | 33.0877 | 12.2225 | 8.9161 | 9.1071 | 33.5181 | 11.8002 | 8.6081 | 7.8632 | 33.8108 | 11.6364 | 8.4886 | 7.1262 | 34.0024 | 11.474 | 8.3701 | 6.6915 | 31.4354 | 13.5263 | 9.8673 | 14.1584 | 31.5165 | 13.4657 | 9.8231 | 13.91 | 31.5579 | 13.35 | 9.7387 | 13.6444 | 31.6394 | 13.246 | 9.6628 | 13.3634 | 31.7486 | 13.105 | 9.5599 | 12.9662 | 31.885 | 12.9492 | 9.4463 | 12.5025 | 32.0309 | 12.7947 | 9.3336 | 11.9541 | 32.1812 | 12.6765 | 9.2473 | 11.4613 | 32.3436 | 12.5258 | 9.1374 | 10.946 | 32.5213 | 12.3709 | 9.0244 | 10.3589 | 33.3631 | 11.7071 | 8.5402 | 8.257 | 34.0673 | 11.0084 | 8.0305 | 7.2031 | 34.4102 | 11.0127 | 8.0336 | 6.8765 | 34.5922 | 10.6522 | 7.7707 | 7.0285 | 31.4313 | 13.5503 | 9.8847 | 14.1448 | 31.5117 | 13.4687 | 9.8252 | 13.8951 | 31.5637 | 13.3948 | 9.7714 | 13.6572 | 31.668 | 13.286 | 9.6919 | 13.395 | 31.8142 | 13.1616 | 9.6012 | 13.0332 | 32.0033 | 12.9978 | 9.4817 | 12.62 | 32.2236 | 12.8338 | 9.3621 | 12.09 | 32.4771 | 12.6539 | 9.2308 | 11.6447 | 32.756 | 12.468 | 9.0952 | 11.2068 | 33.0655 | 12.2753 | 8.9547 | 10.7518 | 34.2292 | 11.0814 | 8.0837 | 7.8225 | 35.2807 | 9.6499 | 7.0395 | 2.2002 | 35.9346 | 8.7277 | 6.3667 | -2.1209 | 36.2633 | 7.982 | 5.8228 | -5.0342 | 31.4312 | 13.5497 | 9.8843 | 14.1331 | 31.526 | 13.4818 | 9.8348 | 13.8144 | 31.5872 | 13.3975 | 9.7733 | 13.5707 | 31.6929 | 13.3117 | 9.7107 | 13.334 | 31.835 | 13.163 | 9.6022 | 12.9771 | 32.0155 | 12.9732 | 9.4638 | 12.5908 | 32.2445 | 12.7787 | 9.3219 | 12.1021 | 32.5068 | 12.5641 | 9.1653 | 11.6912 | 32.8205 | 12.3427 | 9.0038 | 11.1672 | 33.259 | 11.9917 | 8.7478 | 9.8269 | 34.3983 | 10.4007 | 7.5872 | 3.555 | 35.2468 | 8.9926 | 6.56 | -1.4511 | 35.635 | 8.5378 | 6.2282 | -4.3599 | 35.4439 | 8.3753 | 6.1096 | -3.6777
HIGHER WALTON | LEYLAND | PENWORTHAM WEST / STANAH | 358020 | 427270 | 33.9709 | 7.2103 | 5.1822 | 9.9467 | 34.1346 | 6.7111 | 4.8234 | 9.4997 | 34.1876 | 6.0294 | 4.3335 | 9.1684 | 34.2947 | 5.8762 | 4.2233 | 8.65 | 34.1673 | 5.6254 | 4.0431 | 8.45 | 31.6142 | 5.205 | 3.741 | 7.8772 | 30.5176 | 5.0245 | 3.6112 | 7.3358 | 29.0244 | 4.7787 | 3.4345 | 6.6893 | 26.8247 | 4.4165 | 3.1742 | 6.0453 | 26.5613 | 4.3731 | 3.143 | 5.2507 | 19.3293 | 3.1824 | 2.2873 | 0.52096 | 16.9389 | 2.7889 | 2.0044 | -1.6225 | 27.8522 | 4.5857 | 3.2958 | -2.6306 | 35.1719 | 5.7908 | 4.1619 | -3.3039 | 33.8359 | 7.3267 | 5.2659 | 10.2311 | 33.8874 | 7.1416 | 5.1328 | 10.021 | 33.9873 | 6.9303 | 4.9809 | 9.6019 | 34.0969 | 6.7311 | 4.8378 | 9.1156 | 34.223 | 6.5702 | 4.7221 | 8.9702 | 34.3626 | 6.3251 | 4.546 | 8.4858 | 34.5179 | 6.2593 | 4.4987 | 7.9872 | 34.6806 | 6.1766 | 4.4392 | 7.3607 | 34.852 | 6.0617 | 4.3566 | 6.7117 | 35.0272 | 5.9305 | 4.2624 | 6.1003 | 33.5373 | 5.5217 | 3.9685 | 4.3351 | 30.72 | 5.0578 | 3.6352 | 2.7829 | 37.9441 | 6.2472 | 4.49 | 1.5904 | 38.869 | 7.0945 | 5.0989 | 0.72346 | 33.9722 | 7.3405 | 5.2758 | 9.9515 | 34.1371 | 7.156 | 5.1432 | 9.515 | 34.1916 | 6.8391 | 4.9154 | 9.1969 | 34.3007 | 6.3984 | 4.5986 | 8.6975 | 34.4418 | 6.0511 | 4.349 | 8.5143 | 33.9515 | 5.5899 | 4.0175 | 7.9623 | 32.3917 | 5.333 | 3.833 | 7.3783 | 31.4557 | 5.1789 | 3.7222 | 6.7664 | 30.881 | 5.0843 | 3.6542 | 6.1285 | 30.1137 | 4.958 | 3.5634 | 5.4293 | 26.4181 | 4.3495 | 3.1261 | 1.0352 | 23.848 | 3.9264 | 2.822 | -0.57442 | 34.7345 | 5.7188 | 4.1102 | -1.3871 | 41.3891 | 7.1245 | 5.1205 | -1.6246 | 33.9624 | 7.2064 | 5.1794 | 9.9581 | 34.1291 | 6.6747 | 4.7972 | 9.5102 | 34.1979 | 6.3311 | 4.5503 | 9.1848 | 34.3276 | 5.9609 | 4.2842 | 8.6827 | 33.8112 | 5.5668 | 4.0009 | 8.494 | 30.1953 | 4.9714 | 3.5731 | 7.9138 | 29.2749 | 4.8199 | 3.4641 | 7.3441 | 28.3828 | 4.673 | 3.3586 | 6.6786 | 27.3649 | 4.5054 | 3.2381 | 6.1518 | 26.0495 | 4.2888 | 3.0825 | 5.5353 | 16.4353 | 2.706 | 1.9448 | -0.09613 | 7.9849 | 1.3147 | 0.94487 | -8.6861 | 13.5025 | 2.2231 | 1.5978 | -12.8082 | 18.0847 | 2.9775 | 2.14 | -15.3896 | 33.9696 | 7.1998 | 5.1747 | 9.9226 | 34.1577 | 6.5299 | 4.6931 | 9.4172 | 34.2459 | 6.3002 | 4.5281 | 9.0857 | 34.3981 | 6.0548 | 4.3517 | 8.5955 | 34.2051 | 5.6316 | 4.0475 | 8.4184 | 30.8311 | 5.0761 | 3.6483 | 7.8646 | 30.2833 | 4.9859 | 3.5835 | 7.2278 | 29.2837 | 4.8213 | 3.4652 | 6.5673 | 27.8585 | 4.5867 | 3.2965 | 5.8286 | 23.8868 | 3.9328 | 2.8266 | 2.6048 | 14.2502 | 2.3462 | 1.6862 | -6.5568 | 9.3795 | 1.5443 | 1.1099 | -11.5475 | 21.6715 | 3.5681 | 2.5644 | -14.4241 | 20.7524 | 3.4167 | 2.4557 | -13.8362
HILL TOP T11 & T12 | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 21.8608 | 3.5992 | 2.5868 | 9.3618 | 20.7673 | 3.4192 | 2.4574 | 8.8361 | 19.6728 | 3.239 | 2.3279 | 8.3857 | 18.3337 | 3.0185 | 2.1695 | 7.8264 | 16.6486 | 2.7411 | 1.9701 | 7.1666 | 14.6382 | 2.4101 | 1.7322 | 6.3868 | 12.6722 | 2.0864 | 1.4995 | 5.5451 | 11.4838 | 1.8907 | 1.3589 | 4.7342 | 10.6825 | 1.7588 | 1.2641 | 3.8728 | 9.5952 | 1.5798 | 1.1354 | 2.9156 | 3.5137 | 0.5785 | 0.41578 | -0.7828 | 2.6844 | 0.44197 | 0.31765 | -3.0089 | 2.6844 | 0.44197 | 0.31765 | -3.8657 | 2.6844 | 0.44197 | 0.31765 | -4.1671 | 21.9079 | 3.607 | 2.5924 | 9.6101 | 21.5909 | 3.5548 | 2.5549 | 9.3038 | 20.7327 | 3.4135 | 2.4533 | 8.7459 | 19.73 | 3.2484 | 2.3347 | 8.1924 | 18.8893 | 3.11 | 2.2352 | 7.5906 | 17.8784 | 2.9435 | 2.1156 | 6.8848 | 16.7108 | 2.7513 | 1.9774 | 6.1116 | 15.5308 | 2.557 | 1.8378 | 5.3631 | 14.2979 | 2.354 | 1.6919 | 4.5843 | 12.9963 | 2.1397 | 1.5379 | 3.773 | 8.624 | 1.4199 | 1.0205 | 0.98861 | 6.6932 | 1.102 | 0.79201 | -1.0669 | 4.6536 | 0.76618 | 0.55067 | -2.3183 | 2.1783 | 0.35864 | 0.25776 | -3.1465 | 21.8714 | 3.601 | 2.5881 | 9.378 | 20.9762 | 3.4536 | 2.4822 | 8.885 | 19.4786 | 3.207 | 2.3049 | 8.4669 | 17.7291 | 2.919 | 2.0979 | 7.9296 | 17.0122 | 2.8009 | 2.0131 | 7.3052 | 16.3816 | 2.6971 | 1.9385 | 6.5636 | 15.4235 | 2.5394 | 1.8251 | 5.7328 | 14.4227 | 2.3746 | 1.7067 | 4.9233 | 13.3199 | 2.193 | 1.5762 | 4.1062 | 12.2023 | 2.009 | 1.4439 | 3.2401 | 7.2825 | 1.199 | 0.86175 | -0.078627 | 1.9826 | 0.32642 | 0.23461 | -1.8826 | 0.75987 | 0.12511 | 0.089917 | -2.5375 | 2.6844 | 0.44197 | 0.31765 | -2.6313 | 21.8687 | 3.6005 | 2.5878 | 9.3884 | 20.6986 | 3.4079 | 2.4493 | 8.8981 | 19.5728 | 3.2225 | 2.3161 | 8.4895 | 18.0271 | 2.968 | 2.1332 | 7.9604 | 16.3214 | 2.6872 | 1.9313 | 7.3961 | 14.1218 | 2.3251 | 1.6711 | 6.7203 | 12.8053 | 2.1083 | 1.5153 | 5.9737 | 12.1104 | 1.9939 | 1.433 | 5.2669 | 11.1926 | 1.8428 | 1.3244 | 4.5933 | 10.0007 | 1.6465 | 1.1834 | 3.8876 | 0.68077 | 0.11208 | 0.080556 | -0.56872 | 2.6844 | 0.44197 | 0.31765 | -7.6749 | 2.6844 | 0.44197 | 0.31765 | -12.9527 | 2.6844 | 0.44197 | 0.31765 | -16.5797 | 21.799 | 3.589 | 2.5795 | 9.32 | 20.1749 | 3.3216 | 2.3873 | 8.7446 | 18.3108 | 3.0147 | 2.1667 | 8.3301 | 16.1207 | 2.6541 | 1.9076 | 7.8346 | 16.225 | 2.6713 | 1.9199 | 7.3189 | 15.2945 | 2.5181 | 1.8098 | 6.7188 | 13.9681 | 2.2997 | 1.6529 | 5.9962 | 12.731 | 2.0961 | 1.5065 | 5.3367 | 11.2137 | 1.8463 | 1.3269 | 4.5463 | 8.5097 | 1.4011 | 1.007 | 2.8577 | 2.6844 | 0.44197 | 0.31765 | -5.4211 | 2.6844 | 0.44197 | 0.31765 | -11.946 | 2.6844 | 0.44197 | 0.31765 | -15.6025 | 2.6844 | 0.44197 | 0.31765 | -14.8022
HILL TOP T13 | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 6.1287 | 6.1287 | 6.1287 | 1.3135 | 6.1675 | 6.1675 | 6.1675 | 1.1825 | 6.1962 | 6.1962 | 6.1962 | 1.0159 | 6.2374 | 6.2374 | 6.2374 | 0.83729 | 6.2917 | 6.2917 | 6.2917 | 0.6636 | 6.3574 | 6.3574 | 6.3574 | 0.41059 | 6.4271 | 6.4271 | 6.4271 | 0.15429 | 6.498 | 6.498 | 6.498 | -0.086277 | 6.5741 | 6.5741 | 6.5741 | -0.343 | 6.6577 | 6.6577 | 6.6577 | -0.63818 | 7.0865 | 7.0865 | 7.0865 | -1.8184 | 7.5532 | 7.5532 | 7.5532 | -2.6292 | 7.9157 | 7.9157 | 7.9157 | -2.9855 | 8.2817 | 8.2817 | 8.2817 | -3.201 | 6.1163 | 6.1163 | 6.1163 | 1.3452 | 6.1449 | 6.1449 | 6.1449 | 1.2406 | 6.1872 | 6.1872 | 6.1872 | 1.0346 | 6.2338 | 6.2338 | 6.2338 | 0.85361 | 6.287 | 6.287 | 6.287 | 0.6908 | 6.3437 | 6.3437 | 6.3437 | 0.45222 | 6.4023 | 6.4023 | 6.4023 | 0.20817 | 6.4651 | 6.4651 | 6.4651 | -0.020037 | 6.5323 | 6.5323 | 6.5323 | -0.26775 | 6.6025 | 6.6025 | 6.6025 | -0.52258 | 6.8369 | 6.8369 | 6.8369 | -1.4483 | 7.0782 | 7.0782 | 7.0782 | -2.1909 | 7.3166 | 7.3166 | 7.3166 | -2.6653 | 7.5266 | 7.5266 | 7.5266 | -3.0535 | 6.1288 | 6.1288 | 6.1288 | 1.3168 | 6.1678 | 6.1678 | 6.1678 | 1.1924 | 6.1968 | 6.1968 | 6.1968 | 1.0326 | 6.2384 | 6.2384 | 6.2384 | 0.85986 | 6.2929 | 6.2929 | 6.2929 | 0.6944 | 6.3587 | 6.3587 | 6.3587 | 0.45083 | 6.4286 | 6.4286 | 6.4286 | 0.20379 | 6.4997 | 6.4997 | 6.4997 | -0.028009 | 6.5752 | 6.5752 | 6.5752 | -0.27185 | 6.6553 | 6.6553 | 6.6553 | -0.54011 | 7.0362 | 7.0362 | 7.0362 | -1.617 | 7.3767 | 7.3767 | 7.3767 | -2.3162 | 7.675 | 7.675 | 7.675 | -2.6126 | 7.9285 | 7.9285 | 7.9285 | -2.777 | 6.1277 | 6.1277 | 6.1277 | 1.3181 | 6.1686 | 6.1686 | 6.1686 | 1.1934 | 6.2066 | 6.2066 | 6.2066 | 1.0332 | 6.2641 | 6.2641 | 6.2641 | 0.85518 | 6.3399 | 6.3399 | 6.3399 | 0.70661 | 6.4272 | 6.4272 | 6.4272 | 0.4799 | 6.5335 | 6.5335 | 6.5335 | 0.24219 | 6.6571 | 6.6571 | 6.6571 | 0.02079 | 6.796 | 6.796 | 6.796 | -0.1886 | 6.9514 | 6.9514 | 6.9514 | -0.40577 | 7.7081 | 7.7081 | 7.7081 | -2.0656 | 8.5036 | 8.5036 | 8.5036 | -5.4328 | 8.9692 | 8.9692 | 8.9692 | -8.1668 | 9.2045 | 9.2045 | 9.2045 | -10.0947 | 6.125 | 6.125 | 6.125 | 1.3304 | 6.1715 | 6.1715 | 6.1715 | 1.202 | 6.213 | 6.213 | 6.213 | 1.0522 | 6.2689 | 6.2689 | 6.2689 | 0.89929 | 6.3418 | 6.3418 | 6.3418 | 0.77786 | 6.43 | 6.43 | 6.43 | 0.58657 | 6.5439 | 6.5439 | 6.5439 | 0.38206 | 6.676 | 6.676 | 6.676 | 0.19553 | 6.8313 | 6.8313 | 6.8313 | -0.09381 | 7.0256 | 7.0256 | 7.0256 | -0.83703 | 7.8661 | 7.8661 | 7.8661 | -4.478 | 8.5284 | 8.5284 | 8.5284 | -7.5633 | 8.8209 | 8.8209 | 8.8209 | -9.4344 | 8.8423 | 8.8423 | 8.8423 | -9.2769
HINDLEY GREEN | ATHERTON | KEARSLEY | 363389 | 403254 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -3.4586 | -1.0591 | -0.40198 | -0.32846 | -11.4649 | -4.7327 | -1.7963 | -1.4678 | -16.4046 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -1.4661 | 2.6844 | 0.44197 | 0.31765 | -10.3804 | -0.812 | -0.3082 | -0.25183 | -15.6316 | -1.3381 | -0.50789 | -0.41499 | -13.7337
HOLLINWOOD | CHADDERTON | WHITEGATE | 390287 | 402592 | 23.1183 | 6.8094 | 4.9674 | 18.1059 | 23.18 | 5.2915 | 3.8601 | 17.8452 | 23.195 | 3.8592 | 2.8153 | 17.7131 | 14.8266 | 2.405 | 1.7544 | 14.8266 | 6.2494 | 1.0137 | 0.73949 | 6.2494 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.4601 | 0.88568 | 0.64609 | 5.4601 | 24.6338 | 4.3627 | 3.1825 | 14.0827 | 24.8615 | 5.2039 | 3.7962 | 14.0646 | 23.0646 | 6.8613 | 5.0052 | 18.2537 | 23.0828 | 5.5225 | 4.0286 | 18.1207 | 23.123 | 4.2044 | 3.067 | 17.9514 | 17.9089 | 2.905 | 2.1192 | 17.751 | 10.0201 | 1.6254 | 1.1857 | 10.0201 | 2.0434 | 0.33145 | 0.24179 | 2.0434 | 1.6052 | 0.26037 | 0.18994 | 1.6052 | 1.1015 | 0.17868 | 0.13034 | 1.1015 | 0.55736 | 0.090409 | 0.065952 | 0.55736 | 0.017491 | 0.0028372 | 0.0020697 | 0.017491 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 7.5207 | 1.2199 | 0.88992 | 7.5207 | 21.6724 | 3.5155 | 2.5645 | 14.7946 | 24.3123 | 4.0146 | 2.9286 | 14.5893 | 23.1183 | 6.8591 | 5.0036 | 18.114 | 23.1802 | 5.4549 | 3.9793 | 17.8581 | 23.1953 | 4.0635 | 2.9643 | 17.731 | 16.4228 | 2.6639 | 1.9433 | 16.4228 | 8.0202 | 1.3009 | 0.94902 | 8.0202 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 9.9317 | 1.611 | 1.1752 | 9.9317 | 24.4649 | 5.0096 | 3.6544 | 14.423 | 24.6215 | 6.0028 | 4.379 | 14.4137 | 23.114 | 6.8072 | 4.9658 | 18.1112 | 23.1729 | 5.2967 | 3.8639 | 17.8551 | 23.1734 | 3.759 | 2.7421 | 17.7265 | 14.923 | 2.4207 | 1.7658 | 14.923 | 6.0459 | 0.9807 | 0.71541 | 6.0459 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 17.6246 | 2.8589 | 2.0855 | 9.6235 | 19.9346 | 3.2336 | 2.3589 | 7.9596 | 23.1142 | 6.8076 | 4.9661 | 18.1012 | 23.1749 | 6.5166 | 4.7538 | 17.8422 | 23.1902 | 6.0047 | 4.3804 | 17.7292 | 23.225 | 6.0758 | 4.4322 | 17.5661 | 23.2804 | 5.7778 | 4.2148 | 17.4827 | 23.3588 | 5.5501 | 4.0487 | 17.2928 | 23.4586 | 5.4197 | 3.9536 | 17.0999 | 23.5709 | 5.2925 | 3.8608 | 16.8751 | 23.6983 | 5.1361 | 3.7467 | 16.5941 | 23.8594 | 4.8376 | 3.529 | 15.8697 | 24.4979 | 4.9241 | 3.5921 | 12.6532 | 24.1543 | 3.9181 | 2.8582 | 9.9994 | 21.9609 | 3.5623 | 2.5986 | 8.4258 | 21.6348 | 3.5094 | 2.56 | 8.7393
HOLME RD | RIBBLE | PENWORTHAM EAST / ROCHDALE | 352311 | 429141 | 30.9201 | 8.0943 | 5.8176 | 11.3016 | 31.0385 | 7.9008 | 5.6785 | 10.5151 | 31.1435 | 7.7498 | 5.57 | 10.2182 | 31.2879 | 7.5113 | 5.3985 | 9.5737 | 31.4468 | 7.3391 | 5.2748 | 9.304 | 31.6159 | 7.1073 | 5.1082 | 8.5872 | 31.7997 | 6.9026 | 4.961 | 8.024 | 31.9762 | 6.7102 | 4.8228 | 7.5867 | 32.1529 | 6.4611 | 4.6437 | 6.8947 | 32.3523 | 6.1433 | 4.4153 | 6.0981 | 33.217 | 5.6303 | 4.0466 | 3.2107 | 33.9002 | 5.7805 | 4.1546 | 1.8203 | 34.3342 | 6.5579 | 4.7133 | 1.4127 | 34.6086 | 6.6222 | 4.7595 | 1.7865 | 30.8647 | 8.164 | 5.8676 | 11.5844 | 30.9335 | 7.9946 | 5.7459 | 11.0534 | 31.0485 | 7.8518 | 5.6432 | 10.7227 | 31.1723 | 7.6563 | 5.5027 | 10.1009 | 31.3115 | 7.5322 | 5.4135 | 9.8813 | 31.4679 | 7.4075 | 5.3239 | 9.2397 | 31.6291 | 7.2822 | 5.2339 | 8.7409 | 31.756 | 7.1701 | 5.1533 | 8.3575 | 31.8897 | 7.0199 | 5.0453 | 7.7348 | 32.0261 | 6.8536 | 4.9258 | 7.12 | 32.4469 | 6.351 | 4.5646 | 5.361 | 32.8161 | 6.3393 | 4.5562 | 3.8307 | 33.069 | 6.9012 | 4.96 | 2.8117 | 33.2293 | 6.947 | 4.993 | 2.2625 | 30.9211 | 8.1577 | 5.8631 | 11.3103 | 31.0399 | 7.9466 | 5.7114 | 10.5465 | 31.1452 | 7.7681 | 5.5831 | 10.2683 | 31.2897 | 7.5696 | 5.4404 | 9.6436 | 31.4475 | 7.4473 | 5.3525 | 9.3964 | 31.6153 | 7.2127 | 5.1839 | 8.7087 | 31.7977 | 7.0215 | 5.0465 | 8.1713 | 31.9735 | 6.8216 | 4.9028 | 7.7564 | 32.147 | 6.5719 | 4.7234 | 7.104 | 32.3355 | 6.4433 | 4.631 | 6.3488 | 33.1426 | 6.1612 | 4.4282 | 3.7789 | 33.7445 | 6.3765 | 4.5829 | 2.6257 | 34.1247 | 6.9734 | 5.0119 | 2.2845 | 34.3532 | 6.9384 | 4.9868 | 2.6713 | 30.9207 | 8.0942 | 5.8174 | 11.3217 | 31.0512 | 7.8981 | 5.6765 | 10.5636 | 31.1957 | 7.6929 | 5.529 | 10.3059 | 31.3756 | 7.459 | 5.3609 | 9.7057 | 31.5671 | 7.2855 | 5.2362 | 9.5198 | 31.8001 | 7.0547 | 5.0703 | 8.8889 | 32.0441 | 6.8387 | 4.9151 | 8.3609 | 32.3165 | 6.6013 | 4.7445 | 7.9704 | 32.6143 | 6.2853 | 4.5174 | 7.4158 | 32.9422 | 6.0453 | 4.3449 | 6.8788 | 31.9513 | 5.2605 | 3.7809 | 3.637 | 25.2113 | 4.1509 | 2.9833 | -2.7952 | 24.3218 | 4.0044 | 2.878 | -7.958 | 19.9939 | 3.2918 | 2.3659 | -11.2739 | 30.9449 | 8.0881 | 5.8131 | 11.2685 | 31.1238 | 7.9012 | 5.6788 | 10.4382 | 31.2551 | 7.7444 | 5.566 | 10.1914 | 31.3942 | 7.4826 | 5.3779 | 9.6239 | 31.5723 | 7.2893 | 5.2389 | 9.428 | 31.7925 | 7.0597 | 5.0739 | 8.8298 | 32.0668 | 6.8135 | 4.897 | 8.3808 | 32.3256 | 6.5902 | 4.7365 | 8.0869 | 32.6304 | 6.4362 | 4.6258 | 7.4007 | 33.0659 | 6.2787 | 4.5126 | 5.79 | 34.2478 | 6.6596 | 4.7864 | -1.4356 | 30.2735 | 4.9843 | 3.5823 | -7.2556 | 24.8712 | 4.0948 | 2.943 | -10.6839 | 24.1588 | 3.9776 | 2.8588 | -9.7088
HOLT ST | BURY | KEARSLEY | 378620 | 416362 | 23.9213 | 13.0918 | 9.4094 | 7.2941 | 23.9782 | 13.0965 | 9.4127 | 6.7999 | 24.0293 | 13.0898 | 9.4079 | 6.4782 | 24.1041 | 13.0594 | 9.3861 | 5.9615 | 24.1999 | 13.012 | 9.352 | 5.5513 | 24.3169 | 12.9064 | 9.2761 | 4.863 | 24.4511 | 12.7339 | 9.1521 | 4.2757 | 24.5998 | 12.5999 | 9.0558 | 3.67 | 24.7617 | 12.334 | 8.8647 | 3.0421 | 24.9413 | 11.8974 | 8.5509 | 2.2662 | 25.8309 | 11.931 | 8.575 | -0.21888 | 26.8213 | 11.7237 | 8.426 | -1.6572 | 27.5901 | 11.7674 | 8.4574 | -2.2577 | 28.3881 | 11.6263 | 8.3561 | -2.4845 | 23.9075 | 13.2346 | 9.512 | 7.513 | 23.9556 | 13.3513 | 9.5958 | 7.1923 | 24.0292 | 13.339 | 9.587 | 6.8493 | 24.1127 | 13.3352 | 9.5842 | 6.4247 | 24.2027 | 13.2716 | 9.5386 | 6.1132 | 24.3067 | 13.1729 | 9.4676 | 5.5412 | 24.4243 | 13.1098 | 9.4222 | 5.0645 | 24.5478 | 13.0344 | 9.3681 | 4.5687 | 24.6771 | 12.9359 | 9.2973 | 4.0424 | 24.8121 | 12.8565 | 9.2402 | 3.4472 | 25.3183 | 12.5507 | 9.0204 | 1.697 | 25.8198 | 12.5089 | 8.9904 | 0.43366 | 26.344 | 12.5212 | 8.9993 | -0.4544 | 26.8128 | 12.5165 | 8.9958 | -0.96553 | 23.9216 | 13.2488 | 9.5222 | 7.2954 | 23.979 | 13.4645 | 9.6772 | 6.8158 | 24.0309 | 13.5112 | 9.7107 | 6.4913 | 24.1068 | 13.4111 | 9.6388 | 5.983 | 24.2034 | 13.4386 | 9.6586 | 5.5836 | 24.3208 | 13.3236 | 9.576 | 4.9095 | 24.4555 | 13.2044 | 9.4903 | 4.3344 | 24.6049 | 13.0982 | 9.414 | 3.7395 | 24.7654 | 12.9844 | 9.3321 | 3.1331 | 24.9367 | 12.9025 | 9.2733 | 2.4211 | 25.7099 | 12.3568 | 8.8811 | 0.18809 | 26.3909 | 12.2898 | 8.8329 | -0.91174 | 27.0048 | 12.5534 | 9.0224 | -1.3376 | 27.5255 | 12.3674 | 8.8887 | -1.3605 | 23.9202 | 13.0998 | 9.4151 | 7.3174 | 23.9811 | 13.1232 | 9.4319 | 6.8436 | 24.0462 | 13.1611 | 9.4591 | 6.5712 | 24.1449 | 13.0923 | 9.4097 | 6.1172 | 24.2745 | 13.0641 | 9.3894 | 5.7964 | 24.4441 | 12.9361 | 9.2975 | 5.2101 | 24.6544 | 12.8067 | 9.2044 | 4.7089 | 24.9009 | 12.5437 | 9.0154 | 4.184 | 25.1796 | 12.1491 | 8.7318 | 3.7076 | 25.4934 | 12.099 | 8.6958 | 3.1623 | 27.1059 | 11.7047 | 8.4124 | -0.21022 | 28.8718 | 10.3926 | 7.4694 | -6.2021 | 30.0345 | 9.6741 | 6.953 | -10.7151 | 30.6418 | 9.0245 | 6.4861 | -13.3848 | 23.9232 | 13.0947 | 9.4114 | 7.2416 | 24.0002 | 13.1496 | 9.4509 | 6.6773 | 24.073 | 13.161 | 9.4591 | 6.3572 | 24.1707 | 13.0994 | 9.4148 | 5.9358 | 24.298 | 12.9392 | 9.2997 | 5.6631 | 24.4729 | 12.4116 | 8.9204 | 5.1248 | 24.7057 | 12.5492 | 9.0194 | 4.6589 | 24.9785 | 12.6789 | 9.1125 | 4.1982 | 25.299 | 12.6761 | 9.1105 | 3.5986 | 25.7117 | 12.4696 | 8.9622 | 2.1464 | 27.5808 | 10.9973 | 7.904 | -4.5578 | 29.0918 | 10.2094 | 7.3377 | -9.8144 | 29.7867 | 9.4718 | 6.8076 | -12.674 | 29.851 | 9.4582 | 6.7978 | -11.5992
HURST | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 23.8411 | 6.8117 | 4.9691 | 9.632 | 23.8989 | 6.8537 | 4.9997 | 9.3969 | 23.9279 | 6.8544 | 5.0002 | 9.1183 | 23.9811 | 6.7764 | 4.9433 | 8.7642 | 24.0562 | 6.6439 | 4.8466 | 8.5381 | 24.149 | 6.4347 | 4.694 | 8.1423 | 24.2532 | 6.2649 | 4.5702 | 7.6634 | 24.3666 | 6.0881 | 4.4411 | 7.186 | 24.4892 | 5.8778 | 4.2878 | 6.6784 | 24.6265 | 5.6154 | 4.0963 | 6.104 | 25.1963 | 5.2502 | 3.83 | 4.2189 | 25.6311 | 5.0718 | 3.6998 | 3.4124 | 25.9007 | 5.4319 | 3.9625 | 3.3656 | 26.0936 | 5.7061 | 4.1625 | 3.6136 | 23.7962 | 6.8819 | 5.0202 | 9.6939 | 23.8182 | 6.8097 | 4.9676 | 9.5103 | 23.8684 | 6.6065 | 4.8194 | 9.2022 | 23.9287 | 6.2632 | 4.5689 | 8.8916 | 23.9972 | 6.1948 | 4.519 | 8.7687 | 24.0705 | 6.1402 | 4.4792 | 8.4271 | 24.1511 | 6.0581 | 4.4193 | 8.074 | 24.2362 | 5.9711 | 4.3558 | 7.7256 | 24.3258 | 5.8728 | 4.2841 | 7.3405 | 24.4176 | 5.7657 | 4.206 | 6.9378 | 24.702 | 5.4457 | 3.9726 | 5.5584 | 24.9362 | 5.3584 | 3.9089 | 4.6791 | 25.1058 | 5.5469 | 4.0464 | 4.2172 | 25.223 | 5.7695 | 4.2088 | 3.9926 | 23.8411 | 6.8807 | 5.0194 | 9.6414 | 23.8989 | 6.7984 | 4.9594 | 9.4143 | 23.9281 | 6.5441 | 4.7738 | 9.1442 | 23.9813 | 6.1155 | 4.4611 | 8.7985 | 24.0562 | 6.2149 | 4.5337 | 8.6055 | 24.1485 | 5.9353 | 4.3297 | 8.2119 | 24.2523 | 5.8518 | 4.2688 | 7.7411 | 24.3654 | 5.8646 | 4.2781 | 7.2746 | 24.4864 | 5.8214 | 4.2466 | 6.7866 | 24.6168 | 5.7618 | 4.2031 | 6.2634 | 25.1474 | 5.394 | 3.9348 | 4.5704 | 25.5296 | 5.0785 | 3.7047 | 3.883 | 25.7722 | 5.4131 | 3.9488 | 3.788 | 25.935 | 5.6074 | 4.0905 | 3.9987 | 23.8369 | 6.8054 | 4.9644 | 9.6367 | 23.8952 | 6.859 | 5.0035 | 9.4051 | 23.9351 | 6.8527 | 4.999 | 9.135 | 24.0077 | 6.7557 | 4.9282 | 8.7929 | 24.1125 | 6.5866 | 4.8048 | 8.6082 | 24.2497 | 6.352 | 4.6337 | 8.2481 | 24.4165 | 6.1491 | 4.4857 | 7.8102 | 24.6081 | 5.9154 | 4.3152 | 7.4006 | 24.8152 | 5.6225 | 4.1015 | 7.0295 | 25.0467 | 5.6076 | 4.0907 | 6.6392 | 25.9369 | 4.8683 | 3.5514 | 4.2908 | 23.2603 | 3.773 | 2.7524 | -0.43729 | 20.703 | 3.3582 | 2.4498 | -4.1191 | 18.7489 | 3.0413 | 2.2186 | -6.5706 | 23.8323 | 6.8099 | 4.9677 | 9.6521 | 23.8908 | 6.8731 | 5.0138 | 9.4006 | 23.9318 | 6.919 | 5.0473 | 9.1274 | 24.0003 | 6.9134 | 5.0433 | 8.8201 | 24.1007 | 6.8626 | 5.0062 | 8.6428 | 24.2279 | 6.7238 | 4.905 | 8.348 | 24.3865 | 6.569 | 4.792 | 7.9594 | 24.5637 | 6.4045 | 4.672 | 7.6243 | 24.7775 | 6.1885 | 4.5144 | 7.1799 | 25.1332 | 5.7831 | 4.2187 | 5.9848 | 25.9298 | 4.8393 | 3.5302 | 0.5059 | 24.0628 | 3.9032 | 2.8473 | -3.7416 | 24.3431 | 3.9487 | 2.8805 | -6.1199 | 23.5467 | 3.8195 | 2.7863 | -5.2456
HUTTON END & SKELTON C | PENRITH & SHAP | HARKER / HUTTON | 345810 | 538827 | 26.2638 | 26.2638 | 19.2679 | 15.5124 | 26.3411 | 26.3411 | 19.0989 | 15.3183 | 26.4018 | 26.3579 | 18.9439 | 15.316 | 26.4883 | 26.1119 | 18.7671 | 15.187 | 26.5779 | 25.8622 | 18.5877 | 15.0452 | 26.6603 | 25.5755 | 18.3816 | 14.7988 | 26.7564 | 25.4711 | 18.3066 | 14.5173 | 26.8241 | 25.3857 | 18.2452 | 14.3504 | 26.9018 | 25.2843 | 18.1723 | 14.0898 | 27.0069 | 25.1507 | 18.0763 | 13.6538 | 27.4578 | 24.6771 | 17.7359 | 12.0813 | 27.8517 | 24.2556 | 17.433 | 11.1961 | 28.1232 | 24.1177 | 17.3339 | 10.7302 | 28.2638 | 23.9926 | 17.244 | 10.9413 | 26.2191 | 26.2191 | 19.2951 | 15.7079 | 26.2609 | 26.2609 | 19.2816 | 15.6727 | 26.3368 | 26.3368 | 19.259 | 15.607 | 26.4199 | 26.4199 | 19.2139 | 15.3866 | 26.479 | 26.479 | 19.1803 | 15.2549 | 26.5448 | 26.5448 | 19.1306 | 15.0202 | 26.6205 | 26.5498 | 19.0818 | 14.7473 | 26.7006 | 26.5009 | 19.0467 | 14.5817 | 26.7839 | 26.4442 | 19.006 | 14.3553 | 26.8706 | 26.3819 | 18.9612 | 14.0853 | 27.2297 | 26.1736 | 18.8115 | 13.2418 | 27.5303 | 25.8993 | 18.6143 | 12.1162 | 27.793 | 25.649 | 18.4344 | 11.1484 | 27.9702 | 25.4552 | 18.2951 | 10.5183 | 26.2647 | 26.2647 | 19.2934 | 15.5143 | 26.3424 | 26.3424 | 19.1446 | 15.3218 | 26.4035 | 26.4035 | 18.9816 | 15.321 | 26.4902 | 26.1476 | 18.7928 | 15.2546 | 26.5796 | 25.9004 | 18.6151 | 15.0904 | 26.6613 | 25.6238 | 18.4163 | 14.8901 | 26.7569 | 25.5289 | 18.3481 | 14.6162 | 26.8243 | 25.4445 | 18.2875 | 14.4548 | 26.9008 | 25.2697 | 18.1619 | 14.2074 | 27.002 | 25.2798 | 18.1691 | 13.8076 | 27.4192 | 24.9693 | 17.9459 | 12.3737 | 27.7335 | 24.6065 | 17.6852 | 11.615 | 27.9588 | 24.2344 | 17.4177 | 11.2225 | 28.0344 | 23.9224 | 17.1935 | 11.462 | 26.26 | 26.26 | 19.2688 | 15.5281 | 26.3338 | 26.3338 | 19.0974 | 15.3402 | 26.3922 | 26.3446 | 18.9344 | 15.3432 | 26.4821 | 26.0794 | 18.7438 | 15.1756 | 26.5978 | 25.8094 | 18.5497 | 14.9932 | 26.7405 | 25.4964 | 18.3248 | 14.6886 | 26.8601 | 25.359 | 18.226 | 14.3203 | 26.9827 | 25.2419 | 18.1418 | 14.0818 | 27.1153 | 25.1176 | 18.0525 | 13.8069 | 27.2608 | 24.983 | 17.9558 | 13.4973 | 27.8619 | 24.4428 | 17.5675 | 12.1936 | 28.318 | 24.0027 | 17.2512 | 11.4101 | 28.4993 | 23.7841 | 17.0941 | 11.344 | 28.5301 | 23.5457 | 16.9228 | 11.2575 | 26.2724 | 26.2724 | 19.2687 | 15.5224 | 26.3707 | 26.3707 | 19.104 | 15.3197 | 26.4422 | 26.353 | 18.9404 | 15.3155 | 26.5337 | 26.0849 | 18.7478 | 15.1359 | 26.6511 | 25.8074 | 18.5483 | 14.9147 | 26.756 | 25.494 | 18.3231 | 14.5969 | 26.8691 | 25.3577 | 18.2251 | 14.2467 | 26.9932 | 25.2452 | 18.1442 | 14.0347 | 27.1273 | 25.1269 | 18.0592 | 13.7875 | 27.2741 | 24.9928 | 17.9628 | 13.449 | 27.85 | 24.4479 | 17.5712 | 12.0282 | 28.2016 | 24.0228 | 17.2657 | 11.4287 | 28.2635 | 23.849 | 17.1408 | 11.529 | 28.2052 | 23.7464 | 17.067 | 11.8633
HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 31.7981 | 11.0085 | 8.0306 | 11.4759 | 31.8918 | 10.8858 | 7.9411 | 11.2026 | 31.9347 | 10.6794 | 7.7905 | 10.9492 | 32.021 | 10.5868 | 7.7229 | 10.5587 | 32.1409 | 10.4532 | 7.6254 | 10.3913 | 32.2905 | 10.261 | 7.4853 | 9.9032 | 32.4592 | 10.0425 | 7.3258 | 9.4268 | 32.6435 | 9.842 | 7.1796 | 8.9947 | 32.842 | 9.8165 | 7.161 | 8.5072 | 33.0598 | 9.6832 | 7.0637 | 7.8669 | 33.8686 | 9.039 | 6.5938 | 5.8881 | 34.4882 | 8.9072 | 6.4977 | 4.825 | 34.9063 | 9.4782 | 6.9142 | 4.5584 | 35.2503 | 9.5988 | 7.0022 | 4.6818 | 31.745 | 11.0411 | 8.0543 | 11.5567 | 31.8006 | 11.0366 | 8.051 | 11.3398 | 31.8999 | 10.974 | 8.0054 | 10.9789 | 32.0226 | 10.8735 | 7.9321 | 10.562 | 32.1626 | 10.8003 | 7.8787 | 10.3969 | 32.3195 | 10.6788 | 7.79 | 9.9137 | 32.4942 | 10.5632 | 7.7057 | 9.4338 | 32.6837 | 10.458 | 7.629 | 8.9926 | 32.8733 | 10.3427 | 7.5449 | 8.4837 | 33.0521 | 10.2082 | 7.4468 | 7.8848 | 33.5008 | 9.9107 | 7.2297 | 6.519 | 33.874 | 9.865 | 7.1964 | 5.4691 | 34.133 | 10.2339 | 7.4655 | 4.8144 | 34.3142 | 10.321 | 7.529 | 4.4241 | 31.7982 | 11.0398 | 8.0534 | 11.4875 | 31.892 | 11.0388 | 8.0527 | 11.23 | 31.9352 | 10.9523 | 7.9895 | 10.9933 | 32.0218 | 10.832 | 7.9018 | 10.6198 | 32.1416 | 10.7324 | 7.8291 | 10.4668 | 32.2907 | 10.587 | 7.723 | 9.9983 | 32.4589 | 10.4519 | 7.6245 | 9.5407 | 32.643 | 10.3258 | 7.5325 | 9.1258 | 32.8391 | 10.1783 | 7.4249 | 8.6646 | 33.0461 | 10.0133 | 7.3046 | 8.0829 | 33.7995 | 9.4962 | 6.9273 | 6.3277 | 34.2998 | 9.4455 | 6.8903 | 5.3699 | 34.6569 | 10.1011 | 7.3686 | 5.1744 | 34.9079 | 10.1306 | 7.3902 | 5.2957 | 31.7907 | 11.0073 | 8.0297 | 11.4823 | 31.8823 | 10.873 | 7.9317 | 11.2165 | 31.9383 | 10.6371 | 7.7596 | 10.978 | 32.0535 | 10.5575 | 7.7015 | 10.606 | 32.222 | 10.4271 | 7.6064 | 10.4715 | 32.4442 | 10.1869 | 7.4312 | 10.019 | 32.7139 | 9.8987 | 7.221 | 9.5595 | 33.0257 | 9.8818 | 7.2087 | 9.1417 | 33.3495 | 9.7772 | 7.1323 | 8.7102 | 33.6346 | 9.606 | 7.0074 | 8.1987 | 34.8305 | 8.6475 | 6.3083 | 5.5991 | 36.0328 | 7.5368 | 5.498 | 0.034172 | 36.5551 | 7.1352 | 5.2051 | -4.338 | 36.7832 | 6.7377 | 4.9151 | -7.184 | 31.7745 | 11.0166 | 8.0365 | 11.5299 | 31.8672 | 10.9234 | 7.9685 | 11.2715 | 31.9266 | 10.7346 | 7.8308 | 11.0501 | 32.0336 | 10.5786 | 7.717 | 10.7335 | 32.1926 | 10.4586 | 7.6294 | 10.6459 | 32.398 | 10.2285 | 7.4616 | 10.2652 | 32.6571 | 9.9724 | 7.2747 | 9.8801 | 32.9486 | 9.9237 | 7.2392 | 9.5396 | 33.2648 | 9.8395 | 7.1778 | 9.0387 | 33.6645 | 9.555 | 6.9703 | 7.5724 | 34.9637 | 9.2001 | 6.7113 | 1.2598 | 35.7446 | 7.7412 | 5.6471 | -3.7475 | 35.969 | 7.2133 | 5.262 | -6.5884 | 35.8438 | 7.1201 | 5.194 | -5.6275
HYNDBURN RD | HUNCOAT | PADIHAM | 375688 | 428877 | 30.0648 | 15.0099 | 10.9495 | 16.3475 | 30.1222 | 14.7629 | 10.7693 | 16.133 | 30.1199 | 14.4513 | 10.542 | 16.1495 | 30.1377 | 14.2584 | 10.4013 | 16.0745 | 30.1689 | 13.8591 | 10.1101 | 15.9747 | 30.2138 | 13.7568 | 10.0354 | 15.8433 | 30.2619 | 13.6794 | 9.979 | 15.7013 | 30.3127 | 13.6152 | 9.9321 | 15.556 | 30.3662 | 13.5145 | 9.8587 | 15.4112 | 30.4235 | 13.3967 | 9.7727 | 15.2591 | 30.7258 | 12.8813 | 9.3967 | 14.6451 | 31.1476 | 12.7964 | 9.3348 | 14.1021 | 31.4902 | 13.7133 | 10.0036 | 13.8218 | 31.8666 | 13.6809 | 9.9801 | 13.6147 | 30.0088 | 15.0963 | 11.0126 | 16.5484 | 30.0254 | 14.7262 | 10.7426 | 16.5133 | 30.0657 | 14.5722 | 10.6302 | 16.3767 | 30.1191 | 14.4261 | 10.5237 | 16.2095 | 30.1805 | 14.2393 | 10.3873 | 16.0509 | 30.2489 | 14.0431 | 10.2443 | 15.8577 | 30.3251 | 13.9783 | 10.197 | 15.6461 | 30.4078 | 13.9051 | 10.1436 | 15.3705 | 30.498 | 13.8199 | 10.0815 | 15.0254 | 30.5948 | 13.7278 | 10.0142 | 14.6536 | 30.7809 | 13.6186 | 9.9346 | 14.2754 | 31.0054 | 13.6422 | 9.9518 | 13.9284 | 31.2487 | 14.1937 | 10.3541 | 13.7454 | 31.4532 | 14.5556 | 10.6181 | 13.6282 | 30.0649 | 15.0829 | 11.0028 | 16.355 | 30.1227 | 14.781 | 10.7825 | 16.1598 | 30.1207 | 14.641 | 10.6804 | 16.1572 | 30.1391 | 14.4377 | 10.5321 | 16.0886 | 30.1709 | 14.2025 | 10.3605 | 15.9902 | 30.2162 | 13.9549 | 10.1799 | 15.8695 | 30.2648 | 13.8671 | 10.1158 | 15.7293 | 30.316 | 13.7669 | 10.0427 | 15.5891 | 30.3695 | 13.6591 | 9.9641 | 15.454 | 30.4251 | 13.5459 | 9.8816 | 15.3128 | 30.6754 | 13.2637 | 9.6757 | 14.7632 | 30.9324 | 13.3993 | 9.7746 | 14.3751 | 31.192 | 14.5321 | 10.601 | 14.1692 | 31.4128 | 14.6494 | 10.6865 | 14.0796 | 30.059 | 15.0099 | 10.9495 | 16.3603 | 30.1117 | 14.7609 | 10.7679 | 16.1581 | 30.1076 | 14.4892 | 10.5697 | 16.1851 | 30.1269 | 14.2383 | 10.3866 | 16.1194 | 30.1633 | 13.8798 | 10.1251 | 16.0247 | 30.2238 | 13.7334 | 10.0183 | 15.8933 | 30.2982 | 13.676 | 9.9764 | 15.7416 | 30.3853 | 13.5447 | 9.8807 | 15.5784 | 30.4839 | 13.4419 | 9.8057 | 15.4195 | 30.5939 | 13.2807 | 9.6881 | 15.2607 | 31.235 | 12.6068 | 9.1965 | 14.0515 | 31.9905 | 11.9945 | 8.7498 | 11.4388 | 32.4698 | 12.3724 | 9.0255 | 9.3948 | 32.6624 | 12.1072 | 8.832 | 8.0288 | 30.05 | 15.0181 | 10.9555 | 16.3812 | 30.0974 | 15.0219 | 10.9583 | 16.1916 | 30.091 | 14.933 | 10.8934 | 16.2305 | 30.1057 | 14.7992 | 10.7958 | 16.1788 | 30.1381 | 14.6965 | 10.7209 | 16.1018 | 30.2002 | 14.6196 | 10.6648 | 15.9893 | 30.285 | 14.4997 | 10.5773 | 15.8383 | 30.3872 | 14.3798 | 10.4899 | 15.6783 | 30.5105 | 14.174 | 10.3397 | 15.4578 | 30.6671 | 13.9537 | 10.179 | 14.8505 | 31.4507 | 13.3722 | 9.7548 | 12.0014 | 32.1149 | 12.4868 | 9.109 | 9.5041 | 32.3885 | 11.8652 | 8.6555 | 8.059 | 32.3632 | 11.9465 | 8.7148 | 8.6521
INDIA ST | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 22.7301 | 15.2989 | 11.1603 | 17.4378 | 22.778 | 13.8049 | 10.0705 | 16.9417 | 22.8127 | 12.2548 | 8.9397 | 16.7217 | 22.8687 | 10.6217 | 7.7484 | 16.3873 | 22.9443 | 8.977 | 6.5486 | 16.2709 | 23.0372 | 7.3366 | 5.3519 | 15.9141 | 23.1365 | 7.281 | 5.3114 | 15.6305 | 23.2214 | 7.2002 | 5.2524 | 15.3957 | 23.3144 | 7.0755 | 5.1615 | 15.0295 | 23.4204 | 6.9213 | 5.049 | 14.6121 | 26.1655 | 6.1957 | 4.5197 | 11.0191 | 27.02 | 8.815 | 6.4304 | 9.9479 | 27.3428 | 12.8981 | 9.409 | 9.7009 | 27.6191 | 13.6011 | 9.9218 | 9.8508 | 22.7136 | 15.3593 | 11.2044 | 17.6218 | 22.752 | 13.6389 | 9.9494 | 17.3158 | 22.8141 | 11.8842 | 8.6694 | 17.1045 | 22.881 | 10.0453 | 7.3279 | 16.7941 | 22.9561 | 8.1418 | 5.9393 | 16.6983 | 23.0382 | 6.6555 | 4.8551 | 16.3707 | 23.1107 | 6.536 | 4.7679 | 16.1092 | 23.1882 | 6.4223 | 4.685 | 15.8922 | 23.2718 | 6.2861 | 4.5857 | 15.5436 | 23.3601 | 6.1324 | 4.4735 | 15.2029 | 23.5916 | 6.4492 | 4.7046 | 14.3607 | 23.8221 | 8.2984 | 6.0536 | 13.6823 | 24.0348 | 11.243 | 8.2016 | 13.1893 | 24.206 | 11.8643 | 8.6549 | 12.9469 | 22.7302 | 15.358 | 11.2035 | 17.4329 | 22.7782 | 13.6552 | 9.9613 | 16.9617 | 22.8132 | 11.9201 | 8.6955 | 16.7416 | 22.8695 | 10.1624 | 7.4133 | 16.4333 | 22.9452 | 8.4167 | 6.1398 | 16.3292 | 23.0379 | 6.6054 | 4.8186 | 15.988 | 23.1374 | 6.6023 | 4.8163 | 15.7179 | 23.2223 | 6.5659 | 4.7897 | 15.495 | 23.3144 | 6.5083 | 4.7477 | 15.1489 | 23.4157 | 6.4602 | 4.7126 | 14.772 | 26.1113 | 6.686 | 4.8774 | 11.3345 | 26.8547 | 9.3485 | 6.8196 | 10.4108 | 27.1321 | 13.4271 | 9.7949 | 10.1973 | 27.319 | 14.4762 | 10.5602 | 10.3889 | 22.7284 | 15.2933 | 11.1563 | 17.4403 | 22.7796 | 13.7994 | 10.0665 | 16.9456 | 22.8282 | 12.2304 | 8.9219 | 16.7315 | 22.9083 | 10.5874 | 7.7233 | 16.4072 | 23.0213 | 8.9507 | 6.5294 | 16.3088 | 23.1358 | 7.3114 | 5.3336 | 15.9699 | 23.2639 | 7.2287 | 5.2732 | 15.6939 | 23.4126 | 7.1045 | 5.1826 | 15.4685 | 23.5759 | 6.937 | 5.0605 | 15.1595 | 23.76 | 6.7648 | 4.9349 | 14.8629 | 26.8792 | 5.3269 | 3.8859 | 10.7056 | 29.0335 | 7.3888 | 5.39 | 5.0851 | 29.4671 | 10.4344 | 7.6117 | 1.5001 | 29.6632 | 10.7123 | 7.8145 | -0.62995 | 22.7228 | 15.2967 | 11.1588 | 17.4585 | 22.7796 | 15.1066 | 11.02 | 16.9469 | 22.8304 | 14.8643 | 10.8433 | 16.7463 | 22.905 | 14.4714 | 10.5567 | 16.4598 | 23.0115 | 14.6434 | 10.6822 | 16.3946 | 23.1105 | 14.815 | 10.8074 | 16.1057 | 23.238 | 14.7996 | 10.7961 | 15.8793 | 23.3852 | 14.7315 | 10.7464 | 15.7102 | 24.0112 | 14.5796 | 10.6356 | 14.8685 | 26.165 | 14.1499 | 10.3221 | 11.914 | 28.3266 | 13.629 | 9.9422 | 5.8067 | 28.9774 | 12.2019 | 8.9011 | 1.8509 | 29.1904 | 11.4291 | 8.3374 | -0.4886 | 29.1168 | 11.2872 | 8.2339 | 0.42271
INGLETON | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 368913 | 472337 | 12.5496 | 12.5496 | 12.5496 | 9.7089 | 12.5801 | 12.5801 | 12.5801 | 9.651 | 12.6268 | 12.6268 | 12.6268 | 9.5855 | 12.6784 | 12.6784 | 12.6784 | 9.4831 | 12.7051 | 12.7051 | 12.7051 | 9.4732 | 12.7364 | 12.7364 | 12.7364 | 9.3375 | 12.7736 | 12.7736 | 12.7736 | 9.2499 | 12.815 | 12.815 | 12.815 | 9.1395 | 12.8598 | 12.8598 | 12.8598 | 9.0782 | 12.9108 | 12.9108 | 12.9108 | 8.9295 | 13.101 | 13.101 | 13.101 | 8.4104 | 13.2476 | 13.2476 | 13.2476 | 8.1373 | 13.3324 | 13.3324 | 13.3324 | 7.9738 | 13.3736 | 13.3736 | 13.3736 | 7.9823 | 12.5583 | 12.5583 | 12.5583 | 9.752 | 12.5949 | 12.5949 | 12.5949 | 9.7289 | 12.6435 | 12.6435 | 12.6435 | 9.6363 | 12.688 | 12.688 | 12.688 | 9.5289 | 12.7368 | 12.7368 | 12.7368 | 9.5118 | 12.782 | 12.782 | 12.782 | 9.3711 | 12.8239 | 12.8239 | 12.8239 | 9.2746 | 12.8702 | 12.8702 | 12.8702 | 9.1513 | 12.9208 | 12.9208 | 12.9208 | 9.0763 | 12.97 | 12.97 | 12.97 | 8.9429 | 13.0899 | 13.0899 | 13.0899 | 8.6584 | 13.1897 | 13.1897 | 13.1897 | 8.3914 | 13.2454 | 13.2454 | 13.2454 | 8.1526 | 13.2752 | 13.2752 | 13.2752 | 7.9945 | 12.5496 | 12.5496 | 12.5496 | 9.7118 | 12.5801 | 12.5801 | 12.5801 | 9.6579 | 12.6268 | 12.6268 | 12.6268 | 9.598 | 12.6785 | 12.6785 | 12.6785 | 9.503 | 12.7059 | 12.7059 | 12.7059 | 9.4975 | 12.7367 | 12.7367 | 12.7367 | 9.3694 | 12.7731 | 12.7731 | 12.7731 | 9.288 | 12.8135 | 12.8135 | 12.8135 | 9.1845 | 12.8568 | 12.8568 | 12.8568 | 9.1294 | 12.9046 | 12.9046 | 12.9046 | 8.9971 | 13.0829 | 13.0829 | 13.0829 | 8.5272 | 13.208 | 13.208 | 13.208 | 8.2857 | 13.2711 | 13.2711 | 13.2711 | 8.1384 | 13.3012 | 13.3012 | 13.3012 | 8.1413 | 12.5511 | 12.5511 | 12.5511 | 9.7116 | 12.5854 | 12.5854 | 12.5854 | 9.6485 | 12.6359 | 12.6359 | 12.6359 | 9.5758 | 12.688 | 12.688 | 12.688 | 9.4647 | 12.7209 | 12.7209 | 12.7209 | 9.4384 | 12.7629 | 12.7629 | 12.7629 | 9.2777 | 12.8143 | 12.8143 | 12.8143 | 9.1562 | 12.8708 | 12.8708 | 12.8708 | 9.0103 | 12.9337 | 12.9337 | 12.9337 | 8.9293 | 13.0044 | 13.0044 | 13.0044 | 8.7918 | 13.2495 | 13.2495 | 13.2495 | 8.227 | 13.4545 | 13.4545 | 13.4545 | 7.5441 | 13.5707 | 13.5707 | 13.5707 | 7.0946 | 13.6291 | 13.6291 | 13.6291 | 6.7781 | 12.5557 | 12.5557 | 12.5557 | 9.7134 | 12.5991 | 12.5991 | 12.5991 | 9.6478 | 12.6504 | 12.6504 | 12.6504 | 9.5794 | 12.6782 | 12.6782 | 12.6782 | 9.4754 | 12.7071 | 12.7071 | 12.7071 | 9.4505 | 12.7441 | 12.7441 | 12.7441 | 9.2993 | 12.7893 | 12.7893 | 12.7893 | 9.194 | 12.8405 | 12.8405 | 12.8405 | 9.0694 | 12.8973 | 12.8973 | 12.8973 | 9.0028 | 12.9649 | 12.9649 | 12.9649 | 8.7856 | 13.1898 | 13.1898 | 13.1898 | 7.8606 | 13.3397 | 13.3397 | 13.3397 | 7.2953 | 13.411 | 13.411 | 13.411 | 7.0159 | 13.4258 | 13.4258 | 13.4258 | 7.1227
IRLAM | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 30.1459 | 13.5212 | 9.8635 | 9.3791 | 30.2862 | 13.1652 | 9.6038 | 8.1369 | 30.3362 | 12.7916 | 9.3313 | 7.5554 | 30.4214 | 12.5626 | 9.1642 | 7.0656 | 30.5399 | 12.3674 | 9.0219 | 7.2875 | 30.6888 | 12.2011 | 8.9005 | 6.6874 | 30.854 | 12.049 | 8.7895 | 6.127 | 31.0313 | 11.9256 | 8.6996 | 5.5621 | 31.221 | 11.7449 | 8.5677 | 4.8028 | 31.4288 | 11.564 | 8.4358 | 4.1664 | 32.9989 | 10.8293 | 7.8998 | 1.4236 | 35.257 | 10.4517 | 7.6244 | -1.2164 | 37.1639 | 11.5286 | 8.4099 | -2.6778 | 39.3397 | 11.1141 | 8.1076 | -4.7421 | 30.0588 | 13.3591 | 9.7453 | 9.816 | 30.1276 | 13.1722 | 9.609 | 9.0466 | 30.2362 | 12.9221 | 9.4265 | 8.4692 | 30.3602 | 12.6454 | 9.2246 | 7.9027 | 30.5057 | 12.4617 | 9.0906 | 8.1252 | 30.6677 | 12.3414 | 9.0029 | 7.5325 | 30.8477 | 12.2314 | 8.9227 | 6.9689 | 31.0403 | 12.1136 | 8.8367 | 6.3624 | 31.2461 | 11.9735 | 8.7345 | 5.6292 | 31.4624 | 11.8632 | 8.6541 | 5.0419 | 32.5298 | 11.4638 | 8.3627 | 2.8819 | 33.8402 | 11.2066 | 8.175 | 0.74935 | 35.2638 | 11.6325 | 8.4858 | -0.84797 | 36.5182 | 12.1873 | 8.8905 | -2.2273 | 30.1467 | 13.3545 | 9.7419 | 9.3896 | 30.2886 | 13.1666 | 9.6048 | 8.1916 | 30.3411 | 12.8928 | 9.4052 | 7.6319 | 30.4296 | 12.5705 | 9.17 | 7.1192 | 30.5517 | 12.3995 | 9.0453 | 7.3991 | 30.7038 | 12.2526 | 8.9381 | 6.8271 | 30.8721 | 12.1211 | 8.8422 | 6.2689 | 31.0523 | 11.9942 | 8.7496 | 5.6731 | 31.2435 | 11.8336 | 8.6324 | 5.0356 | 31.4471 | 11.7092 | 8.5417 | 4.4604 | 32.7532 | 11.2229 | 8.1869 | 1.9674 | 34.138 | 11.0804 | 8.083 | -0.018317 | 35.6055 | 12.5045 | 9.1218 | -1.2883 | 36.9383 | 12.3257 | 8.9915 | -2.1532 | 30.1394 | 13.5237 | 9.8654 | 9.3836 | 30.2786 | 13.1504 | 9.5931 | 8.1517 | 30.3399 | 12.7779 | 9.3213 | 7.5732 | 30.4505 | 12.5434 | 9.1502 | 7.0601 | 30.6019 | 12.343 | 9.004 | 7.3147 | 30.837 | 12.1699 | 8.8778 | 6.7215 | 31.1456 | 12.0161 | 8.7656 | 6.1242 | 31.5025 | 11.8372 | 8.6351 | 5.486 | 31.9009 | 11.6233 | 8.479 | 4.6909 | 32.3504 | 11.4544 | 8.3558 | 4.1053 | 35.7055 | 10.3318 | 7.5369 | -0.24302 | 39.8254 | 8.8708 | 6.4711 | -8.5045 | 41.7122 | 8.8272 | 6.4393 | -15.6878 | 42.268 | 8.0006 | 5.8363 | -20.0379 | 30.1394 | 13.5327 | 9.8719 | 9.4095 | 30.2917 | 13.1779 | 9.6131 | 8.1659 | 30.373 | 12.8219 | 9.3534 | 7.5919 | 30.5039 | 12.5182 | 9.1319 | 7.1209 | 30.6813 | 12.3169 | 8.985 | 7.3743 | 30.9791 | 12.1108 | 8.8346 | 6.7983 | 31.3775 | 11.9329 | 8.7049 | 6.2021 | 31.8671 | 11.773 | 8.5882 | 5.5779 | 32.4586 | 11.5788 | 8.4466 | 4.5552 | 33.2361 | 11.2791 | 8.228 | 2.9158 | 37.502 | 11.4477 | 8.3509 | -5.5952 | 40.8412 | 9.5772 | 6.9864 | -13.8377 | 41.7233 | 8.4007 | 6.1282 | -18.9927 | 41.5604 | 8.229 | 6.0029 | -18.7652
JAMES ST | CARLISLE | HARKER / HUTTON | 340034 | 555418 | 32.4933 | 9.7824 | 7.0308 | 9.5799 | 32.6142 | 9.4693 | 6.8058 | 8.689 | 32.6625 | 9.2471 | 6.6461 | 8.7221 | 32.7424 | 8.869 | 6.3743 | 8.4289 | 32.8381 | 8.5809 | 6.1673 | 8.3196 | 32.9611 | 8.0828 | 5.8092 | 7.7543 | 33.0936 | 7.7103 | 5.5416 | 7.3928 | 33.2273 | 7.4287 | 5.3392 | 7.4085 | 33.3678 | 7.0757 | 5.0855 | 6.8167 | 33.5183 | 6.7671 | 4.8636 | 6.4989 | 34.1596 | 5.8632 | 4.214 | 5.0904 | 33.5381 | 5.5218 | 3.9686 | 3.9224 | 35.378 | 5.8247 | 4.1863 | 3.1753 | 34.9116 | 5.7479 | 4.1312 | 2.8398 | 32.4346 | 9.8982 | 7.1141 | 9.9955 | 32.5238 | 9.7146 | 6.9821 | 9.4609 | 32.6612 | 9.5383 | 6.8554 | 9.299 | 32.813 | 9.3154 | 6.6952 | 8.8757 | 32.9759 | 9.1284 | 6.5608 | 8.6676 | 33.1204 | 8.7498 | 6.2886 | 8.0445 | 33.2819 | 8.4958 | 6.1061 | 7.5899 | 33.4565 | 8.3037 | 5.968 | 7.5077 | 33.6444 | 8.0122 | 5.7585 | 6.7803 | 33.8443 | 7.7151 | 5.545 | 6.2214 | 34.2451 | 7.541 | 5.4199 | 5.2158 | 34.6721 | 7.3045 | 5.2499 | 4.3629 | 35.0988 | 7.4719 | 5.3702 | 3.7356 | 35.4391 | 7.7524 | 5.5718 | 3.4612 | 32.4935 | 9.8914 | 7.1091 | 9.5921 | 32.6148 | 9.6935 | 6.9669 | 8.7307 | 32.6638 | 9.4873 | 6.8187 | 8.7846 | 32.7449 | 9.1512 | 6.5771 | 8.5146 | 32.8415 | 8.9501 | 6.4326 | 8.4282 | 32.9651 | 8.5553 | 6.1489 | 7.8944 | 33.0983 | 8.1389 | 5.8496 | 7.5606 | 33.2328 | 7.9403 | 5.7069 | 7.5957 | 33.3728 | 7.5958 | 5.4592 | 7.0427 | 33.5187 | 7.3916 | 5.3125 | 6.7731 | 34.0666 | 6.9861 | 5.021 | 5.5542 | 34.5503 | 6.8439 | 4.9189 | 4.7001 | 34.9889 | 7.1226 | 5.1191 | 4.1126 | 35.3434 | 6.8982 | 4.9579 | 4.0045 | 32.4861 | 9.7803 | 7.0293 | 9.5917 | 32.6037 | 9.4421 | 6.7862 | 8.7097 | 32.6558 | 9.1902 | 6.6052 | 8.7446 | 32.7359 | 8.8249 | 6.3426 | 8.4419 | 32.8476 | 8.4321 | 6.0603 | 8.322 | 33.0073 | 7.9574 | 5.7191 | 7.7355 | 33.1954 | 7.5564 | 5.431 | 7.3303 | 33.4101 | 7.2398 | 5.2034 | 7.2895 | 33.65 | 6.7996 | 4.887 | 6.6496 | 33.8824 | 6.4086 | 4.606 | 6.3192 | 32.8507 | 5.4086 | 3.8873 | 3.8101 | 24.188 | 3.9824 | 2.8622 | -1.7749 | 21.2829 | 3.5041 | 2.5184 | -6.4837 | 16.5589 | 2.7263 | 1.9594 | -9.27 | 32.4612 | 9.7848 | 7.0326 | 9.6159 | 32.5609 | 9.5348 | 6.8529 | 8.7392 | 32.5859 | 9.188 | 6.6036 | 8.7852 | 32.6369 | 8.8415 | 6.3546 | 8.5102 | 32.7225 | 8.5522 | 6.1466 | 8.4244 | 32.8642 | 8.0936 | 5.817 | 7.8792 | 33.0569 | 7.7552 | 5.5738 | 7.5026 | 33.2853 | 7.5461 | 5.4236 | 7.4897 | 33.5526 | 7.2474 | 5.2089 | 6.7861 | 33.8805 | 6.8771 | 4.9427 | 5.5955 | 30.2706 | 4.9838 | 3.582 | -0.59146 | 20.4163 | 3.3614 | 2.4159 | -5.9635 | 15.8738 | 2.6135 | 1.8784 | -9.14 | 15.425 | 2.5396 | 1.8253 | -8.0565
KAY ST | HUNCOAT | PADIHAM | 373863 | 427594 | 29.3915 | 14.9352 | 10.895 | 17.5835 | 29.432 | 14.5653 | 10.6252 | 17.4328 | 29.4643 | 14.207 | 10.3638 | 17.2594 | 29.5171 | 13.9097 | 10.1469 | 17.0121 | 29.5886 | 13.6393 | 9.9497 | 16.7077 | 29.6761 | 13.3454 | 9.7353 | 16.3631 | 29.778 | 13.2539 | 9.6685 | 15.983 | 29.8908 | 13.2585 | 9.6719 | 15.5822 | 30.0141 | 13.1797 | 9.6144 | 15.1284 | 30.1528 | 13.0554 | 9.5237 | 14.5989 | 30.7505 | 12.6068 | 9.1965 | 12.8852 | 31.2613 | 12.4571 | 9.0873 | 12.1829 | 31.5521 | 13.3834 | 9.763 | 12.2287 | 31.7622 | 13.3705 | 9.7536 | 12.4829 | 29.3733 | 14.9346 | 10.8946 | 17.6298 | 29.4021 | 14.5816 | 10.6371 | 17.5248 | 29.4564 | 14.2027 | 10.3607 | 17.3155 | 29.5217 | 13.9913 | 10.2064 | 17.083 | 29.5972 | 13.6654 | 9.9687 | 16.8145 | 29.6834 | 13.5558 | 9.8888 | 16.5103 | 29.7796 | 13.4841 | 9.8365 | 16.1721 | 29.8836 | 13.4069 | 9.7802 | 15.8119 | 29.9966 | 13.3235 | 9.7193 | 15.4262 | 30.1169 | 13.2101 | 9.6366 | 15.0485 | 30.3916 | 12.9217 | 9.4262 | 13.9759 | 30.6332 | 12.8431 | 9.3689 | 13.2434 | 30.8178 | 13.367 | 9.751 | 12.9127 | 30.9539 | 13.7914 | 10.0606 | 12.7684 | 29.3919 | 14.9301 | 10.8913 | 17.5909 | 29.4327 | 14.5345 | 10.6027 | 17.4627 | 29.4651 | 14.2181 | 10.3719 | 17.3056 | 29.5181 | 13.9764 | 10.1956 | 17.0694 | 29.5895 | 13.7108 | 10.0019 | 16.7785 | 29.6764 | 13.4225 | 9.7915 | 16.4481 | 29.7776 | 13.2953 | 9.6987 | 16.082 | 29.8897 | 13.1845 | 9.6179 | 15.6772 | 30.0108 | 13.0491 | 9.5191 | 15.2239 | 30.142 | 12.8992 | 9.4098 | 14.7416 | 30.6897 | 12.5021 | 9.1201 | 13.1896 | 31.1098 | 12.4943 | 9.1144 | 12.6106 | 31.3643 | 13.5921 | 9.9152 | 12.693 | 31.5178 | 13.5029 | 9.8502 | 13.0248 | 29.39 | 14.9358 | 10.8955 | 17.5893 | 29.4324 | 14.5752 | 10.6324 | 17.4487 | 29.475 | 14.2231 | 10.3755 | 17.2932 | 29.5472 | 13.925 | 10.1581 | 17.0728 | 29.6495 | 13.6454 | 9.9541 | 16.8091 | 29.7833 | 13.3867 | 9.7654 | 16.5111 | 29.9516 | 13.3674 | 9.7513 | 16.1745 | 30.1477 | 13.2747 | 9.6837 | 15.8258 | 30.3648 | 13.2073 | 9.6346 | 15.5105 | 30.6091 | 13.1126 | 9.5654 | 15.2109 | 31.4403 | 12.3762 | 9.0283 | 13.0117 | 32.2171 | 11.2823 | 8.2302 | 8.3965 | 32.6835 | 11.3327 | 8.267 | 4.9561 | 32.9182 | 10.7811 | 7.8647 | 2.8414 | 29.3826 | 14.9424 | 10.9003 | 17.6046 | 29.4279 | 14.9163 | 10.8813 | 17.4269 | 29.4737 | 14.7909 | 10.7897 | 17.2636 | 29.5426 | 14.762 | 10.7687 | 17.0689 | 29.6419 | 14.6927 | 10.7181 | 16.8296 | 29.7692 | 14.609 | 10.6571 | 16.5784 | 29.9341 | 14.5177 | 10.5904 | 16.2897 | 30.1219 | 14.4465 | 10.5385 | 16.0032 | 30.3559 | 14.3166 | 10.4438 | 15.5777 | 30.6085 | 14.0264 | 10.232 | 14.4249 | 31.4961 | 13.2889 | 9.6941 | 9.1558 | 32.0911 | 11.8373 | 8.6351 | 5.053 | 32.3222 | 11.063 | 8.0703 | 2.9231 | 32.2599 | 10.932 | 7.9748 | 4.0174
KENDAL | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351915 | 491858 | 28.456 | 9.4765 | 6.8109 | 8.1873 | 28.5498 | 9.3182 | 6.6972 | 7.4306 | 28.5871 | 9.2403 | 6.6412 | 7.3663 | 28.675 | 9.0652 | 6.5154 | 6.8671 | 28.792 | 8.9491 | 6.4319 | 6.724 | 28.939 | 8.7254 | 6.2711 | 6.0689 | 29.1088 | 8.498 | 6.1077 | 5.4941 | 29.2935 | 8.3485 | 6.0003 | 5.2963 | 29.4927 | 8.106 | 5.826 | 4.5944 | 29.715 | 7.8676 | 5.6546 | 3.8851 | 30.5656 | 6.8835 | 4.9473 | 1.4687 | 31.2684 | 6.169 | 4.4338 | 0.025511 | 31.7168 | 5.7826 | 4.1561 | -0.78302 | 31.9729 | 5.6554 | 4.0646 | -0.6059 | 28.409 | 9.5169 | 6.84 | 8.3383 | 28.4748 | 9.3918 | 6.7501 | 7.7116 | 28.5826 | 9.308 | 6.6899 | 7.5395 | 28.7274 | 9.1713 | 6.5916 | 7.0196 | 28.8922 | 9.0905 | 6.5335 | 6.8597 | 29.0779 | 8.8994 | 6.3961 | 6.1858 | 29.289 | 8.7362 | 6.2789 | 5.5782 | 29.5192 | 8.633 | 6.2047 | 5.3366 | 29.7592 | 8.4463 | 6.0705 | 4.5891 | 30.0026 | 8.2733 | 5.9462 | 3.967 | 30.4623 | 7.8289 | 5.6268 | 2.4592 | 30.9078 | 7.3584 | 5.2887 | 0.96818 | 31.1933 | 7.0417 | 5.061 | -0.30173 | 31.356 | 6.8591 | 4.9298 | -1.0252 | 28.4579 | 9.5132 | 6.8373 | 8.2012 | 28.5524 | 9.3829 | 6.7437 | 7.4884 | 28.5895 | 9.2738 | 6.6653 | 7.46 | 28.6778 | 9.0822 | 6.5275 | 6.9939 | 28.7944 | 8.9632 | 6.4421 | 6.8773 | 28.94 | 8.7344 | 6.2776 | 6.2576 | 29.1077 | 8.5275 | 6.1289 | 5.7149 | 29.2899 | 8.3814 | 6.0239 | 5.5395 | 29.4843 | 8.142 | 5.8518 | 4.8837 | 29.6944 | 7.9328 | 5.7015 | 4.2569 | 30.4908 | 7.1784 | 5.1593 | 2.118 | 31.0813 | 6.5129 | 4.681 | 0.87438 | 31.4461 | 6.0398 | 4.3409 | 0.26802 | 31.6257 | 5.6478 | 4.0592 | 0.4203 | 28.4507 | 9.4758 | 6.8104 | 8.1972 | 28.5429 | 9.2608 | 6.6559 | 7.4367 | 28.5835 | 9.1614 | 6.5845 | 7.37 | 28.6907 | 8.9598 | 6.4396 | 6.8556 | 28.8403 | 8.8112 | 6.3328 | 6.6878 | 29.0392 | 8.5428 | 6.1399 | 5.9901 | 29.2856 | 8.265 | 5.9402 | 5.3354 | 29.5675 | 8.0617 | 5.7941 | 5.063 | 29.8805 | 7.7799 | 5.5916 | 4.3688 | 30.2289 | 7.5114 | 5.3986 | 3.816 | 31.5057 | 6.1044 | 4.3873 | 0.73333 | 25.8609 | 4.2578 | 3.0602 | -5.4759 | 18.0141 | 2.9659 | 2.1316 | -10.4496 | 12.6911 | 2.0895 | 1.5018 | -13.685 | 28.4338 | 9.4821 | 6.815 | 8.2278 | 28.5211 | 9.3198 | 6.6983 | 7.4705 | 28.5532 | 9.1982 | 6.6109 | 7.4346 | 28.6418 | 8.9814 | 6.4551 | 6.9785 | 28.7729 | 8.821 | 6.3398 | 6.8445 | 28.9503 | 8.5191 | 6.1228 | 6.2163 | 29.1819 | 8.2458 | 5.9264 | 5.6522 | 29.4432 | 8.0556 | 5.7897 | 5.4786 | 29.7401 | 7.7687 | 5.5836 | 4.7448 | 30.1085 | 7.3266 | 5.2658 | 3.1927 | 31.4085 | 5.2515 | 3.7743 | -3.8641 | 20.8349 | 3.4303 | 2.4654 | -9.4415 | 16.2852 | 2.6812 | 1.9271 | -12.8219 | 15.1988 | 2.5024 | 1.7985 | -11.8813
KESWICK | STAINBURN & SIDDICK | HARKER / HUTTON | 327022 | 523784 | 18.3008 | 18.3008 | 18.3008 | 5.6502 | 18.3626 | 18.3626 | 18.3626 | 5.3475 | 18.4442 | 18.4442 | 18.4442 | 5.1637 | 18.5431 | 18.5431 | 18.5431 | 4.9787 | 18.6564 | 18.6564 | 18.6564 | 4.8425 | 18.7809 | 18.7809 | 18.7809 | 4.6447 | 18.928 | 18.928 | 18.928 | 4.3617 | 19.0819 | 19.0819 | 19.0819 | 4.1771 | 19.2391 | 19.2391 | 19.2391 | 3.9709 | 19.4497 | 19.4497 | 19.3468 | 3.6463 | 20.1115 | 20.1115 | 18.9481 | 2.5454 | 20.5646 | 20.5646 | 18.6972 | 1.9601 | 20.6693 | 20.6693 | 18.5739 | 1.6991 | 20.6806 | 20.6806 | 18.4795 | 1.8451 | 18.3037 | 18.3037 | 18.3037 | 5.9055 | 18.3643 | 18.3643 | 18.3643 | 5.8192 | 18.447 | 18.447 | 18.447 | 5.5584 | 18.5132 | 18.5132 | 18.5132 | 5.3271 | 18.5943 | 18.5943 | 18.5943 | 5.1508 | 18.6862 | 18.6862 | 18.6862 | 4.9273 | 18.7933 | 18.7933 | 18.7933 | 4.6066 | 18.9086 | 18.9086 | 18.9086 | 4.3683 | 19.0308 | 19.0308 | 19.0308 | 3.6904 | 19.1588 | 19.1588 | 19.1588 | 2.8777 | 19.5397 | 19.5397 | 19.315 | 2.4042 | 19.9118 | 19.9118 | 19.194 | 2.1331 | 20.1848 | 20.1848 | 19.1196 | 2.0748 | 20.3654 | 20.3654 | 19.0587 | 1.962 | 18.3008 | 18.3008 | 18.3008 | 5.6602 | 18.3626 | 18.3626 | 18.3626 | 5.3725 | 18.4442 | 18.4442 | 18.4442 | 5.2084 | 18.5431 | 18.5431 | 18.5431 | 5.0459 | 18.6559 | 18.6559 | 18.6559 | 4.9303 | 18.7798 | 18.7798 | 18.7798 | 4.7539 | 18.9262 | 18.9262 | 18.9262 | 4.4948 | 19.0799 | 19.0799 | 19.0799 | 4.3316 | 19.2352 | 19.2352 | 19.2352 | 4.1493 | 19.4379 | 19.4379 | 19.3126 | 3.8721 | 20.0872 | 20.0872 | 19.0485 | 2.9197 | 20.5241 | 20.5241 | 18.8658 | 2.4364 | 20.6294 | 20.6294 | 18.7479 | 2.2292 | 20.6389 | 20.6389 | 18.5854 | 2.3675 | 18.3016 | 18.3016 | 18.3016 | 5.6567 | 18.3813 | 18.3813 | 18.3813 | 5.345 | 18.4951 | 18.4951 | 18.4951 | 5.1459 | 18.635 | 18.635 | 18.635 | 4.9459 | 18.8062 | 18.8062 | 18.8062 | 4.777 | 19.0012 | 19.0012 | 19.0012 | 4.5328 | 19.2512 | 19.2512 | 19.2512 | 4.1787 | 19.5349 | 19.5349 | 19.4229 | 3.9157 | 19.7374 | 19.7374 | 19.3223 | 3.6533 | 19.9608 | 19.9608 | 19.2107 | 3.3388 | 20.688 | 20.688 | 18.6941 | 1.9954 | 20.9638 | 20.9638 | 18.0825 | -0.48408 | 21.0192 | 21.0192 | 17.6537 | -2.3797 | 21.0149 | 21.0149 | 17.292 | -3.8035 | 18.3057 | 18.3057 | 18.3057 | 5.662 | 18.4008 | 18.4008 | 18.4008 | 5.3461 | 18.5231 | 18.5231 | 18.5231 | 5.1544 | 18.6598 | 18.6598 | 18.6598 | 4.9634 | 18.8231 | 18.8231 | 18.8231 | 4.8024 | 19.0103 | 19.0103 | 19.0103 | 4.5832 | 19.2452 | 19.2452 | 19.2452 | 4.2697 | 19.463 | 19.463 | 19.4118 | 4.0611 | 19.6437 | 19.6437 | 19.3076 | 3.8418 | 19.9629 | 19.9629 | 19.1404 | 3.1851 | 20.5218 | 20.5218 | 18.411 | 0.33984 | 20.6904 | 20.6904 | 17.7104 | -2.0766 | 20.666 | 20.666 | 17.3918 | -3.3238 | 20.5546 | 20.5546 | 17.3352 | -2.8447
KINGSWAY | BELFIELD | ROCHDALE | 391636 | 411724 | 41.3777 | 8.518 | 6.122 | 38.5896 | 41.4514 | 7.3716 | 5.2981 | 38.212 | 37.8644 | 6.2341 | 4.4806 | 37.8644 | 31.2464 | 5.1445 | 3.6974 | 31.2464 | 24.7742 | 4.0789 | 2.9316 | 24.7742 | 24.0302 | 3.9564 | 2.8435 | 24.0302 | 23.4092 | 3.8541 | 2.7701 | 23.4092 | 22.7202 | 3.7407 | 2.6885 | 22.7202 | 22.9138 | 3.7726 | 2.7114 | 22.9138 | 22.5183 | 3.7075 | 2.6646 | 22.5183 | 22.0788 | 3.6351 | 2.6126 | 22.0788 | 30.5628 | 5.0319 | 3.6166 | 30.5628 | 43.1819 | 7.5615 | 5.4346 | 36.4422 | 43.7989 | 8.1299 | 5.8431 | 35.861 | 41.3079 | 8.6043 | 6.1841 | 38.8741 | 41.3195 | 7.6371 | 5.4889 | 38.7593 | 40.3864 | 6.6493 | 4.779 | 38.5988 | 34.3242 | 5.6512 | 4.0616 | 34.3242 | 28.1376 | 4.6326 | 3.3296 | 28.1376 | 27.7464 | 4.5682 | 3.2833 | 27.7464 | 27.4292 | 4.516 | 3.2457 | 27.4292 | 27.2198 | 4.4815 | 3.221 | 27.2198 | 27.0318 | 4.4506 | 3.1987 | 27.0318 | 26.7553 | 4.4051 | 3.166 | 26.7553 | 26.5952 | 4.3787 | 3.1471 | 26.5952 | 32.7414 | 5.3906 | 3.8743 | 32.7414 | 42.4565 | 6.9901 | 5.0239 | 37.2163 | 42.994 | 7.3664 | 5.2943 | 36.9286 | 41.3779 | 8.6093 | 6.1877 | 38.5899 | 41.4521 | 7.6292 | 5.4833 | 38.2125 | 39.9428 | 6.5763 | 4.7265 | 38.0259 | 33.508 | 5.5168 | 3.9651 | 33.508 | 26.8881 | 4.4269 | 3.1817 | 26.8881 | 25.9646 | 4.2749 | 3.0724 | 25.9646 | 26.0391 | 4.2871 | 3.0812 | 26.0391 | 25.9589 | 4.2739 | 3.0718 | 25.9589 | 25.8248 | 4.2519 | 3.0559 | 25.8248 | 25.5474 | 4.2062 | 3.0231 | 25.5474 | 26.1504 | 4.3055 | 3.0944 | 26.1504 | 35.1323 | 5.7843 | 4.1573 | 35.1323 | 42.7045 | 8.2723 | 5.9454 | 36.8894 | 43.0572 | 8.8627 | 6.3698 | 36.5676 | 41.3721 | 8.5192 | 6.1229 | 38.6007 | 41.4404 | 7.3823 | 5.3058 | 38.2347 | 37.5734 | 6.1862 | 4.4461 | 37.5734 | 31.1028 | 5.1208 | 3.6804 | 31.1028 | 24.6019 | 4.0505 | 2.9112 | 24.6019 | 23.4335 | 3.8582 | 2.7729 | 23.4335 | 23.2419 | 3.8266 | 2.7503 | 23.2419 | 22.926 | 3.7746 | 2.7129 | 22.926 | 22.6759 | 3.7334 | 2.6833 | 22.6759 | 21.8635 | 3.5997 | 2.5871 | 21.8635 | 21.1867 | 3.4882 | 2.5071 | 21.1867 | 28.9145 | 4.7605 | 3.4215 | 28.9145 | 43.0585 | 7.0893 | 5.0952 | 35.3508 | 43.9744 | 7.626 | 5.481 | 35.0598 | 41.3812 | 9.4922 | 6.8222 | 38.5946 | 41.466 | 9.3462 | 6.7173 | 38.2179 | 41.4969 | 9.1835 | 6.6003 | 38.0341 | 41.5283 | 9.0694 | 6.5184 | 38.0482 | 41.5632 | 8.9261 | 6.4154 | 38.0237 | 41.6339 | 8.7588 | 6.2952 | 37.9247 | 41.7314 | 8.5322 | 6.1323 | 37.7833 | 41.8519 | 8.6377 | 6.2081 | 37.686 | 41.9922 | 8.6072 | 6.1861 | 37.6265 | 42.1539 | 8.4825 | 6.0966 | 37.4257 | 43.1561 | 8.0694 | 5.7997 | 36.5668 | 43.8188 | 7.6962 | 5.5314 | 35.6292 | 44.0013 | 7.7053 | 5.538 | 35.1971 | 43.9433 | 7.6709 | 5.5132 | 35.1454
KINKRY HILL | - | HARKER / HUTTON | 350800 | 575111 | 3.067 | 3.067 | 3.067 | 2.2668 | 3.0803 | 3.0803 | 3.0803 | 2.2222 | 3.1018 | 3.1018 | 3.1018 | 2.1923 | 3.1245 | 3.1245 | 3.1245 | 2.1486 | 3.1384 | 3.1384 | 3.1384 | 2.1141 | 3.1513 | 3.1513 | 3.1513 | 2.0627 | 3.1679 | 3.1679 | 3.1679 | 2.003 | 3.1864 | 3.1864 | 3.1864 | 1.95 | 3.2072 | 3.2072 | 3.2072 | 1.8805 | 3.2311 | 3.2311 | 3.2311 | 1.7945 | 3.3252 | 3.3252 | 3.3252 | 1.5051 | 3.3784 | 3.3784 | 3.3784 | 1.3892 | 3.4007 | 3.4007 | 3.4007 | 1.3667 | 3.4094 | 3.4094 | 3.4094 | 1.455 | 3.0713 | 3.0713 | 3.0713 | 2.2807 | 3.0883 | 3.0883 | 3.0883 | 2.249 | 3.1111 | 3.1111 | 3.1111 | 2.2165 | 3.1319 | 3.1319 | 3.1319 | 2.18 | 3.1433 | 3.1433 | 3.1433 | 2.1426 | 3.1565 | 3.1565 | 3.1565 | 2.0981 | 3.1721 | 3.1721 | 3.1721 | 2.0396 | 3.1893 | 3.1893 | 3.1893 | 1.9799 | 3.2082 | 3.2082 | 3.2082 | 1.916 | 3.2256 | 3.2256 | 3.2256 | 1.8509 | 3.259 | 3.259 | 3.259 | 1.7067 | 3.2854 | 3.2854 | 3.2854 | 1.563 | 3.302 | 3.302 | 3.302 | 1.4356 | 3.3111 | 3.3111 | 3.3111 | 1.368 | 3.067 | 3.067 | 3.067 | 2.2677 | 3.0803 | 3.0803 | 3.0803 | 2.2255 | 3.1018 | 3.1018 | 3.1018 | 2.1979 | 3.1245 | 3.1245 | 3.1245 | 2.1566 | 3.1383 | 3.1383 | 3.1383 | 2.1238 | 3.1512 | 3.1512 | 3.1512 | 2.0744 | 3.1677 | 3.1677 | 3.1677 | 2.0165 | 3.1862 | 3.1862 | 3.1862 | 1.9649 | 3.2066 | 3.2066 | 3.2066 | 1.899 | 3.2293 | 3.2293 | 3.2293 | 1.823 | 3.3173 | 3.3173 | 3.3173 | 1.5707 | 3.3687 | 3.3687 | 3.3687 | 1.4652 | 3.3892 | 3.3892 | 3.3892 | 1.4421 | 3.3975 | 3.3975 | 3.3975 | 1.5072 | 3.0673 | 3.0673 | 3.0673 | 2.268 | 3.0817 | 3.0817 | 3.0817 | 2.2217 | 3.1039 | 3.1039 | 3.1039 | 2.191 | 3.127 | 3.127 | 3.127 | 2.1474 | 3.1507 | 3.1507 | 3.1507 | 2.11 | 3.1714 | 3.1714 | 3.1714 | 2.0551 | 3.1993 | 3.1993 | 3.1993 | 1.9909 | 3.2317 | 3.2317 | 3.2317 | 1.9377 | 3.2685 | 3.2685 | 3.2685 | 1.8781 | 3.3082 | 3.3082 | 3.3082 | 1.8249 | 3.4031 | 3.4031 | 3.4031 | 1.618 | 3.4538 | 3.4538 | 3.4538 | 1.3774 | 3.4403 | 3.4403 | 3.4403 | 1.2831 | 3.389 | 3.389 | 3.389 | 1.2376 | 3.0718 | 3.0718 | 3.0718 | 2.2581 | 3.0915 | 3.0915 | 3.0915 | 2.2007 | 3.1141 | 3.1141 | 3.1141 | 2.1688 | 3.1358 | 3.1358 | 3.1358 | 2.1253 | 3.1538 | 3.1538 | 3.1538 | 2.0831 | 3.1734 | 3.1734 | 3.1734 | 2.0278 | 3.2002 | 3.2002 | 3.2002 | 1.9675 | 3.2301 | 3.2301 | 3.2301 | 1.9213 | 3.2628 | 3.2628 | 3.2628 | 1.87 | 3.2967 | 3.2967 | 3.2967 | 1.817 | 3.3697 | 3.3697 | 3.3697 | 1.6071 | 3.3986 | 3.3986 | 3.3986 | 1.5134 | 3.3678 | 3.3678 | 3.3678 | 1.4931 | 3.3213 | 3.3213 | 3.3213 | 1.5081
KIRKBY LONSDALE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 359833 | 478813 | 13.6053 | 13.6053 | 13.6053 | 5.184 | 13.6651 | 13.6651 | 13.6651 | 5.031 | 13.7322 | 13.7322 | 13.7322 | 4.9289 | 13.8053 | 13.8053 | 13.8053 | 4.7812 | 13.8899 | 13.8899 | 13.8899 | 4.7674 | 13.9623 | 13.9623 | 13.9623 | 4.5322 | 14.0443 | 14.0443 | 14.0443 | 4.3424 | 14.1184 | 14.1184 | 14.1184 | 4.1512 | 14.185 | 14.185 | 14.185 | 3.9078 | 14.2597 | 14.2597 | 14.2597 | 3.581 | 14.5183 | 14.5183 | 14.5183 | 2.4781 | 14.708 | 14.708 | 14.708 | 1.9592 | 14.8159 | 14.8159 | 14.8159 | 1.8459 | 14.8801 | 14.8801 | 14.8801 | 2.0867 | 13.602 | 13.602 | 13.602 | 5.3427 | 13.6617 | 13.6617 | 13.6617 | 5.3101 | 13.7441 | 13.7441 | 13.7441 | 5.1447 | 13.8196 | 13.8196 | 13.8196 | 4.9706 | 13.9034 | 13.9034 | 13.9034 | 4.9394 | 13.9986 | 13.9986 | 13.9986 | 4.7145 | 14.1093 | 14.1093 | 14.1093 | 4.5205 | 14.2294 | 14.2294 | 14.2294 | 4.363 | 14.3396 | 14.3396 | 14.3396 | 4.123 | 14.4456 | 14.4456 | 14.4456 | 3.8656 | 14.5634 | 14.5634 | 14.5634 | 3.1933 | 14.6612 | 14.6612 | 14.6612 | 2.5702 | 14.7288 | 14.7288 | 14.7288 | 2.1473 | 14.7671 | 14.7671 | 14.7671 | 1.916 | 13.6053 | 13.6053 | 13.6053 | 5.1863 | 13.6652 | 13.6652 | 13.6652 | 5.0358 | 13.7323 | 13.7323 | 13.7323 | 4.9495 | 13.8054 | 13.8054 | 13.8054 | 4.7953 | 13.8896 | 13.8896 | 13.8896 | 4.7729 | 13.9619 | 13.9619 | 13.9619 | 4.5425 | 14.0436 | 14.0436 | 14.0436 | 4.3533 | 14.118 | 14.118 | 14.118 | 4.2091 | 14.1838 | 14.1838 | 14.1838 | 3.9784 | 14.2555 | 14.2555 | 14.2555 | 3.6818 | 14.4959 | 14.4959 | 14.4959 | 2.6761 | 14.6602 | 14.6602 | 14.6602 | 2.2216 | 14.7553 | 14.7553 | 14.7553 | 2.1309 | 14.805 | 14.805 | 14.805 | 2.3626 | 13.6045 | 13.6045 | 13.6045 | 5.1954 | 13.6676 | 13.6676 | 13.6676 | 5.0445 | 13.7458 | 13.7458 | 13.7458 | 4.9422 | 13.8409 | 13.8409 | 13.8409 | 4.7909 | 13.936 | 13.936 | 13.936 | 4.7584 | 14.0282 | 14.0282 | 14.0282 | 4.4857 | 14.1113 | 14.1113 | 14.1113 | 4.2256 | 14.2045 | 14.2045 | 14.2045 | 4.0554 | 14.307 | 14.307 | 14.307 | 3.8505 | 14.4205 | 14.4205 | 14.4205 | 3.5874 | 14.7722 | 14.7722 | 14.7722 | 2.6019 | 15.0163 | 15.0163 | 15.0163 | 1.4464 | 15.1178 | 15.1178 | 15.1178 | 0.80436 | 15.1524 | 15.1524 | 15.1473 | 0.40789 | 13.6151 | 13.6151 | 13.6151 | 5.1949 | 13.7007 | 13.7007 | 13.7007 | 5.0354 | 13.7819 | 13.7819 | 13.7819 | 4.9405 | 13.8492 | 13.8492 | 13.8492 | 4.7944 | 13.9202 | 13.9202 | 13.9202 | 4.7299 | 13.9875 | 13.9875 | 13.9875 | 4.4606 | 14.0634 | 14.0634 | 14.0634 | 4.2059 | 14.1432 | 14.1432 | 14.1432 | 4.0668 | 14.2298 | 14.2298 | 14.2298 | 3.8789 | 14.3301 | 14.3301 | 14.3301 | 3.5051 | 14.6512 | 14.6512 | 14.6512 | 1.9766 | 14.8142 | 14.8142 | 14.8142 | 1.0552 | 14.8331 | 14.8331 | 14.8331 | 0.72201 | 14.7835 | 14.7835 | 14.7835 | 1.0272
KIRKBY MOOR | ULVERSTON | HARKER / HUTTON | 326099 | 483011 | 1.9509 | 1.9509 | 1.9509 | 1.9509 | 1.9728 | 1.9728 | 1.9728 | 1.9728 | 2.0176 | 2.0176 | 2.0176 | 2.0176 | 2.0559 | 2.0559 | 2.0559 | 2.0559 | 2.0822 | 2.0822 | 2.0822 | 2.0822 | 2.1108 | 2.1108 | 2.1108 | 2.1108 | 2.1458 | 2.1458 | 2.1458 | 2.1458 | 2.1845 | 2.1845 | 2.1845 | 2.1845 | 2.227 | 2.227 | 2.227 | 2.227 | 2.28 | 2.28 | 2.28 | 2.28 | 2.4832 | 2.4832 | 2.4832 | 2.4832 | 2.6175 | 2.6175 | 2.6175 | 2.6175 | 2.6964 | 2.6964 | 2.6964 | 2.6964 | 2.7554 | 2.7554 | 2.7554 | 2.7554 | 1.9579 | 1.9579 | 1.9579 | 1.9579 | 1.9833 | 1.9833 | 1.9833 | 1.9833 | 2.0209 | 2.0209 | 2.0209 | 2.0209 | 2.0514 | 2.0514 | 2.0514 | 2.0514 | 2.0777 | 2.0777 | 2.0777 | 2.0777 | 2.0997 | 2.0997 | 2.0997 | 2.0997 | 2.1256 | 2.1256 | 2.1256 | 2.1256 | 2.154 | 2.154 | 2.154 | 2.154 | 2.1848 | 2.1848 | 2.1848 | 2.1848 | 2.2178 | 2.2178 | 2.2178 | 2.2178 | 2.3028 | 2.3028 | 2.3028 | 2.3028 | 2.3863 | 2.3863 | 2.3863 | 2.3863 | 2.4566 | 2.4566 | 2.4566 | 2.4566 | 2.5117 | 2.5117 | 2.5117 | 2.5117 | 1.9509 | 1.9509 | 1.9509 | 1.9509 | 1.9728 | 1.9728 | 1.9728 | 1.9728 | 2.0177 | 2.0177 | 2.0177 | 2.0177 | 2.056 | 2.056 | 2.056 | 2.056 | 2.0823 | 2.0823 | 2.0823 | 2.0823 | 2.1107 | 2.1107 | 2.1107 | 2.1107 | 2.1456 | 2.1456 | 2.1456 | 2.1456 | 2.1842 | 2.1842 | 2.1842 | 2.1842 | 2.2261 | 2.2261 | 2.2261 | 2.2261 | 2.2766 | 2.2766 | 2.2766 | 2.2766 | 2.465 | 2.465 | 2.465 | 2.465 | 2.5779 | 2.5779 | 2.5779 | 2.5779 | 2.6464 | 2.6464 | 2.6464 | 2.6464 | 2.6926 | 2.6926 | 2.6926 | 2.6926 | 1.9521 | 1.9521 | 1.9521 | 1.9521 | 1.977 | 1.977 | 1.977 | 1.977 | 2.0238 | 2.0238 | 2.0238 | 2.0238 | 2.068 | 2.068 | 2.068 | 2.068 | 2.1124 | 2.1124 | 2.1124 | 2.1124 | 2.1621 | 2.1621 | 2.1621 | 2.1621 | 2.2228 | 2.2228 | 2.2228 | 2.2228 | 2.2843 | 2.2843 | 2.2843 | 2.2843 | 2.3521 | 2.3521 | 2.3521 | 2.3521 | 2.4294 | 2.4294 | 2.4294 | 2.4294 | 2.6898 | 2.6898 | 2.6898 | 2.6898 | 2.8776 | 2.8776 | 2.8776 | 2.8776 | 2.9701 | 2.9701 | 2.9701 | 2.9701 | 3.0142 | 3.0142 | 3.0142 | 3.0142 | 1.9641 | 1.9641 | 1.9641 | 1.9641 | 2.0045 | 2.0045 | 2.0045 | 2.0045 | 2.0513 | 2.0513 | 2.0513 | 2.0513 | 2.0841 | 2.0841 | 2.0841 | 2.0841 | 2.1261 | 2.1261 | 2.1261 | 2.1261 | 2.1755 | 2.1755 | 2.1755 | 2.1755 | 2.2258 | 2.2258 | 2.2258 | 2.2258 | 2.2819 | 2.2819 | 2.2819 | 2.2819 | 2.3442 | 2.3442 | 2.3442 | 2.3442 | 2.4168 | 2.4168 | 2.4168 | 2.4168 | 2.6509 | 2.6509 | 2.6509 | 2.6509 | 2.7813 | 2.7813 | 2.7813 | 2.7813 | 2.8145 | 2.8145 | 2.8145 | 2.8145 | 2.804 | 2.804 | 2.804 | 2.804
KIRKBY STEPHEN | PENRITH & SHAP | HARKER / HUTTON | 376579 | 509136 | 17.7122 | 17.7122 | 17.7122 | 11.064 | 17.7558 | 17.7558 | 17.7558 | 10.7919 | 17.8274 | 17.8274 | 17.8274 | 10.687 | 17.8739 | 17.8739 | 17.8739 | 10.4703 | 17.9221 | 17.9221 | 17.9221 | 10.3586 | 17.9784 | 17.9784 | 17.9784 | 10.1468 | 18.0491 | 18.0491 | 18.0491 | 9.9089 | 18.1286 | 18.1286 | 18.1286 | 9.7129 | 18.2186 | 18.2186 | 18.2186 | 9.4471 | 18.3176 | 18.3176 | 18.3176 | 9.0205 | 18.7518 | 18.7518 | 18.7518 | 7.3781 | 19.2274 | 19.2274 | 19.2274 | 6.3292 | 19.5375 | 19.5375 | 19.5375 | 5.694 | 19.7978 | 19.7978 | 19.7978 | 5.7727 | 17.7357 | 17.7357 | 17.7357 | 11.1242 | 17.7996 | 17.7996 | 17.7996 | 10.9122 | 17.882 | 17.882 | 17.882 | 10.7802 | 17.9354 | 17.9354 | 17.9354 | 10.5953 | 17.987 | 17.987 | 17.987 | 10.4898 | 18.0478 | 18.0478 | 18.0478 | 10.2733 | 18.1206 | 18.1206 | 18.1206 | 10.0232 | 18.1949 | 18.1949 | 18.1949 | 9.8266 | 18.2682 | 18.2682 | 18.2682 | 9.5774 | 18.3486 | 18.3486 | 18.3486 | 9.303 | 18.6026 | 18.6026 | 18.6026 | 8.5405 | 18.9309 | 18.9309 | 18.9309 | 7.3787 | 19.2171 | 19.2171 | 19.2171 | 6.3421 | 19.4211 | 19.4211 | 19.4211 | 5.6208 | 17.7147 | 17.7147 | 17.7147 | 11.065 | 17.7593 | 17.7593 | 17.7593 | 10.8193 | 17.8303 | 17.8303 | 17.8303 | 10.7306 | 17.8767 | 17.8767 | 17.8767 | 10.5352 | 17.925 | 17.925 | 17.925 | 10.4042 | 17.9807 | 17.9807 | 17.9807 | 10.2086 | 18.0501 | 18.0501 | 18.0501 | 9.985 | 18.1278 | 18.1278 | 18.1278 | 9.7853 | 18.2147 | 18.2147 | 18.2147 | 9.5383 | 18.3102 | 18.3102 | 18.3102 | 9.1569 | 18.6968 | 18.6968 | 18.6968 | 7.685 | 19.0411 | 19.0411 | 19.0411 | 6.8059 | 19.2934 | 19.2934 | 19.2934 | 6.2803 | 19.4539 | 19.4539 | 19.4539 | 6.4055 | 17.718 | 17.718 | 17.718 | 11.0628 | 17.7703 | 17.7703 | 17.7703 | 10.7587 | 17.8499 | 17.8499 | 17.8499 | 10.6171 | 17.9066 | 17.9066 | 17.9066 | 10.3609 | 17.976 | 17.976 | 17.976 | 10.1774 | 18.0665 | 18.0665 | 18.0665 | 9.8585 | 18.1864 | 18.1864 | 18.1864 | 9.4766 | 18.3083 | 18.3083 | 18.3083 | 9.1678 | 18.4459 | 18.4459 | 18.4459 | 8.829 | 18.6011 | 18.6011 | 18.6011 | 8.4803 | 19.3008 | 19.3008 | 19.3008 | 6.8119 | 19.9418 | 19.9418 | 19.9418 | 5.0432 | 20.3356 | 20.3356 | 20.3356 | 4.1167 | 20.5232 | 20.5232 | 20.5232 | 3.5768 | 17.7374 | 17.7374 | 17.7374 | 11.0402 | 17.7944 | 17.7944 | 17.7944 | 10.7139 | 17.85 | 17.85 | 17.85 | 10.5792 | 17.9084 | 17.9084 | 17.9084 | 10.32 | 17.9789 | 17.9789 | 17.9789 | 10.0921 | 18.0712 | 18.0712 | 18.0712 | 9.7567 | 18.1822 | 18.1822 | 18.1822 | 9.3924 | 18.3118 | 18.3118 | 18.3118 | 9.0884 | 18.459 | 18.459 | 18.459 | 8.7667 | 18.6292 | 18.6292 | 18.6292 | 8.2355 | 19.3267 | 19.3267 | 19.3267 | 5.8183 | 19.8611 | 19.8611 | 19.8611 | 4.2951 | 20.1172 | 20.1172 | 20.1172 | 3.7174 | 20.086 | 20.086 | 20.086 | 3.9865
KIRKBY THORE | PENRITH & SHAP | HARKER / HUTTON | 364439 | 526672 | 29.9295 | 26.3299 | 18.9238 | 17.1869 | 29.9943 | 26.2014 | 18.8315 | 16.9937 | 30.0457 | 26.1065 | 18.7632 | 16.9284 | 30.118 | 26.057 | 18.7276 | 16.738 | 30.2057 | 26.0085 | 18.6928 | 16.5711 | 30.3069 | 25.9992 | 18.6861 | 16.4229 | 30.4088 | 25.9463 | 18.6481 | 16.1685 | 30.4824 | 25.8847 | 18.6039 | 15.9863 | 30.5688 | 25.8059 | 18.5472 | 15.7753 | 30.7022 | 25.7164 | 18.4829 | 15.5381 | 31.3012 | 25.3452 | 18.2161 | 14.5547 | 31.6879 | 25.1017 | 18.0411 | 14.1101 | 31.8951 | 24.9374 | 17.923 | 13.9585 | 32.1488 | 24.8173 | 17.8367 | 14.0797 | 29.9056 | 26.3797 | 18.9596 | 17.397 | 29.9446 | 26.3261 | 18.9211 | 17.3704 | 30.0124 | 26.2395 | 18.8589 | 17.2134 | 30.0876 | 26.1423 | 18.789 | 16.9793 | 30.1693 | 26.0492 | 18.722 | 16.7806 | 30.2246 | 25.9331 | 18.6387 | 16.6141 | 30.2865 | 25.8539 | 18.5817 | 16.3354 | 30.3508 | 25.7904 | 18.5361 | 16.1204 | 30.417 | 25.7131 | 18.4805 | 15.8733 | 30.4854 | 25.6394 | 18.4276 | 15.6509 | 30.8011 | 25.5782 | 18.3836 | 14.9854 | 31.282 | 25.4592 | 18.298 | 14.4503 | 31.5229 | 25.3367 | 18.21 | 14.0324 | 31.6658 | 25.2299 | 18.1333 | 13.8921 | 29.9296 | 26.379 | 18.9591 | 17.1922 | 29.9946 | 26.3277 | 18.9222 | 17.0039 | 30.0463 | 26.2449 | 18.8627 | 16.9444 | 30.1188 | 26.1542 | 18.7975 | 16.7607 | 30.2066 | 26.069 | 18.7363 | 16.6008 | 30.3074 | 25.9865 | 18.677 | 16.4597 | 30.4108 | 25.8991 | 18.6142 | 16.2137 | 30.4846 | 25.8213 | 18.5583 | 16.039 | 30.5707 | 25.7355 | 18.4966 | 15.8387 | 30.7012 | 25.653 | 18.4373 | 15.6213 | 31.2375 | 25.3799 | 18.2411 | 14.7034 | 31.5086 | 25.134 | 18.0643 | 14.3507 | 31.6628 | 24.9163 | 17.9079 | 14.2335 | 31.8239 | 24.7241 | 17.7697 | 14.4113 | 29.9266 | 26.3347 | 18.9272 | 17.2075 | 29.9878 | 26.2325 | 18.8538 | 17.0295 | 30.0337 | 26.2144 | 18.8408 | 16.9832 | 30.1036 | 26.1379 | 18.7858 | 16.8117 | 30.1899 | 26.0602 | 18.73 | 16.6557 | 30.2935 | 25.9918 | 18.6808 | 16.5166 | 30.4146 | 25.899 | 18.6141 | 16.2638 | 30.5427 | 25.8074 | 18.5483 | 16.0875 | 30.6727 | 25.7074 | 18.4764 | 15.9106 | 30.8072 | 25.6069 | 18.4042 | 15.7633 | 31.4692 | 25.1369 | 18.0664 | 14.8615 | 32.4826 | 24.5932 | 17.6756 | 13.4675 | 32.8088 | 24.2607 | 17.4366 | 12.8385 | 32.9921 | 24.0381 | 17.2766 | 12.5737 | 29.9277 | 26.335 | 18.9275 | 17.2057 | 29.9976 | 26.3144 | 18.9127 | 17.0164 | 30.044 | 26.2963 | 18.8997 | 16.9724 | 30.104 | 26.242 | 18.8606 | 16.8126 | 30.1801 | 26.1685 | 18.8078 | 16.6588 | 30.2727 | 26.0824 | 18.7459 | 16.5325 | 30.3894 | 25.97 | 18.6652 | 16.2984 | 31.0095 | 25.7874 | 18.5339 | 15.6454 | 31.1057 | 25.6923 | 18.4656 | 15.5181 | 31.2423 | 25.5708 | 18.3782 | 15.2867 | 31.9225 | 25.0182 | 17.9811 | 13.958 | 32.5126 | 24.5094 | 17.6154 | 12.8493 | 32.6677 | 24.2757 | 17.4474 | 12.5407 | 32.5807 | 24.2349 | 17.4181 | 13.0605
KIRKHALL LANE | ATHERTON | KEARSLEY | 365510 | 401069 | 20.6878 | 11.8491 | 8.5162 | 8.5595 | 20.7259 | 11.7225 | 8.4252 | 8.1254 | 20.7749 | 11.6025 | 8.3389 | 8.1738 | 20.8559 | 11.4652 | 8.2403 | 7.7356 | 20.9641 | 11.3491 | 8.1568 | 7.6204 | 21.0928 | 11.1825 | 8.0371 | 7.2245 | 21.242 | 11.0394 | 7.9343 | 6.8714 | 21.4071 | 10.8122 | 7.771 | 6.4816 | 21.5855 | 10.797 | 7.76 | 6.0932 | 21.782 | 10.6387 | 7.6462 | 5.5908 | 22.4031 | 10.0333 | 7.2112 | 4.0402 | 22.8329 | 9.536 | 6.8537 | 3.326 | 23.082 | 10.1639 | 7.305 | 3.1523 | 23.1888 | 10.0586 | 7.2293 | 3.3876 | 20.6754 | 11.8215 | 8.4964 | 8.621 | 20.7051 | 11.6912 | 8.4027 | 8.2412 | 20.7606 | 11.6402 | 8.366 | 8.2443 | 20.8291 | 11.4862 | 8.2554 | 7.8329 | 20.9079 | 11.4224 | 8.2095 | 7.8116 | 20.9962 | 11.2952 | 8.1181 | 7.4383 | 21.0945 | 11.2205 | 8.0644 | 7.1758 | 21.1994 | 11.1309 | 8 | 6.8566 | 21.31 | 11.0544 | 7.945 | 6.529 | 21.4236 | 10.9641 | 7.8801 | 6.1444 | 21.7589 | 10.5942 | 7.6142 | 5.0488 | 22.0004 | 10.3739 | 7.456 | 4.3075 | 22.1333 | 10.6534 | 7.6568 | 3.8395 | 22.2189 | 10.9704 | 7.8846 | 3.6244 | 20.6878 | 11.8072 | 8.486 | 8.5744 | 20.7259 | 11.7413 | 8.4387 | 8.1511 | 20.7749 | 11.6352 | 8.3624 | 8.218 | 20.8559 | 11.3691 | 8.1712 | 7.7857 | 20.9636 | 11.3212 | 8.1368 | 7.6041 | 21.0913 | 11.0927 | 7.9726 | 7.2467 | 21.2397 | 10.871 | 7.8132 | 6.9039 | 21.4042 | 10.8821 | 7.8212 | 6.5226 | 21.5798 | 10.7926 | 7.7569 | 6.1287 | 21.7648 | 10.6498 | 7.6542 | 5.6872 | 22.3544 | 10.2384 | 7.3586 | 4.2764 | 22.7515 | 9.939 | 7.1433 | 3.6454 | 22.9967 | 10.3753 | 7.4569 | 3.4936 | 23.1174 | 10.2014 | 7.332 | 3.7078 | 20.6863 | 11.8497 | 8.5166 | 8.5638 | 20.7279 | 11.7196 | 8.4231 | 8.1344 | 20.7946 | 11.592 | 8.3314 | 8.189 | 20.9096 | 11.4455 | 8.2261 | 7.7534 | 21.0711 | 11.3224 | 8.1376 | 7.7229 | 21.273 | 11.1376 | 8.0048 | 7.3272 | 21.5202 | 10.9537 | 7.8727 | 6.9987 | 21.7913 | 10.8671 | 7.8104 | 6.6385 | 22.0309 | 10.6877 | 7.6815 | 6.3364 | 22.283 | 10.4589 | 7.517 | 5.9775 | 23.0112 | 9.6691 | 6.9493 | 4.0003 | 23.459 | 8.5072 | 6.1143 | -0.13729 | 23.693 | 8.2549 | 5.9329 | -3.5514 | 23.8088 | 7.6083 | 5.4682 | -5.8074 | 20.6807 | 11.8561 | 8.5212 | 8.5907 | 20.735 | 11.7437 | 8.4405 | 8.1563 | 20.8161 | 11.7391 | 8.4371 | 8.2112 | 20.9334 | 11.5403 | 8.2942 | 7.8109 | 21.095 | 11.449 | 8.2286 | 7.7587 | 21.2852 | 11.1132 | 7.9873 | 7.4098 | 21.5232 | 11.1177 | 7.9905 | 7.1338 | 21.762 | 11.036 | 7.9318 | 6.8402 | 21.976 | 10.9087 | 7.8403 | 6.4796 | 22.2352 | 10.6227 | 7.6348 | 5.4116 | 22.9492 | 9.9265 | 7.1343 | 0.70306 | 23.2646 | 8.7667 | 6.3008 | -3.031 | 23.3427 | 8.162 | 5.8662 | -5.2917 | 23.2346 | 8.093 | 5.8166 | -4.5904
KITT GREEN | ORRELL | WASHWAY FARM / KIRKBY | 354934 | 405497 | 31.9631 | 12.9658 | 9.4584 | 11.4102 | 32.0528 | 12.8237 | 9.3547 | 10.8188 | 32.0573 | 12.7686 | 9.3145 | 10.7556 | 32.0913 | 12.6773 | 9.2479 | 10.6753 | 32.1434 | 12.5603 | 9.1626 | 10.5389 | 32.2138 | 12.4112 | 9.0538 | 10.3333 | 32.2894 | 12.2063 | 8.9044 | 10.1287 | 32.369 | 12.1716 | 8.879 | 9.953 | 32.4517 | 12.1656 | 8.8746 | 9.742 | 32.5485 | 12.1067 | 8.8316 | 9.5 | 41.1609 | 10.4319 | 7.6099 | 0.61427 | 42.8067 | 10.0703 | 7.3461 | -0.87259 | 43.8115 | 10.0155 | 7.3062 | -1.6886 | 44.4282 | 10.0351 | 7.3204 | -1.9338 | 31.8698 | 13.0632 | 9.5294 | 11.9004 | 31.8805 | 12.9846 | 9.4721 | 11.7581 | 31.9202 | 12.8689 | 9.3876 | 11.5922 | 31.968 | 12.7329 | 9.2885 | 11.4229 | 32.0267 | 12.552 | 9.1565 | 11.2236 | 32.0907 | 12.4996 | 9.1183 | 10.9999 | 32.1604 | 12.5287 | 9.1395 | 10.7515 | 32.2327 | 12.4972 | 9.1165 | 10.5312 | 32.3076 | 12.4384 | 9.0737 | 10.2851 | 32.3829 | 12.3737 | 9.0264 | 10.031 | 32.907 | 12.1287 | 8.8477 | 9.1701 | 33.5726 | 11.981 | 8.74 | 8.4494 | 34.2537 | 11.9713 | 8.7329 | 7.8794 | 34.8298 | 11.9317 | 8.704 | 7.4823 | 31.9636 | 13.06 | 9.5271 | 11.3966 | 32.0539 | 12.9636 | 9.4568 | 10.8333 | 32.0598 | 12.6861 | 9.2543 | 10.77 | 32.0955 | 12.7304 | 9.2866 | 10.6921 | 32.1493 | 12.6797 | 9.2497 | 10.5436 | 32.2214 | 12.5915 | 9.1853 | 10.3571 | 32.2985 | 12.4979 | 9.1171 | 10.172 | 32.3797 | 12.3939 | 9.0412 | 9.976 | 32.4633 | 12.3176 | 8.9855 | 9.7713 | 32.5585 | 12.2246 | 8.9177 | 9.5515 | 41.0339 | 11.833 | 8.632 | 0.80454 | 42.1915 | 11.6028 | 8.4641 | -0.26961 | 42.9534 | 11.6199 | 8.4766 | -0.87349 | 43.1044 | 11.6171 | 8.4745 | -0.75382 | 31.9584 | 12.9704 | 9.4617 | 11.4452 | 32.0481 | 12.8332 | 9.3617 | 10.8957 | 32.0623 | 12.7616 | 9.3094 | 10.8707 | 32.1149 | 12.6459 | 9.225 | 10.8203 | 32.1925 | 12.4874 | 9.1094 | 10.6775 | 32.3211 | 12.2297 | 8.9214 | 10.4364 | 32.4914 | 12.2781 | 8.9567 | 10.1748 | 32.6964 | 12.2048 | 8.9032 | 9.9037 | 32.8907 | 12.1026 | 8.8287 | 9.6527 | 33.1031 | 11.9805 | 8.7396 | 9.3896 | 43.1961 | 9.8896 | 7.2143 | -1.1344 | 48.2407 | 8.532 | 6.2239 | -7.6864 | 49.5388 | 8.0783 | 5.893 | -10.1922 | 49.2685 | 7.9918 | 5.8299 | -10.9562 | 31.9589 | 12.9718 | 9.4628 | 11.4445 | 32.0557 | 12.8662 | 9.3857 | 10.8846 | 32.0814 | 12.7948 | 9.3336 | 10.8533 | 32.1455 | 12.5759 | 9.1739 | 10.8056 | 32.2395 | 12.5755 | 9.1737 | 10.6889 | 32.4063 | 12.5419 | 9.1492 | 10.479 | 32.6381 | 12.4415 | 9.0759 | 10.1869 | 32.9238 | 12.3286 | 8.9935 | 9.8344 | 33.2232 | 12.2099 | 8.9069 | 9.4591 | 43.2865 | 10.4353 | 7.6124 | -1.0319 | 43.9876 | 9.8266 | 7.1684 | -3.5665 | 45.3878 | 9.0156 | 6.5768 | -6.3685 | 46.1069 | 8.7541 | 6.386 | -8.0013 | 45.6644 | 8.811 | 6.4275 | -7.123
KNOTT MILL | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 32.5902 | 6.1404 | 4.4794 | 7.9637 | 32.7192 | 5.9835 | 4.3649 | 6.8273 | 32.7097 | 5.9627 | 4.3497 | 6.68 | 32.7537 | 5.8698 | 4.282 | 6.5159 | 32.8226 | 5.8632 | 4.2771 | 6.2902 | 32.9183 | 5.7702 | 4.2092 | 5.9993 | 33.0148 | 5.668 | 4.1347 | 5.6188 | 33.1111 | 5.5475 | 4.0468 | 5.3228 | 33.2071 | 5.4626 | 3.9849 | 5.1882 | 32.9432 | 5.3437 | 3.8982 | 4.872 | 29.5742 | 4.7972 | 3.4995 | 3.6412 | 26.5927 | 4.3136 | 3.1467 | 2.8812 | 31.5286 | 5.1142 | 3.7308 | 2.5366 | 33.9044 | 5.8442 | 4.2632 | 2.5412 | 32.4603 | 6.5542 | 4.7812 | 8.5811 | 32.4891 | 6.4381 | 4.6965 | 8.0079 | 32.5625 | 6.3706 | 4.6473 | 7.8165 | 32.6746 | 6.2593 | 4.5661 | 7.5675 | 32.8018 | 6.2109 | 4.5307 | 7.2776 | 32.9416 | 6.1246 | 4.4678 | 6.9402 | 33.093 | 6.0209 | 4.3921 | 6.4922 | 33.2533 | 5.9345 | 4.3291 | 6.1108 | 33.4237 | 5.8572 | 4.2727 | 5.8663 | 33.59 | 5.7481 | 4.1931 | 5.4891 | 33.8563 | 5.5201 | 4.0268 | 4.5295 | 32.9777 | 5.3493 | 3.9022 | 3.7712 | 34.1346 | 5.8748 | 4.2856 | 3.3134 | 34.148 | 6.465 | 4.7161 | 3.047 | 32.5902 | 6.5528 | 4.7801 | 7.9722 | 32.7192 | 6.4254 | 4.6872 | 6.8565 | 32.7097 | 6.3388 | 4.6241 | 6.7277 | 32.7537 | 6.2371 | 4.5499 | 6.5793 | 32.8224 | 6.1368 | 4.4767 | 6.3691 | 32.9179 | 6.0228 | 4.3935 | 6.0928 | 33.0142 | 5.8931 | 4.299 | 5.7276 | 33.1104 | 5.7929 | 4.2259 | 5.4457 | 33.2057 | 5.7065 | 4.1628 | 5.3265 | 33.3045 | 5.6065 | 4.0899 | 5.0376 | 32.1786 | 5.2197 | 3.8077 | 3.8969 | 30.5421 | 4.9542 | 3.614 | 3.1729 | 33.877 | 5.5085 | 4.0184 | 2.858 | 33.8783 | 6.1878 | 4.5139 | 2.8493 | 32.5775 | 6.147 | 4.4841 | 7.9963 | 32.6944 | 5.9462 | 4.3376 | 6.8892 | 32.6757 | 5.9671 | 4.3529 | 6.7732 | 32.7164 | 5.9132 | 4.3136 | 6.6324 | 32.787 | 5.872 | 4.2836 | 6.4151 | 32.8902 | 5.7605 | 4.2022 | 6.1205 | 33.0007 | 5.6437 | 4.117 | 5.7118 | 33.1156 | 5.5213 | 4.0277 | 5.3785 | 33.2335 | 5.4225 | 3.9557 | 5.2455 | 32.6921 | 5.303 | 3.8685 | 4.9649 | 28.5294 | 4.6277 | 3.3759 | 3.4247 | 22.6383 | 3.6722 | 2.6788 | 0.32319 | 24.7285 | 4.0112 | 2.9261 | -1.9933 | 27.0922 | 4.3946 | 3.2058 | -3.7238 | 32.5652 | 6.1545 | 4.4896 | 8.0067 | 32.6701 | 6.1059 | 4.4542 | 6.9217 | 32.6364 | 6.0829 | 4.4374 | 6.8459 | 32.6565 | 6.025 | 4.3951 | 6.7608 | 32.7065 | 5.8818 | 4.2907 | 6.5895 | 32.7858 | 5.7838 | 4.2192 | 6.3522 | 32.8729 | 5.637 | 4.1121 | 6.0069 | 32.9608 | 5.5129 | 4.0215 | 5.7417 | 33.0504 | 5.41 | 3.9465 | 5.6552 | 32.0255 | 5.1949 | 3.7896 | 4.9231 | 24.8686 | 4.0339 | 2.9427 | 1.3826 | 20.7826 | 3.3711 | 2.4592 | -1.4134 | 27.2814 | 4.4253 | 3.2282 | -2.9903 | 27.1463 | 4.4034 | 3.2122 | -2.5338
LAMBERHEAD | ORRELL | WASHWAY FARM / KIRKBY | 355516 | 404030 | 23.5401 | 10.0419 | 7.3254 | 15.7981 | 23.5951 | 9.8801 | 7.2074 | 15.1836 | 23.6338 | 9.7655 | 7.1238 | 14.8082 | 23.6944 | 9.6252 | 7.0214 | 14.4528 | 23.7766 | 9.532 | 6.9535 | 13.9981 | 23.876 | 9.3817 | 6.8438 | 13.4973 | 23.9897 | 9.2559 | 6.7521 | 12.9557 | 24.1114 | 9.094 | 6.634 | 12.4281 | 24.2417 | 8.886 | 6.4822 | 11.8859 | 24.3845 | 8.7314 | 6.3694 | 11.3035 | 24.981 | 8.5495 | 6.2367 | 9.2406 | 25.4579 | 10.2401 | 7.47 | 8.2903 | 25.7657 | 13.4211 | 9.7905 | 8.1807 | 26.0014 | 14.1521 | 10.3238 | 8.4497 | 23.5117 | 10.1321 | 7.3912 | 16.1178 | 23.5449 | 10.0435 | 7.3266 | 15.7931 | 23.6028 | 9.9563 | 7.263 | 15.4313 | 23.6696 | 9.8487 | 7.1845 | 15.1074 | 23.7467 | 9.7641 | 7.1228 | 14.7319 | 23.8329 | 9.6489 | 7.0387 | 14.3242 | 23.9292 | 9.5105 | 6.9378 | 13.8796 | 24.0316 | 9.3518 | 6.822 | 13.4424 | 24.141 | 9.2299 | 6.7331 | 12.9836 | 24.2559 | 9.198 | 6.7098 | 12.5344 | 24.517 | 9.2101 | 6.7187 | 11.164 | 24.7275 | 10.3617 | 7.5587 | 10.3371 | 24.8854 | 12.201 | 8.9005 | 9.979 | 24.9981 | 12.758 | 9.3068 | 9.8754 | 23.5401 | 10.1285 | 7.3886 | 15.8021 | 23.5952 | 10.0427 | 7.326 | 15.192 | 23.634 | 9.9165 | 7.2339 | 14.8208 | 23.6948 | 9.8249 | 7.1671 | 14.4701 | 23.7767 | 9.647 | 7.0374 | 14.0228 | 23.8756 | 9.4915 | 6.9239 | 13.5311 | 23.9889 | 9.4751 | 6.912 | 12.9981 | 24.1103 | 9.4071 | 6.8623 | 12.4779 | 24.2388 | 9.3022 | 6.7858 | 11.9514 | 24.3738 | 9.1963 | 6.7086 | 11.415 | 24.9233 | 8.9502 | 6.529 | 9.5067 | 25.3304 | 10.7664 | 7.8539 | 8.6651 | 25.6019 | 13.8383 | 10.0949 | 8.5783 | 25.794 | 14.4553 | 10.5449 | 8.8478 | 23.5382 | 10.0425 | 7.3259 | 15.817 | 23.595 | 9.88 | 7.2073 | 15.2269 | 23.6451 | 9.7507 | 7.113 | 14.8846 | 23.727 | 9.6504 | 7.0398 | 14.5699 | 23.8421 | 9.5095 | 6.9371 | 14.1816 | 23.9892 | 9.3738 | 6.8381 | 13.7601 | 24.1686 | 9.1518 | 6.6761 | 13.3014 | 24.3707 | 9.0213 | 6.5809 | 12.8662 | 24.5944 | 8.9759 | 6.5478 | 12.4651 | 24.8431 | 8.8686 | 6.4695 | 12.0765 | 25.7482 | 8.2112 | 5.9899 | 9.6077 | 26.5631 | 9.148 | 6.6733 | 4.6332 | 27.0574 | 11.5536 | 8.4282 | 0.83973 | 27.3349 | 11.7742 | 8.5891 | -1.6451 | 23.5421 | 10.0253 | 7.3133 | 15.7324 | 23.6086 | 9.8837 | 7.21 | 15.0569 | 23.6634 | 9.7471 | 7.1103 | 14.6926 | 23.7439 | 9.6754 | 7.0581 | 14.3912 | 23.8568 | 9.5636 | 6.9765 | 14.0215 | 23.9959 | 9.3517 | 6.8219 | 13.6497 | 24.1708 | 9.2454 | 6.7444 | 13.2351 | 24.3603 | 9.3195 | 6.7984 | 12.8691 | 24.575 | 9.3789 | 6.8418 | 12.4288 | 24.8477 | 9.3084 | 6.7904 | 11.4924 | 25.7982 | 13.958 | 10.1822 | 5.8501 | 26.4076 | 12.8252 | 9.3558 | 1.5201 | 26.6423 | 12.3291 | 8.9939 | -0.83462 | 26.5847 | 12.2881 | 8.964 | -0.048748
LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 25.4795 | 4.195 | 3.015 | 7.5951 | 25.007 | 4.1172 | 2.9591 | 7.6275 | 22.2577 | 3.6646 | 2.6338 | 7.3433 | 19.5939 | 3.226 | 2.3186 | 6.9475 | 17.0592 | 2.8087 | 2.0186 | 4.6405 | 15.6972 | 2.5844 | 1.8575 | 4.3875 | 14.0035 | 2.3056 | 1.6571 | 3.8412 | 12.762 | 2.1012 | 1.5101 | 2.9177 | 12.1686 | 2.0035 | 1.4399 | 2.6828 | 11.0991 | 1.8274 | 1.3134 | 2.0363 | 8.0783 | 1.33 | 0.95592 | -0.71772 | 14.2005 | 2.338 | 1.6804 | -3.2263 | 28.7213 | 4.7287 | 3.3986 | -4.8422 | 32.8896 | 5.8185 | 4.1818 | -2.4079 | 26.3223 | 4.3338 | 3.1148 | 7.9973 | 26.4638 | 4.3571 | 3.1315 | 8.3573 | 25.8868 | 4.2621 | 3.0632 | 7.973 | 25.3143 | 4.1678 | 2.9955 | 7.567 | 24.4786 | 4.0302 | 2.8966 | 6.883 | 23.9453 | 3.9424 | 2.8335 | 6.5865 | 23.1777 | 3.816 | 2.7427 | 6.0138 | 22.0809 | 3.6355 | 2.6129 | 5.0967 | 21.5664 | 3.5507 | 2.552 | 4.8073 | 20.7683 | 3.4193 | 2.4576 | 4.2329 | 18.8771 | 3.108 | 2.2338 | 2.097 | 22.6463 | 3.7285 | 2.6798 | 0.48405 | 29.7289 | 5.1296 | 3.6868 | -1.8113 | 30.0194 | 5.8986 | 4.2394 | -0.34525 | 26.314 | 4.3324 | 3.1138 | 7.6112 | 26.4022 | 4.3469 | 3.1242 | 7.6609 | 25.6726 | 4.2268 | 3.0379 | 7.3977 | 24.8164 | 4.0858 | 2.9366 | 7.0154 | 23.7219 | 3.9056 | 2.8071 | 4.7274 | 22.8951 | 3.7695 | 2.7092 | 4.4902 | 21.88 | 3.6024 | 2.5891 | 3.9606 | 20.5874 | 3.3896 | 2.4361 | 3.0561 | 20.1677 | 3.3205 | 2.3865 | 2.8446 | 19.3716 | 3.1894 | 2.2923 | 2.2607 | 17.2845 | 2.8458 | 2.0453 | -0.22951 | 24.4883 | 4.0318 | 2.8977 | -2.4611 | 32.0517 | 6.3085 | 4.534 | -3.9196 | 32.2549 | 7.2482 | 5.2094 | -1.3757 | 25.4966 | 4.1978 | 3.0171 | 7.6285 | 24.9882 | 4.1141 | 2.9569 | 7.6956 | 22.1624 | 3.6489 | 2.6225 | 7.4594 | 20.0343 | 3.2985 | 2.3707 | 7.1132 | 17.1422 | 2.8223 | 2.0285 | 4.9411 | 15.7777 | 2.5977 | 1.867 | 4.7598 | 14.069 | 2.3164 | 1.6648 | 4.2707 | 11.7305 | 1.9313 | 1.3881 | 2.2691 | 11.2398 | 1.8506 | 1.33 | 2.2523 | 10.3508 | 1.7042 | 1.2248 | 1.9172 | 6.3782 | 1.0501 | 0.75474 | -0.97711 | 7.9754 | 1.3131 | 0.94374 | -6.8641 | 18.3793 | 3.026 | 2.1748 | -11.5344 | 22.8739 | 3.766 | 2.7067 | -10.7639 | 25.4802 | 4.1951 | 3.0151 | 7.5988 | 24.9218 | 4.1032 | 2.949 | 7.61 | 22.0564 | 3.6314 | 2.61 | 7.3733 | 20.1054 | 3.3102 | 2.3791 | 7.0669 | 18.4146 | 3.0318 | 2.179 | 6.4402 | 14.398 | 2.3705 | 1.7037 | 3.5168 | 12.7206 | 2.0943 | 1.5052 | 3.1775 | 12.066 | 1.9866 | 1.4278 | 2.4705 | 12.256 | 2.0179 | 1.4503 | 2.442 | 11.6506 | 1.9182 | 1.3786 | 1.3937 | 31.147 | 5.1281 | 3.6857 | -4.6061 | 24.3967 | 4.0167 | 2.8869 | -8.9274 | 22.5598 | 3.7143 | 2.6695 | -12.4692 | 25.3933 | 4.1808 | 3.0048 | -8.5818
LANGLEY | CHADDERTON | WHITEGATE | 386421 | 406330 | 31.5813 | 12.8026 | 9.2015 | 12.9849 | 31.6581 | 12.5984 | 9.0547 | 12.2865 | 31.6899 | 12.3991 | 8.9115 | 11.9969 | 31.7524 | 12.1519 | 8.7338 | 11.714 | 31.837 | 11.924 | 8.57 | 11.3598 | 31.9372 | 11.7337 | 8.4333 | 10.9366 | 32.0464 | 11.6221 | 8.353 | 10.5134 | 32.163 | 11.4988 | 8.2644 | 10.0296 | 32.2868 | 11.3306 | 8.1435 | 9.5149 | 32.4258 | 11.2197 | 8.0638 | 8.9462 | 33.0155 | 10.6215 | 7.6339 | 6.8123 | 33.4935 | 10.3896 | 7.4672 | 5.5458 | 33.8078 | 10.7164 | 7.7021 | 5.0364 | 34.0382 | 10.7607 | 7.7339 | 4.9605 | 31.5318 | 12.6413 | 9.0856 | 13.2142 | 31.5693 | 12.399 | 8.9114 | 12.7816 | 31.6357 | 12.1796 | 8.7537 | 12.4381 | 31.7159 | 12.0026 | 8.6265 | 12.2058 | 31.8069 | 11.8099 | 8.488 | 11.8571 | 31.9041 | 11.613 | 8.3465 | 11.4675 | 32.0099 | 11.5221 | 8.2812 | 11.0977 | 32.1218 | 11.4148 | 8.204 | 10.6571 | 32.2395 | 11.2878 | 8.1128 | 10.1677 | 32.3616 | 11.1783 | 8.0341 | 9.7074 | 32.6857 | 10.8532 | 7.8004 | 8.1524 | 32.9678 | 10.7304 | 7.7122 | 6.9431 | 33.1785 | 11.0318 | 7.9288 | 6.173 | 33.3361 | 11.031 | 7.9282 | 5.6073 | 31.5814 | 12.6374 | 9.0827 | 13.003 | 31.6581 | 12.3544 | 8.8793 | 12.3485 | 31.6901 | 12.0825 | 8.684 | 12.0437 | 31.7527 | 11.8875 | 8.5438 | 11.8051 | 31.8371 | 11.6854 | 8.3986 | 11.4595 | 31.937 | 11.497 | 8.2631 | 11.0603 | 32.0459 | 11.3965 | 8.1909 | 10.6693 | 32.1623 | 11.2399 | 8.0783 | 10.2069 | 32.2848 | 11.1296 | 7.9991 | 9.7216 | 32.4183 | 11.0278 | 7.9259 | 9.2103 | 32.9727 | 10.5668 | 7.5946 | 7.2962 | 33.3959 | 10.4805 | 7.5325 | 6.1903 | 33.6817 | 10.9748 | 7.8878 | 5.7258 | 33.8763 | 11.0028 | 7.9079 | 5.628 | 31.5763 | 12.8016 | 9.2007 | 12.9837 | 31.6514 | 12.6018 | 9.0571 | 12.2824 | 31.6912 | 12.3779 | 8.8962 | 11.9761 | 31.7718 | 12.1097 | 8.7035 | 11.6799 | 31.8852 | 11.8828 | 8.5404 | 11.3233 | 32.0272 | 11.6706 | 8.3879 | 10.8813 | 32.1977 | 11.5333 | 8.2892 | 10.3965 | 32.3905 | 11.3552 | 8.1612 | 9.8389 | 32.5955 | 11.2287 | 8.0703 | 9.3307 | 32.8211 | 11.0387 | 7.9337 | 8.8433 | 33.6516 | 10.1051 | 7.2627 | 5.8931 | 34.3365 | 8.748 | 6.2874 | -0.25492 | 34.7544 | 8.1469 | 5.8553 | -5.1176 | 35.0019 | 7.545 | 5.4227 | -8.7215 | 31.5643 | 12.812 | 9.2082 | 13.029 | 31.6368 | 12.7248 | 9.1456 | 12.3421 | 31.6778 | 12.5996 | 9.0556 | 12.0547 | 31.7493 | 12.3908 | 8.9055 | 11.7688 | 31.8511 | 12.1806 | 8.7544 | 11.4443 | 31.9812 | 12.1063 | 8.701 | 11.0604 | 32.1404 | 11.9778 | 8.6087 | 10.6461 | 32.3172 | 11.8214 | 8.4963 | 10.1711 | 32.5201 | 11.6549 | 8.3766 | 9.6123 | 32.8157 | 11.3523 | 8.1591 | 8.1571 | 33.6283 | 10.3073 | 7.408 | 1.2721 | 34.1639 | 8.8847 | 6.3856 | -4.2794 | 34.38 | 8.2385 | 5.9212 | -7.6124 | 34.3243 | 8.0953 | 5.8182 | -7.0923
LANGROYD RD | NELSON | PADIHAM | 389077 | 440584 | 30.3962 | 13.3915 | 9.7689 | 15.2284 | 30.4469 | 13.3481 | 9.7372 | 14.9441 | 30.4807 | 13.2986 | 9.7012 | 14.757 | 30.5377 | 13.1944 | 9.6251 | 14.508 | 30.6121 | 13.0585 | 9.526 | 14.2364 | 30.7041 | 12.935 | 9.4359 | 13.9 | 30.81 | 12.7499 | 9.3009 | 13.5042 | 30.9257 | 12.5658 | 9.1665 | 13.0689 | 31.0514 | 12.3518 | 9.0105 | 12.6393 | 31.1977 | 12.1221 | 8.8429 | 12.0998 | 31.7689 | 11.0708 | 8.076 | 10.2914 | 32.1671 | 11.0072 | 8.0296 | 9.4198 | 32.3636 | 11.3261 | 8.2622 | 9.2908 | 32.4444 | 11.291 | 8.2366 | 9.6061 | 30.3816 | 13.4468 | 9.8093 | 15.3481 | 30.4272 | 13.411 | 9.7832 | 15.1558 | 30.4945 | 13.4169 | 9.7874 | 14.9024 | 30.5691 | 13.4351 | 9.8008 | 14.6509 | 30.6518 | 13.4167 | 9.7873 | 14.3871 | 30.7316 | 13.3664 | 9.7506 | 14.0748 | 30.8217 | 13.2376 | 9.6566 | 13.6926 | 30.9186 | 13.0906 | 9.5494 | 13.2805 | 31.0224 | 12.9791 | 9.4681 | 12.8635 | 31.1318 | 12.8463 | 9.3712 | 12.4268 | 31.3828 | 12.3085 | 8.9789 | 11.2957 | 31.5849 | 12.0116 | 8.7623 | 10.4433 | 31.7043 | 12.193 | 8.8946 | 9.977 | 31.7672 | 11.9134 | 8.6907 | 9.7007 | 30.3966 | 13.4398 | 9.8041 | 15.2419 | 30.4474 | 13.4084 | 9.7812 | 14.9715 | 30.4813 | 13.3175 | 9.7149 | 14.7953 | 30.5384 | 13.2952 | 9.6986 | 14.5717 | 30.6124 | 13.2348 | 9.6546 | 14.3125 | 30.7036 | 13.138 | 9.584 | 13.9934 | 30.8086 | 12.9377 | 9.4379 | 13.6048 | 30.9233 | 12.7007 | 9.265 | 13.2025 | 31.0467 | 12.5342 | 9.1435 | 12.7985 | 31.1856 | 12.398 | 9.0442 | 12.3224 | 31.7228 | 11.9742 | 8.735 | 10.6874 | 32.0875 | 11.8758 | 8.6632 | 9.9179 | 32.2594 | 12.172 | 8.8793 | 9.8457 | 32.3302 | 12.0116 | 8.7623 | 10.1502 | 30.3945 | 13.3887 | 9.7669 | 15.2332 | 30.4485 | 13.3192 | 9.7162 | 14.9405 | 30.4941 | 13.2452 | 9.6622 | 14.7442 | 30.5713 | 13.1304 | 9.5785 | 14.4883 | 30.678 | 12.9942 | 9.4791 | 14.2047 | 30.8172 | 12.8422 | 9.3682 | 13.8461 | 30.9909 | 12.6321 | 9.2149 | 13.4217 | 31.1687 | 12.408 | 9.0514 | 12.9707 | 31.3585 | 12.1544 | 8.8665 | 12.5764 | 31.573 | 11.8979 | 8.6793 | 12.1675 | 32.3729 | 10.6872 | 7.7962 | 9.6989 | 33.1389 | 9.7386 | 7.1042 | 4.3845 | 33.5144 | 9.1522 | 6.6764 | 0.52656 | 33.7097 | 8.4324 | 6.1513 | -1.9313 | 30.3813 | 13.3949 | 9.7714 | 15.2603 | 30.4281 | 13.25 | 9.6657 | 14.982 | 30.4661 | 13.0766 | 9.5392 | 14.8125 | 30.5289 | 12.8018 | 9.3387 | 14.6041 | 30.6232 | 12.5562 | 9.1596 | 14.3557 | 30.7433 | 12.321 | 8.988 | 14.0568 | 30.8973 | 12.1677 | 8.8761 | 13.7062 | 31.0685 | 12.0878 | 8.8179 | 13.3442 | 31.2667 | 11.8215 | 8.6236 | 12.8784 | 31.5659 | 11.5736 | 8.4428 | 11.5474 | 32.4044 | 10.3131 | 7.5233 | 5.5233 | 32.8644 | 9.3128 | 6.7936 | 0.87188 | 33.0267 | 8.8522 | 6.4576 | -1.4947 | 32.9408 | 8.7939 | 6.415 | -0.32922
LEIGH | ATHERTON | KEARSLEY | 365863 | 399907 | 19.1155 | 19.1155 | 19.1155 | 11.3292 | 19.1338 | 19.1338 | 19.1338 | 11.1823 | 19.1505 | 19.1505 | 19.1505 | 11.1688 | 19.1721 | 19.1721 | 19.1721 | 11.0596 | 19.2022 | 19.2022 | 19.2022 | 11.0324 | 19.2357 | 19.2357 | 19.2357 | 10.8759 | 19.2689 | 19.2689 | 19.2689 | 10.78 | 19.2987 | 19.2987 | 19.2987 | 10.669 | 19.3304 | 19.3304 | 19.3304 | 10.5684 | 19.3653 | 19.3653 | 19.3653 | 10.3907 | 19.4961 | 19.4961 | 19.4961 | 9.8879 | 19.6145 | 19.6145 | 19.6145 | 9.5663 | 19.6963 | 19.6963 | 19.6963 | 9.3897 | 19.7654 | 19.7654 | 19.7654 | 9.3583 | 19.1165 | 19.1165 | 19.1165 | 11.3846 | 19.1365 | 19.1365 | 19.1365 | 11.2845 | 19.1622 | 19.1622 | 19.1622 | 11.2362 | 19.1835 | 19.1835 | 19.1835 | 11.1093 | 19.2125 | 19.2125 | 19.2125 | 11.0696 | 19.2452 | 19.2452 | 19.2452 | 10.9048 | 19.2813 | 19.2813 | 19.2813 | 10.7957 | 19.3199 | 19.3199 | 19.3199 | 10.668 | 19.3607 | 19.3607 | 19.3607 | 10.5476 | 19.4007 | 19.4007 | 19.4007 | 10.3727 | 19.5199 | 19.5199 | 19.5199 | 10.0384 | 19.5954 | 19.5954 | 19.5954 | 9.7512 | 19.6578 | 19.6578 | 19.6578 | 9.5189 | 19.7041 | 19.7041 | 19.7041 | 9.3743 | 19.1155 | 19.1155 | 19.1155 | 11.3328 | 19.1339 | 19.1339 | 19.1339 | 11.1918 | 19.1506 | 19.1506 | 19.1506 | 11.1833 | 19.1722 | 19.1722 | 19.1722 | 11.0798 | 19.2023 | 19.2023 | 19.2023 | 11.057 | 19.2358 | 19.2358 | 19.2358 | 10.9071 | 19.269 | 19.269 | 19.269 | 10.8167 | 19.2988 | 19.2988 | 19.2988 | 10.7113 | 19.3302 | 19.3302 | 19.3302 | 10.6182 | 19.3638 | 19.3638 | 19.3638 | 10.4564 | 19.4832 | 19.4832 | 19.4832 | 9.9981 | 19.5772 | 19.5772 | 19.5772 | 9.7174 | 19.6466 | 19.6466 | 19.6466 | 9.5588 | 19.696 | 19.696 | 19.696 | 9.533 | 19.1153 | 19.1153 | 19.1153 | 11.3309 | 19.1359 | 19.1359 | 19.1359 | 11.1842 | 19.1589 | 19.1589 | 19.1589 | 11.1698 | 19.1915 | 19.1915 | 19.1915 | 11.0561 | 19.2202 | 19.2202 | 19.2202 | 11.0259 | 19.2525 | 19.2525 | 19.2525 | 10.8609 | 19.291 | 19.291 | 19.291 | 10.7448 | 19.3345 | 19.3345 | 19.3345 | 10.6107 | 19.3822 | 19.3822 | 19.3822 | 10.5009 | 19.4348 | 19.4348 | 19.4348 | 10.3354 | 19.6419 | 19.6419 | 19.6419 | 9.4827 | 19.8699 | 19.8699 | 19.7013 | 7.4834 | 20.0101 | 20.0101 | 19.7739 | 5.8743 | 20.0802 | 20.0802 | 19.6653 | 4.8354 | 19.1088 | 19.1088 | 19.1088 | 11.3479 | 19.1253 | 19.1253 | 19.1253 | 11.2115 | 19.1465 | 19.1465 | 19.1465 | 11.206 | 19.1767 | 19.1767 | 19.1767 | 11.1069 | 19.1957 | 19.1957 | 19.1957 | 11.0855 | 19.2222 | 19.2222 | 19.2222 | 10.9373 | 19.2558 | 19.2558 | 19.2558 | 10.8425 | 19.2939 | 19.2939 | 19.2939 | 10.7321 | 19.3395 | 19.3395 | 19.3395 | 10.5823 | 19.4035 | 19.4035 | 19.4035 | 10.0528 | 19.6598 | 19.6598 | 19.6598 | 7.8182 | 19.8457 | 19.8457 | 19.7887 | 6.0151 | 19.9181 | 19.9181 | 19.7432 | 4.9509 | 19.8925 | 19.8925 | 19.7279 | 5.2657
LEVENSHULME | LONGSIGHT | BREDBURY | 387494 | 394155 | 24.6865 | 14.3111 | 10.4398 | 7.6317 | 24.7507 | 14.227 | 10.3784 | 7.5246 | 24.784 | 13.9602 | 10.1837 | 7.145 | 24.8504 | 13.6679 | 9.9706 | 6.8831 | 24.945 | 13.3312 | 9.725 | 6.5657 | 25.0643 | 13.1048 | 9.5597 | 6.1917 | 25.1989 | 13.008 | 9.4891 | 5.5382 | 25.347 | 12.9194 | 9.4245 | 5.0815 | 25.5067 | 12.8372 | 9.3646 | 4.7138 | 25.6837 | 12.673 | 9.2448 | 4.0623 | 26.4395 | 12.0667 | 8.8025 | 1.8635 | 27.1286 | 11.6748 | 8.5166 | 0.62298 | 27.5734 | 11.7009 | 8.5356 | 0.047023 | 27.9737 | 11.6116 | 8.4705 | -0.15302 | 24.6528 | 14.3945 | 10.5006 | 7.6382 | 24.6926 | 13.8822 | 10.1269 | 7.5334 | 24.7641 | 13.7036 | 9.9966 | 7.095 | 24.8533 | 13.4887 | 9.8398 | 6.8398 | 24.959 | 13.271 | 9.681 | 6.5424 | 25.0794 | 13.078 | 9.5402 | 6.1816 | 25.2136 | 12.9105 | 9.418 | 5.5352 | 25.3598 | 12.7928 | 9.3321 | 5.0933 | 25.5175 | 12.6826 | 9.2518 | 4.7511 | 25.6861 | 12.5086 | 9.1249 | 3.8389 | 26.1357 | 12.2461 | 8.9334 | 2.6654 | 26.5507 | 12.0476 | 8.7886 | 1.5269 | 26.8863 | 12.0914 | 8.8205 | 0.78423 | 27.1538 | 12.0243 | 8.7716 | 0.30889 | 24.6874 | 14.3934 | 10.4998 | 7.6435 | 24.752 | 14.1445 | 10.3182 | 7.5524 | 24.7859 | 13.6145 | 9.9316 | 7.1934 | 24.8528 | 13.5939 | 9.9166 | 6.9468 | 24.9476 | 13.4202 | 9.7899 | 6.6478 | 25.0662 | 13.2256 | 9.6479 | 6.2829 | 25.1999 | 13.0579 | 9.5255 | 5.6601 | 25.3468 | 12.9292 | 9.4317 | 5.2017 | 25.5036 | 12.8246 | 9.3554 | 4.8657 | 25.6713 | 12.6045 | 9.1948 | 4.265 | 26.3611 | 12.1691 | 8.8772 | 2.3442 | 26.8918 | 11.9737 | 8.7347 | 1.2888 | 27.2572 | 12.0033 | 8.7563 | 0.81248 | 27.5289 | 11.9209 | 8.6961 | 0.80444 | 24.6836 | 14.313 | 10.4411 | 7.6324 | 24.748 | 14.2261 | 10.3777 | 7.5207 | 24.7923 | 13.9313 | 10.1627 | 7.1347 | 24.8816 | 13.6212 | 9.9365 | 6.8553 | 25.0117 | 13.2634 | 9.6755 | 6.55 | 25.1866 | 13.08 | 9.5417 | 6.182 | 25.3995 | 12.9579 | 9.4526 | 5.5202 | 25.6469 | 12.8477 | 9.3722 | 5.0639 | 25.8941 | 12.7582 | 9.3069 | 4.7991 | 26.16 | 12.5843 | 9.1801 | 4.2619 | 27.2409 | 11.6214 | 8.4777 | 1.1606 | 28.3646 | 10.2408 | 7.4705 | -5.1985 | 29.0691 | 9.2962 | 6.7814 | -10.0727 | 29.4189 | 8.68 | 6.332 | -12.9674 | 24.6717 | 14.3235 | 10.4488 | 7.6763 | 24.7369 | 14.3452 | 10.4646 | 7.5709 | 24.7848 | 14.1279 | 10.3061 | 7.1979 | 24.8701 | 13.85 | 10.1034 | 6.9631 | 24.9949 | 13.5565 | 9.8893 | 6.7163 | 25.165 | 13.6241 | 9.9386 | 6.4174 | 25.383 | 13.4819 | 9.8348 | 5.8373 | 25.6251 | 13.3588 | 9.745 | 5.4419 | 25.8703 | 13.2523 | 9.6673 | 5.0127 | 26.1833 | 12.8663 | 9.3858 | 3.3792 | 27.4146 | 11.2901 | 8.2359 | -3.8435 | 28.3404 | 9.7851 | 7.1381 | -9.4868 | 28.7415 | 9.0804 | 6.624 | -12.6323 | 28.712 | 9.0527 | 6.6038 | -11.4656
LEYLAND NATIONAL | STAINBURN & SIDDICK | HARKER / HUTTON | 301973 | 525948 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 10.117 | 2.9061 | 2.0887 | 10.117 | 10.4118 | 3.8695 | 2.7811 | 10.4118 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 9.1068 | 1.4994 | 1.0776 | 9.1068 | 9.9935 | 2.7019 | 1.9419 | 9.9935 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 11.3228 | 1.9672 | 1.4139 | 11.3228 | 11.5008 | 2.6752 | 1.9227 | 11.5008 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 10.228 | 4.4337 | 3.1866 | 10.228 | 11.036 | 3.7614 | 2.7034 | 11.036 | 11.2857 | 3.224 | 2.3172 | 11.2857 | 11.2447 | 2.7933 | 2.0076 | 11.2447
LITTLE HULTON | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 22.4455 | 12.3812 | 8.8986 | 6.9738 | 22.5293 | 12.2559 | 8.8085 | 6.2512 | 22.5728 | 12.0799 | 8.682 | 5.8032 | 22.6409 | 11.7487 | 8.444 | 5.0975 | 22.7322 | 11.4486 | 8.2283 | 4.3092 | 22.8452 | 11.4587 | 8.2356 | 2.916 | 22.9724 | 11.3158 | 8.1329 | 1.5065 | 23.1105 | 11.1736 | 8.0307 | 0.42114 | 23.2585 | 11.023 | 7.9225 | -0.65152 | 23.4202 | 10.8938 | 7.8296 | -1.6232 | 24.3873 | 10.3404 | 7.4319 | -4.1935 | 25.6116 | 9.8019 | 7.0448 | -6.0142 | 26.5458 | 9.5687 | 6.8772 | -6.8386 | 27.5539 | 8.9155 | 6.4077 | -7.4437 | 22.4042 | 12.3593 | 8.8829 | 7.3343 | 22.4555 | 12.2272 | 8.7879 | 6.9471 | 22.5356 | 12.0635 | 8.6703 | 6.4976 | 22.6267 | 11.8771 | 8.5363 | 6.0541 | 22.7317 | 11.7513 | 8.4459 | 5.5571 | 22.8496 | 11.6874 | 8.4 | 4.8542 | 22.9814 | 11.6216 | 8.3527 | 4.1301 | 23.1243 | 11.5473 | 8.2993 | 3.4738 | 23.2786 | 11.4635 | 8.2391 | 2.8185 | 23.4281 | 11.4148 | 8.2041 | 2.1957 | 24.0336 | 11.2479 | 8.0841 | 0.14664 | 24.7046 | 11.0493 | 7.9414 | -1.467 | 25.4134 | 10.7772 | 7.7458 | -2.4892 | 26.0248 | 10.3443 | 7.4346 | -3.3169 | 22.4462 | 12.3478 | 8.8746 | 6.9919 | 22.5309 | 12.0306 | 8.6466 | 6.2816 | 22.5756 | 12.1869 | 8.759 | 5.8459 | 22.645 | 12.2705 | 8.819 | 5.1513 | 22.7377 | 12.2163 | 8.7801 | 4.3792 | 22.8516 | 12.1931 | 8.7634 | 3.0038 | 22.9793 | 12.0952 | 8.6931 | 1.6118 | 23.1179 | 11.9907 | 8.6179 | 0.54367 | 23.2648 | 11.8727 | 8.5331 | -0.50403 | 23.4201 | 11.7356 | 8.4346 | -1.4218 | 24.2467 | 11.2109 | 8.0575 | -3.7344 | 25.0714 | 10.6627 | 7.6635 | -5.1961 | 25.8038 | 10.5432 | 7.5776 | -5.8626 | 26.4399 | 10.1245 | 7.2767 | -6.2532 | 22.4427 | 12.3818 | 8.8991 | 6.9797 | 22.5273 | 12.2408 | 8.7977 | 6.2605 | 22.5809 | 11.967 | 8.6009 | 5.8052 | 22.6687 | 11.5346 | 8.2901 | 5.0737 | 22.7889 | 11.6126 | 8.3462 | 4.2983 | 22.9591 | 11.5608 | 8.309 | 2.905 | 23.1737 | 11.3609 | 8.1653 | 1.4629 | 23.427 | 11.2148 | 8.0603 | 0.32694 | 23.7129 | 11.0409 | 7.9353 | -0.72611 | 24.0338 | 10.8608 | 7.8059 | -1.6333 | 25.8209 | 9.5191 | 6.8416 | -5.2596 | 27.8232 | 8.464 | 6.0832 | -11.8834 | 29.1494 | 6.9632 | 5.0046 | -16.933 | 29.8207 | 5.9832 | 4.3002 | -20.5907 | 22.4387 | 12.3836 | 8.9003 | 6.9825 | 22.5305 | 12.1748 | 8.7503 | 6.2299 | 22.5934 | 11.738 | 8.4364 | 5.7612 | 22.6861 | 11.8863 | 8.5429 | 5.0426 | 22.8118 | 11.9574 | 8.594 | 4.2984 | 23.003 | 11.7701 | 8.4594 | 2.9472 | 23.2615 | 11.582 | 8.3242 | 1.5327 | 23.5709 | 11.3517 | 8.1587 | 0.42888 | 23.9289 | 11.1337 | 8.002 | -0.7248 | 24.3479 | 10.7335 | 7.7143 | -2.5867 | 26.4177 | 9.3766 | 6.7392 | -9.9989 | 28.184 | 7.7592 | 5.5767 | -16.0403 | 29.0248 | 6.9006 | 4.9596 | -19.5153 | 29.178 | 6.6001 | 4.7436 | -19.1982
LITTLE SALKELD | PENRITH & SHAP | HARKER / HUTTON | 356221 | 537513 | 16.4453 | 16.4453 | 16.4453 | 8.4039 | 16.4989 | 16.4989 | 16.4989 | 8.1701 | 16.5667 | 16.5667 | 16.5667 | 8.0804 | 16.653 | 16.653 | 16.653 | 7.9234 | 16.7548 | 16.7548 | 16.7548 | 7.71 | 16.8341 | 16.8341 | 16.8341 | 7.5038 | 16.8984 | 16.8984 | 16.8984 | 7.2114 | 16.9687 | 16.9687 | 16.9687 | 6.9515 | 17.0447 | 17.0447 | 16.8866 | 6.6653 | 17.1328 | 17.1328 | 16.7925 | 6.3141 | 17.5219 | 17.5219 | 16.4521 | 4.9461 | 17.8525 | 17.8525 | 16.2029 | 4.1322 | 18.066 | 18.066 | 16.0385 | 3.7463 | 18.2325 | 18.2325 | 15.9185 | 3.7731 | 16.4322 | 16.4322 | 16.4322 | 8.4496 | 16.4733 | 16.4733 | 16.4733 | 8.2792 | 16.5396 | 16.5396 | 16.5396 | 8.1811 | 16.6094 | 16.6094 | 16.6094 | 8.0074 | 16.6877 | 16.6877 | 16.6877 | 7.8041 | 16.7688 | 16.7688 | 16.7688 | 7.6091 | 16.866 | 16.866 | 16.866 | 7.3303 | 16.9695 | 16.9695 | 16.9695 | 7.0777 | 17.078 | 17.078 | 17.078 | 6.8002 | 17.1906 | 17.1906 | 17.1906 | 6.5226 | 17.4075 | 17.4075 | 17.4075 | 5.7328 | 17.6031 | 17.6031 | 17.3356 | 5.0228 | 17.7612 | 17.7612 | 17.1901 | 4.3894 | 17.8764 | 17.8764 | 17.0567 | 3.9061 | 16.4464 | 16.4464 | 16.4464 | 8.4052 | 16.5005 | 16.5005 | 16.5005 | 8.1794 | 16.5686 | 16.5686 | 16.5686 | 8.098 | 16.6551 | 16.6551 | 16.6551 | 7.997 | 16.7566 | 16.7566 | 16.7566 | 7.7737 | 16.835 | 16.835 | 16.835 | 7.5587 | 16.8989 | 16.8989 | 16.8989 | 7.3282 | 16.9685 | 16.9685 | 16.9685 | 7.0815 | 17.0431 | 17.0431 | 16.9463 | 6.8072 | 17.1268 | 17.1268 | 16.8738 | 6.4739 | 17.4791 | 17.4791 | 16.6352 | 5.244 | 17.7362 | 17.7362 | 16.4064 | 4.6041 | 17.9035 | 17.9035 | 16.1821 | 4.3178 | 18.0084 | 18.0084 | 16.0113 | 4.4322 | 16.4463 | 16.4463 | 16.4463 | 8.4107 | 16.5045 | 16.5045 | 16.5045 | 8.1659 | 16.5858 | 16.5858 | 16.5858 | 8.0503 | 16.6959 | 16.6959 | 16.6959 | 7.8739 | 16.8065 | 16.8065 | 16.8065 | 7.6778 | 16.8847 | 16.8847 | 16.8847 | 7.4028 | 16.9862 | 16.9862 | 16.9655 | 7.0713 | 17.1033 | 17.1033 | 16.8625 | 6.7923 | 17.234 | 17.234 | 16.7602 | 6.5276 | 17.373 | 17.373 | 16.6537 | 6.2373 | 17.9147 | 17.9147 | 16.1701 | 4.5222 | 18.3792 | 18.3792 | 15.7106 | 2.9061 | 18.6239 | 18.6239 | 15.416 | 2.0304 | 18.7236 | 18.7236 | 15.2049 | 1.5273 | 16.4626 | 16.4626 | 16.4626 | 8.4088 | 16.5486 | 16.5486 | 16.5486 | 8.1407 | 16.646 | 16.646 | 16.646 | 8.0302 | 16.7424 | 16.7424 | 16.7424 | 7.8643 | 16.7989 | 16.7989 | 16.7989 | 7.6523 | 16.8755 | 16.8755 | 16.8755 | 7.3817 | 16.9791 | 16.9791 | 16.9791 | 7.0767 | 17.0971 | 17.0971 | 16.9163 | 6.8332 | 17.2219 | 17.2219 | 16.8156 | 6.5525 | 17.3597 | 17.3597 | 16.6961 | 6.1591 | 17.8889 | 17.8889 | 16.1918 | 4.243 | 18.2504 | 18.2504 | 15.7818 | 3.0805 | 18.3734 | 18.3734 | 15.5611 | 2.6053 | 18.3637 | 18.3637 | 15.4481 | 2.6573
LITTLEBOROUGH | BELFIELD | ROCHDALE | 393221 | 416124 | 25.4256 | 10.1015 | 7.3689 | 6.6724 | 25.5156 | 10.0052 | 7.2986 | 6.0208 | 25.5416 | 9.9606 | 7.2661 | 5.8944 | 25.5992 | 9.9108 | 7.2298 | 5.7765 | 25.68 | 9.7565 | 7.1172 | 5.4004 | 25.782 | 9.6425 | 7.0341 | 4.9215 | 25.8938 | 9.5012 | 6.931 | 4.4367 | 26.0131 | 9.3674 | 6.8334 | 4.1197 | 26.1387 | 9.2362 | 6.7377 | 3.5124 | 26.2744 | 9.1055 | 6.6423 | 3.103 | 26.8206 | 8.6528 | 6.3121 | 1.5819 | 27.2439 | 8.287 | 6.0453 | 0.74675 | 27.5121 | 8.0888 | 5.9007 | 0.56436 | 27.706 | 7.9524 | 5.8012 | 0.57522 | 25.3586 | 10.1083 | 7.3739 | 6.9255 | 25.3953 | 10.0166 | 7.307 | 6.5009 | 25.4637 | 9.9095 | 7.2289 | 6.3091 | 25.5486 | 9.8235 | 7.1661 | 6.1535 | 25.6448 | 9.6899 | 7.0687 | 5.7785 | 25.7499 | 9.5699 | 6.9811 | 5.3189 | 25.8651 | 9.4613 | 6.9019 | 4.8484 | 25.9872 | 9.3754 | 6.8392 | 4.5389 | 26.1164 | 9.2436 | 6.7431 | 3.9371 | 26.251 | 9.1486 | 6.6738 | 3.5754 | 26.5463 | 8.8333 | 6.4438 | 2.4102 | 26.7877 | 8.628 | 6.294 | 1.4768 | 26.9594 | 8.379 | 6.1124 | 0.95044 | 27.0719 | 8.3429 | 6.086 | 0.511 | 25.4256 | 10.1063 | 7.3724 | 6.6782 | 25.5157 | 10.0012 | 7.2957 | 6.034 | 25.5417 | 9.8441 | 7.1811 | 5.9127 | 25.5994 | 9.7362 | 7.1024 | 5.8 | 25.6801 | 9.5083 | 6.9362 | 5.4325 | 25.7816 | 9.4244 | 6.875 | 4.9639 | 25.8931 | 9.2957 | 6.7811 | 4.4893 | 26.0122 | 9.1958 | 6.7082 | 4.1801 | 26.1363 | 9.0554 | 6.6058 | 3.5891 | 26.266 | 8.9458 | 6.5258 | 3.2128 | 26.7761 | 8.5014 | 6.2017 | 1.7828 | 27.1488 | 8.1238 | 5.9262 | 1.0027 | 27.3906 | 8.0325 | 5.8596 | 0.82247 | 27.5547 | 7.7755 | 5.6721 | 0.82372 | 25.4184 | 10.1047 | 7.3713 | 6.6898 | 25.5037 | 10.0216 | 7.3106 | 6.0619 | 25.5323 | 9.9998 | 7.2947 | 5.9676 | 25.6004 | 9.8998 | 7.2218 | 5.8863 | 25.7006 | 9.7622 | 7.1214 | 5.5703 | 25.8328 | 9.6385 | 7.0311 | 5.1658 | 25.9891 | 9.4885 | 6.9218 | 4.7546 | 26.1651 | 9.3683 | 6.8341 | 4.5197 | 26.3582 | 9.219 | 6.7251 | 4.049 | 26.5713 | 9.1588 | 6.6812 | 3.8244 | 27.3288 | 8.5088 | 6.207 | 2.1305 | 27.9842 | 7.428 | 5.4186 | -2.1483 | 28.354 | 6.5567 | 4.783 | -5.6764 | 28.539 | 5.936 | 4.3302 | -8.1291 | 25.4074 | 10.1403 | 7.3972 | 6.7108 | 25.4907 | 10.1018 | 7.3691 | 6.0735 | 25.5174 | 10.1214 | 7.3834 | 5.9882 | 25.576 | 10.1089 | 7.3743 | 5.9474 | 25.666 | 9.9949 | 7.2911 | 5.6708 | 25.7833 | 9.8437 | 7.1808 | 5.3269 | 25.9273 | 9.7125 | 7.0851 | 4.9784 | 26.0853 | 9.6306 | 7.0254 | 4.8148 | 26.2647 | 9.5028 | 6.9322 | 4.3071 | 26.4915 | 9.283 | 6.7718 | 3.4915 | 27.2804 | 8.1163 | 5.9208 | -1.0165 | 27.7647 | 6.9322 | 5.057 | -5.1312 | 27.9224 | 6.2358 | 4.549 | -7.4113 | 27.8353 | 6.2234 | 4.5399 | -6.8579
LONGFORD BRIDGE | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 30.6588 | 7.8991 | 5.7623 | 14.875 | 30.7132 | 7.6909 | 5.6104 | 13.9463 | 30.772 | 7.5867 | 5.5344 | 13.4776 | 30.8462 | 7.5059 | 5.4754 | 13.2992 | 30.9417 | 7.3341 | 5.3501 | 13.0133 | 31.0464 | 7.1812 | 5.2386 | 12.689 | 31.1602 | 7.1413 | 5.2095 | 12.2347 | 31.2824 | 7.1064 | 5.184 | 11.9949 | 31.4227 | 7.0348 | 5.1318 | 11.6099 | 31.6193 | 6.9351 | 5.059 | 11.1407 | 32.1887 | 6.5188 | 4.7554 | 9.4094 | 32.5813 | 6.5053 | 4.7455 | 8.3235 | 32.8443 | 7.1097 | 5.1864 | 7.8436 | 33.0292 | 7.3544 | 5.3649 | 7.8299 | 30.6617 | 7.9589 | 5.8059 | 15.2536 | 30.7184 | 7.8622 | 5.7353 | 14.7591 | 30.792 | 7.8128 | 5.6993 | 14.3357 | 30.8482 | 7.7745 | 5.6714 | 14.1687 | 30.923 | 7.6966 | 5.6146 | 13.9072 | 31.0079 | 7.6312 | 5.5669 | 13.6071 | 31.1012 | 7.5171 | 5.4836 | 13.208 | 31.2003 | 7.381 | 5.3843 | 12.9355 | 31.3053 | 7.3718 | 5.3776 | 12.589 | 31.4147 | 7.3105 | 5.3329 | 12.2179 | 31.8249 | 7.1282 | 5.2 | 11.1004 | 32.0765 | 7.1491 | 5.2152 | 10.0655 | 32.2396 | 7.5556 | 5.5117 | 9.3063 | 32.3545 | 7.6879 | 5.6082 | 8.7355 | 30.6588 | 7.9702 | 5.8141 | 14.8869 | 30.7132 | 7.8588 | 5.7329 | 13.9389 | 30.7721 | 7.7455 | 5.6502 | 13.5132 | 30.8465 | 7.7207 | 5.6321 | 13.3533 | 30.9417 | 7.6769 | 5.6002 | 13.0836 | 31.0461 | 7.6095 | 5.5511 | 12.74 | 31.1596 | 7.5198 | 5.4856 | 12.3625 | 31.2816 | 7.4432 | 5.4297 | 12.0395 | 31.4206 | 7.3528 | 5.3638 | 11.6778 | 31.6117 | 7.2496 | 5.2885 | 11.3023 | 32.1479 | 6.9372 | 5.0606 | 9.7474 | 32.4918 | 7.0843 | 5.1679 | 8.8705 | 32.7293 | 7.7816 | 5.6765 | 8.4581 | 32.8838 | 7.9851 | 5.825 | 8.4294 | 30.6602 | 7.8986 | 5.7619 | 14.8756 | 30.726 | 7.6853 | 5.6063 | 13.9548 | 30.81 | 7.566 | 5.5193 | 13.47 | 30.9243 | 7.4836 | 5.4592 | 13.2808 | 31.0738 | 7.3128 | 5.3346 | 12.9895 | 31.2671 | 7.165 | 5.2268 | 12.6422 | 31.5048 | 7.1118 | 5.188 | 12.1056 | 31.6657 | 7.0451 | 5.1393 | 11.7633 | 31.8417 | 6.9522 | 5.0716 | 11.3612 | 32.0363 | 6.8665 | 5.009 | 10.9548 | 32.7343 | 6.2192 | 4.5368 | 8.4151 | 33.2496 | 5.3934 | 3.9344 | 3.0495 | 32.5411 | 5.2785 | 3.8506 | -1.0038 | 30.7691 | 4.9911 | 3.6409 | -3.8445 | 30.649 | 7.9038 | 5.7657 | 14.8995 | 30.7109 | 7.6767 | 5.6001 | 13.9726 | 30.7934 | 7.5342 | 5.4961 | 13.5238 | 30.9112 | 7.4081 | 5.4041 | 13.3684 | 31.0869 | 7.3437 | 5.3571 | 13.0721 | 31.2927 | 7.2844 | 5.3139 | 12.7294 | 31.4565 | 7.1677 | 5.2287 | 12.2514 | 31.6034 | 7.094 | 5.175 | 11.9909 | 31.7695 | 6.9883 | 5.0979 | 11.5218 | 31.9897 | 6.7581 | 4.9299 | 10.251 | 32.7654 | 6.5127 | 4.751 | 4.2821 | 32.9921 | 5.3516 | 3.9039 | -0.53254 | 31.1981 | 5.0606 | 3.6917 | -3.2207 | 31.2869 | 5.075 | 3.7022 | -2.5577
LONGRIDGE | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 360581 | 437001 | 30.7432 | 15.5664 | 11.3555 | 14.9304 | 30.8214 | 15.3617 | 11.2061 | 14.562 | 30.8532 | 15.1571 | 11.0569 | 14.2141 | 30.91 | 14.9976 | 10.9405 | 13.8091 | 30.9809 | 14.7757 | 10.7787 | 13.6412 | 31.0696 | 14.5419 | 10.6081 | 13.2568 | 31.1684 | 14.4125 | 10.5137 | 12.8341 | 31.2727 | 14.247 | 10.393 | 12.4371 | 31.3822 | 14.114 | 10.296 | 12.0716 | 31.5095 | 13.9242 | 10.1575 | 11.3926 | 32.0884 | 13.1107 | 9.564 | 8.9171 | 32.6789 | 12.4648 | 9.0929 | 7.3309 | 33.0771 | 12.4353 | 9.0714 | 6.4348 | 33.4137 | 12.2737 | 8.9535 | 6.4219 | 30.7053 | 15.5111 | 11.3151 | 15.0288 | 30.7578 | 15.4303 | 11.2562 | 14.7538 | 30.8336 | 15.5201 | 11.3217 | 14.3811 | 30.9222 | 15.4441 | 11.2662 | 14.0183 | 31.0211 | 15.4058 | 11.2383 | 13.8737 | 31.1318 | 15.2669 | 11.137 | 13.5066 | 31.2556 | 15.1467 | 11.0493 | 13.0938 | 31.3883 | 15.0951 | 11.0117 | 12.6995 | 31.5315 | 15.0083 | 10.9483 | 12.3261 | 31.6712 | 14.923 | 10.8861 | 11.8167 | 32.0163 | 14.6324 | 10.6742 | 10.4667 | 32.3653 | 14.3169 | 10.444 | 8.9738 | 32.6792 | 14.3148 | 10.4425 | 7.6353 | 32.9296 | 14.2671 | 10.4076 | 6.7725 | 30.7436 | 15.5106 | 11.3148 | 14.9384 | 30.8222 | 15.4838 | 11.2952 | 14.5871 | 30.8544 | 15.5682 | 11.3568 | 14.2598 | 30.9116 | 15.4812 | 11.2933 | 13.8804 | 30.9829 | 15.3841 | 11.2225 | 13.733 | 31.0714 | 15.2229 | 11.1049 | 13.3725 | 31.1701 | 15.0883 | 11.0067 | 12.9741 | 31.2741 | 14.9606 | 10.9136 | 12.6008 | 31.3822 | 14.8258 | 10.8152 | 12.257 | 31.505 | 14.6787 | 10.7079 | 11.6485 | 32.0289 | 14.2086 | 10.365 | 9.431 | 32.4711 | 13.8391 | 10.0954 | 8.1013 | 32.8119 | 14.0287 | 10.2337 | 7.2891 | 33.0304 | 13.6582 | 9.9635 | 7.3066 | 30.7388 | 15.5659 | 11.3551 | 14.9352 | 30.8157 | 15.3522 | 11.1992 | 14.5413 | 30.8503 | 15.1684 | 11.0651 | 14.1649 | 30.9156 | 14.9307 | 10.8918 | 13.7275 | 31.0024 | 14.7151 | 10.7345 | 13.5048 | 31.1208 | 14.4652 | 10.5521 | 13.0289 | 31.2664 | 14.2412 | 10.3888 | 12.4596 | 31.4307 | 14.0656 | 10.2606 | 11.9062 | 31.6104 | 13.8864 | 10.1299 | 11.4596 | 31.8089 | 13.6673 | 9.9701 | 10.8699 | 32.668 | 12.5803 | 9.1771 | 8.3239 | 33.4866 | 11.4066 | 8.321 | 4.6053 | 33.9673 | 10.9591 | 7.9945 | 2.0856 | 34.2028 | 10.5034 | 7.6621 | 0.3634 | 30.7295 | 15.5688 | 11.3572 | 14.9538 | 30.8023 | 15.4596 | 11.2775 | 14.5685 | 30.8313 | 15.3926 | 11.2287 | 14.2214 | 30.887 | 15.2711 | 11.1401 | 13.8165 | 30.9657 | 15.1563 | 11.0563 | 13.5987 | 31.0785 | 14.9419 | 10.8999 | 13.16 | 31.2248 | 14.7473 | 10.7579 | 12.6671 | 31.391 | 14.5556 | 10.6181 | 12.207 | 31.5763 | 14.359 | 10.4747 | 11.8078 | 31.7964 | 14.0633 | 10.259 | 10.8153 | 32.6947 | 12.4444 | 9.078 | 6.4408 | 33.3696 | 11.5707 | 8.4407 | 3.3008 | 33.645 | 10.884 | 7.9397 | 1.5861 | 33.6573 | 10.759 | 7.8485 | 1.9228
LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 25.2854 | 11.8947 | 8.677 | 9.6271 | 25.3963 | 11.4801 | 8.3745 | 8.9826 | 25.4131 | 11.0877 | 8.0883 | 9.011 | 25.4761 | 10.6511 | 7.7698 | 8.5804 | 25.5683 | 10.27 | 7.4918 | 8.4578 | 25.6887 | 10.0534 | 7.3338 | 8.0396 | 25.8113 | 9.9327 | 7.2458 | 7.6238 | 25.9401 | 9.8027 | 7.1509 | 7.3107 | 26.0761 | 9.5539 | 6.9694 | 6.8214 | 26.2293 | 9.4818 | 6.9169 | 6.3613 | 26.8088 | 8.8528 | 6.458 | 4.4838 | 27.3112 | 8.541 | 6.2306 | 3.3186 | 27.644 | 8.5721 | 6.2533 | 2.7361 | 27.8691 | 8.5229 | 6.2173 | 2.6685 | 25.203 | 11.9694 | 8.7315 | 9.9041 | 25.2514 | 11.1012 | 8.0982 | 9.4959 | 25.3435 | 10.7951 | 7.8749 | 9.4083 | 25.4638 | 10.519 | 7.6735 | 8.8892 | 25.5992 | 10.2543 | 7.4804 | 8.6906 | 25.7506 | 10.0288 | 7.3159 | 8.2692 | 25.9165 | 9.8867 | 7.2122 | 7.7915 | 26.095 | 9.7789 | 7.1336 | 7.4016 | 26.2864 | 9.6512 | 7.0404 | 6.8676 | 26.4912 | 9.5199 | 6.9447 | 6.374 | 26.9128 | 9.2269 | 6.7309 | 5.0332 | 27.2601 | 9.0557 | 6.606 | 3.9171 | 27.494 | 9.0716 | 6.6176 | 3.1154 | 27.6489 | 8.9858 | 6.555 | 2.6151 | 25.2863 | 11.9658 | 8.7289 | 9.6579 | 25.3975 | 11.5334 | 8.4135 | 9.0278 | 25.4147 | 10.9572 | 7.9931 | 9.049 | 25.478 | 10.764 | 7.8522 | 8.62 | 25.5702 | 10.4578 | 7.6288 | 8.5075 | 25.6898 | 10.2431 | 7.4722 | 8.1039 | 25.8117 | 10.0879 | 7.359 | 7.7027 | 25.9396 | 9.9698 | 7.2728 | 7.4027 | 26.0735 | 9.8198 | 7.1634 | 6.9339 | 26.2209 | 9.6662 | 7.0513 | 6.5094 | 26.7556 | 9.1875 | 6.7021 | 4.7192 | 27.1535 | 8.9944 | 6.5613 | 3.6391 | 27.4189 | 9.08 | 6.6238 | 3.0902 | 27.5887 | 8.9566 | 6.5337 | 3.051 | 25.2774 | 11.8972 | 8.6789 | 9.6427 | 25.3817 | 11.4776 | 8.3727 | 9.0144 | 25.3986 | 11.0686 | 8.0744 | 9.0596 | 25.4702 | 10.6235 | 7.7497 | 8.6393 | 25.5793 | 10.2063 | 7.4454 | 8.5357 | 25.7307 | 10.045 | 7.3277 | 8.1307 | 25.891 | 9.8957 | 7.2188 | 7.6902 | 26.0675 | 9.7187 | 7.0897 | 7.347 | 26.2575 | 9.5797 | 6.9883 | 6.8715 | 26.465 | 9.4139 | 6.8673 | 6.471 | 27.2397 | 8.5672 | 6.2496 | 4.296 | 27.9758 | 7.359 | 5.3683 | -0.8395 | 28.3846 | 6.6419 | 4.8451 | -4.9029 | 28.5583 | 6.0498 | 4.4132 | -7.5959 | 25.258 | 11.9072 | 8.6861 | 9.69 | 25.3506 | 11.6468 | 8.4962 | 9.0848 | 25.3582 | 11.3493 | 8.2791 | 9.1555 | 25.4137 | 10.9818 | 8.011 | 8.7668 | 25.4991 | 10.641 | 7.7625 | 8.6932 | 25.6154 | 10.569 | 7.7099 | 8.3425 | 25.7568 | 10.3427 | 7.5449 | 7.9721 | 25.9143 | 10.2709 | 7.4925 | 7.7053 | 26.0898 | 10.104 | 7.3707 | 7.2198 | 26.3139 | 9.7744 | 7.1303 | 6.1898 | 27.1582 | 8.4938 | 6.1961 | 0.7722 | 27.7497 | 7.045 | 5.1393 | -4.0332 | 27.9615 | 6.2852 | 4.585 | -6.8028 | 27.8785 | 6.2166 | 4.5349 | -6.0569
LOSTOCK | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 38.3767 | 7.1138 | 5.1128 | 16.0069 | 38.5365 | 6.522 | 4.6875 | 14.8719 | 37.3629 | 6.1515 | 4.4212 | 14.663 | 34.4285 | 5.6684 | 4.074 | 14.2611 | 31.9401 | 5.2587 | 3.7795 | 14.0706 | 29.1012 | 4.7913 | 3.4436 | 13.3628 | 28.2716 | 4.6547 | 3.3454 | 12.9066 | 27.3385 | 4.5011 | 3.235 | 12.3879 | 26.6937 | 4.3949 | 3.1587 | 11.937 | 25.9183 | 4.2673 | 3.067 | 11.2443 | 23.4526 | 3.8613 | 2.7752 | 9.3879 | 26.3196 | 4.3333 | 3.1144 | 8.6313 | 41.6154 | 8.3935 | 6.0326 | 8.4752 | 42.2164 | 8.5795 | 6.1662 | 8.5944 | 38.1817 | 7.3608 | 5.2904 | 16.7328 | 38.1807 | 6.9435 | 4.9905 | 16.2486 | 38.2385 | 6.4213 | 4.6151 | 16.0228 | 35.4975 | 5.8444 | 4.2005 | 15.5241 | 32.4562 | 5.3437 | 3.8406 | 15.3489 | 29.8464 | 4.914 | 3.5318 | 14.7182 | 29.2983 | 4.8237 | 3.4669 | 14.3175 | 28.6186 | 4.7118 | 3.3865 | 13.8542 | 28.072 | 4.6218 | 3.3218 | 13.4424 | 27.3547 | 4.5037 | 3.2369 | 12.8512 | 25.7087 | 4.2327 | 3.0422 | 11.4911 | 26.1691 | 4.3085 | 3.0966 | 10.6707 | 40.3383 | 6.7061 | 4.8198 | 10.0374 | 40.6526 | 9.1023 | 6.542 | 9.8976 | 38.3769 | 7.3654 | 5.2936 | 16.0152 | 38.5372 | 6.9263 | 4.9781 | 14.8883 | 38.5354 | 6.4098 | 4.6068 | 14.6667 | 35.3362 | 5.8178 | 4.1814 | 14.2853 | 32.47 | 5.3459 | 3.8422 | 14.1026 | 29.3536 | 4.8328 | 3.4735 | 13.4058 | 28.7574 | 4.7347 | 3.4029 | 12.9585 | 28.0486 | 4.618 | 3.319 | 12.448 | 27.5663 | 4.5386 | 3.262 | 12.0136 | 26.8161 | 4.4151 | 3.1732 | 11.3712 | 25.4104 | 4.1836 | 3.0069 | 9.7184 | 27.5677 | 4.5388 | 3.2621 | 9.2213 | 41.0782 | 9.1825 | 6.5996 | 9.1632 | 41.4272 | 9.2788 | 6.6689 | 9.5358 | 38.3607 | 7.1147 | 5.1135 | 16.0384 | 38.5076 | 6.5458 | 4.7046 | 14.9425 | 37.4312 | 6.1628 | 4.4293 | 14.7687 | 34.4481 | 5.6716 | 4.0763 | 14.4855 | 32.1684 | 5.2963 | 3.8065 | 14.4144 | 29.3582 | 4.8336 | 3.474 | 13.8259 | 28.5155 | 4.6949 | 3.3743 | 13.5179 | 27.982 | 4.607 | 3.3112 | 13.1021 | 27.5498 | 4.5359 | 3.26 | 12.8908 | 26.6556 | 4.3886 | 3.1542 | 12.2951 | 23.3544 | 3.8451 | 2.7636 | 9.8386 | 21.5984 | 3.556 | 2.5558 | 5.7172 | 42.1429 | 6.9385 | 4.9868 | 2.4132 | 40.3392 | 6.6415 | 4.7734 | 0.27483 | 38.3695 | 7.1093 | 5.1096 | 16.0033 | 38.5372 | 6.9637 | 5.005 | 14.848 | 38.5438 | 7.0309 | 5.0532 | 14.6435 | 38.6066 | 6.9422 | 4.9895 | 14.366 | 38.7138 | 6.8982 | 4.9579 | 14.3124 | 38.8843 | 6.6911 | 4.809 | 13.7886 | 39.1051 | 6.5724 | 4.7237 | 13.4569 | 39.3581 | 6.5685 | 4.7209 | 13.1707 | 39.4788 | 6.4999 | 4.6716 | 12.731 | 37.8531 | 6.2322 | 4.4792 | 11.4507 | 41.6624 | 8.3212 | 5.9806 | 6.6727 | 42.9135 | 7.1838 | 5.1631 | 3.0149 | 41.2956 | 6.799 | 4.8866 | 0.55524 | 41.7173 | 6.8684 | 4.9365 | 1.5011
LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 30.976 | 13.9641 | 10.1866 | 16.7504 | 31.0799 | 13.7695 | 10.0447 | 16.4921 | 31.1061 | 13.5768 | 9.9041 | 16.4778 | 31.1581 | 13.4665 | 9.8236 | 16.3411 | 31.2309 | 13.3339 | 9.7269 | 16.4109 | 31.3205 | 13.1499 | 9.5927 | 16.2337 | 31.4184 | 13.1196 | 9.5706 | 16.0912 | 31.5141 | 13.0676 | 9.5327 | 16.0019 | 31.6096 | 12.9879 | 9.4745 | 15.9757 | 31.711 | 12.8877 | 9.4014 | 15.7694 | 32.2179 | 12.536 | 9.1448 | 15.3919 | 32.6755 | 12.685 | 9.2536 | 15.1659 | 32.96 | 13.2589 | 9.6721 | 14.9873 | 33.2105 | 13.5175 | 9.8609 | 15.0186 | 30.8643 | 14.0625 | 10.2584 | 17.1165 | 30.8754 | 13.9652 | 10.1874 | 17.1551 | 30.9267 | 13.7931 | 10.0619 | 17.0296 | 30.9839 | 13.6576 | 9.963 | 16.8245 | 31.0482 | 13.5649 | 9.8954 | 16.8446 | 31.1169 | 13.4184 | 9.7885 | 16.6622 | 31.1927 | 13.3597 | 9.7457 | 16.5022 | 31.2671 | 13.3229 | 9.7188 | 16.3865 | 31.3419 | 13.2885 | 9.6938 | 16.3249 | 31.4143 | 13.2162 | 9.641 | 16.0961 | 31.7038 | 13.0935 | 9.5515 | 15.7874 | 31.9612 | 13.2903 | 9.6951 | 15.5725 | 32.1746 | 13.7953 | 10.0634 | 15.3343 | 32.3126 | 13.8336 | 10.0915 | 15.4044 | 30.9761 | 14.0608 | 10.2571 | 16.7523 | 31.0803 | 13.9427 | 10.171 | 16.4963 | 31.1068 | 13.7826 | 10.0542 | 16.4846 | 31.1592 | 13.6232 | 9.9379 | 16.3512 | 31.2321 | 13.5273 | 9.868 | 16.4235 | 31.3215 | 13.3537 | 9.7413 | 16.25 | 31.4193 | 13.2636 | 9.6756 | 16.1111 | 31.5151 | 13.2028 | 9.6313 | 16.0251 | 31.6093 | 13.1529 | 9.5949 | 16.0034 | 31.7038 | 13.0706 | 9.5349 | 15.809 | 32.1475 | 12.9163 | 9.4223 | 15.4935 | 32.4592 | 13.2474 | 9.6638 | 15.3923 | 32.6729 | 14.0178 | 10.2258 | 15.2753 | 32.8004 | 14.1502 | 10.3223 | 15.4155 | 30.9679 | 13.9661 | 10.1881 | 16.775 | 31.0655 | 13.769 | 10.0443 | 16.5414 | 31.0885 | 13.5108 | 9.8559 | 16.5521 | 31.1394 | 13.4594 | 9.8184 | 16.4426 | 31.2145 | 13.334 | 9.727 | 16.537 | 31.3159 | 13.1859 | 9.6189 | 16.3835 | 31.4358 | 13.1245 | 9.5741 | 16.2606 | 31.5614 | 13.0393 | 9.512 | 16.1873 | 31.6918 | 12.9527 | 9.4488 | 16.1789 | 31.8293 | 12.7987 | 9.3365 | 16.0066 | 32.6132 | 12.394 | 9.0413 | 15.5021 | 33.4402 | 12.2264 | 8.919 | 14.5592 | 33.9225 | 12.4983 | 9.1173 | 13.7814 | 34.1053 | 12.6071 | 9.1967 | 13.5782 | 30.9965 | 13.9648 | 10.1871 | 16.7594 | 31.1179 | 13.828 | 10.0873 | 16.5134 | 31.1476 | 13.7967 | 10.0645 | 16.5235 | 31.2014 | 13.7319 | 10.0172 | 16.417 | 31.2799 | 13.7052 | 9.9978 | 16.5145 | 31.3857 | 13.5914 | 9.9148 | 16.3631 | 31.5182 | 13.4847 | 9.8369 | 16.2366 | 31.6553 | 13.4135 | 9.785 | 16.1595 | 31.8066 | 13.342 | 9.7328 | 16.1311 | 32.0003 | 13.1958 | 9.6261 | 15.7927 | 32.9255 | 13.4587 | 9.8179 | 14.6595 | 33.6006 | 12.9272 | 9.4302 | 13.8271 | 33.8312 | 12.6734 | 9.2451 | 13.3708 | 33.7097 | 12.6507 | 9.2285 | 13.8369
LYONS RD | BARTON | CARRINGTON | 378253 | 397241 | 30.1601 | 10.3506 | 7.5506 | 16.5592 | 30.2529 | 9.9388 | 7.2502 | 15.4827 | 30.2806 | 9.6215 | 7.0187 | 15.0674 | 30.3229 | 9.3704 | 6.8356 | 15.1422 | 30.3697 | 9.0641 | 6.6121 | 15.1907 | 30.406 | 8.7906 | 6.4126 | 14.9759 | 30.4436 | 8.8586 | 6.4622 | 14.8519 | 30.4821 | 8.8779 | 6.4763 | 14.6824 | 30.521 | 8.868 | 6.469 | 14.5111 | 30.5597 | 8.8409 | 6.4493 | 14.289 | 34.4377 | 8.1577 | 5.9509 | 10.1245 | 35.358 | 5.7354 | 4.1839 | -6.2129 | 40.7586 | 6.6114 | 4.823 | -7.3842 | 46.9197 | 7.6108 | 5.552 | -6.6591 | 30.0818 | 10.5294 | 7.6811 | 17.2585 | 30.1133 | 10.2827 | 7.5011 | 16.8171 | 30.1728 | 9.958 | 7.2642 | 16.4513 | 30.2387 | 9.5527 | 6.9686 | 16.4721 | 30.2916 | 9.4969 | 6.9279 | 16.4726 | 30.339 | 9.2914 | 6.7779 | 16.268 | 30.3909 | 9.2584 | 6.7539 | 16.1384 | 30.446 | 9.2121 | 6.7201 | 15.9213 | 30.504 | 9.1669 | 6.6871 | 15.7356 | 30.5637 | 9.1282 | 6.6589 | 15.5907 | 30.9271 | 9.0146 | 6.576 | 15.0028 | 31.4205 | 9.0984 | 6.6371 | 14.3117 | 31.9727 | 9.8577 | 7.191 | 13.5442 | 32.4118 | 10.4795 | 7.6447 | 13.2276 | 30.1604 | 10.5344 | 7.6847 | 16.5636 | 30.2539 | 10.2736 | 7.4944 | 15.4907 | 30.2825 | 9.9402 | 7.2512 | 15.0813 | 30.3262 | 9.6543 | 7.0427 | 15.1279 | 30.3754 | 9.4369 | 6.8841 | 15.1768 | 30.4133 | 9.2489 | 6.747 | 14.9514 | 30.4525 | 9.2023 | 6.713 | 14.8408 | 30.4926 | 9.1524 | 6.6766 | 14.671 | 30.5326 | 9.1085 | 6.6445 | 14.5001 | 30.5715 | 9.0688 | 6.6156 | 14.2785 | 34.328 | 8.9314 | 6.5154 | 10.2401 | 50.0416 | 9.1222 | 6.6545 | -5.7291 | 50.6389 | 10.2586 | 7.4835 | -6.7123 | 49.7693 | 11.0703 | 8.0756 | -5.6533 | 30.1543 | 10.3534 | 7.5527 | 16.5788 | 30.2414 | 9.9416 | 7.2523 | 15.523 | 30.2635 | 9.6182 | 7.0163 | 15.1284 | 30.3004 | 9.3594 | 6.8276 | 15.2235 | 30.3487 | 9.0635 | 6.6117 | 15.2888 | 30.4044 | 8.8259 | 6.4384 | 15.0814 | 30.4794 | 8.8852 | 6.4816 | 14.9514 | 30.5728 | 8.8937 | 6.4878 | 14.7635 | 30.6825 | 8.8808 | 6.4784 | 14.562 | 30.8061 | 8.8531 | 6.4582 | 14.3049 | 34.5159 | 5.5988 | 4.0843 | -6.1027 | 33.888 | 5.497 | 4.01 | -7.4113 | 38.2794 | 6.2093 | 4.5296 | -9.3039 | 44.0747 | 7.1494 | 5.2154 | -8.4966 | 30.1705 | 10.3504 | 7.5505 | 16.5625 | 30.2768 | 10.0891 | 7.3599 | 15.4814 | 30.3076 | 9.9122 | 7.2308 | 15.0752 | 30.3513 | 9.7789 | 7.1336 | 15.1322 | 30.4057 | 9.603 | 7.0052 | 15.1856 | 30.4982 | 9.4048 | 6.8607 | 14.9496 | 30.6292 | 9.3286 | 6.8051 | 14.7779 | 30.7959 | 9.368 | 6.8339 | 14.5356 | 30.986 | 9.372 | 6.8368 | 14.2701 | 35.0047 | 8.723 | 6.3633 | 9.9368 | 35.6823 | 8.5671 | 6.2496 | 8.3859 | 36.57 | 8.1653 | 5.9565 | 6.6044 | 37.0627 | 9.2134 | 6.7211 | 5.4401 | 36.949 | 9.2905 | 6.7773 | 5.9216
MANCHESTER UNIVERSITY | LONGSIGHT | BREDBURY | 384762 | 396769 | 32.938 | 10.8116 | 7.8869 | 13.3428 | 33.1072 | 9.9993 | 7.2943 | 13.0492 | 33.0773 | 9.0482 | 6.6005 | 12.9393 | 33.0911 | 8.512 | 6.2094 | 12.8918 | 33.1261 | 7.8251 | 5.7083 | 12.7374 | 33.1847 | 7.1928 | 5.2471 | 12.7487 | 33.2385 | 7.0394 | 5.1352 | 12.1428 | 33.2855 | 7.0265 | 5.1257 | 12.3116 | 33.3266 | 6.9858 | 5.0961 | 12.4186 | 33.3621 | 6.8719 | 5.0129 | 12.1922 | 33.4889 | 6.8015 | 4.9616 | 12.0397 | 33.5272 | 7.5487 | 5.5067 | 11.9104 | 33.4979 | 9.0361 | 6.5917 | 11.8527 | 33.4168 | 9.4684 | 6.9071 | 12.0843 | 32.7244 | 10.7108 | 7.8134 | 13.8301 | 32.7094 | 9.7337 | 7.1006 | 13.9492 | 32.7421 | 8.9818 | 6.5521 | 13.706 | 32.8006 | 8.2472 | 6.0162 | 13.5586 | 32.8641 | 7.5372 | 5.4983 | 13.345 | 32.9264 | 6.8918 | 5.0275 | 13.3413 | 32.9902 | 6.731 | 4.9102 | 12.73 | 33.05 | 6.7316 | 4.9106 | 12.8565 | 33.1069 | 6.7164 | 4.8995 | 12.9172 | 33.1598 | 6.6327 | 4.8385 | 12.6574 | 33.3238 | 6.5985 | 4.8135 | 12.4225 | 33.4243 | 7.0831 | 5.167 | 12.1534 | 33.438 | 7.9085 | 5.7692 | 11.9952 | 33.3659 | 8.3487 | 6.0903 | 12.1841 | 32.938 | 10.6899 | 7.7981 | 13.3429 | 33.1072 | 10.1254 | 7.3863 | 13.0504 | 33.0773 | 9.3894 | 6.8494 | 12.9416 | 33.0911 | 8.6149 | 6.2845 | 12.8945 | 33.1261 | 7.878 | 5.7469 | 12.7406 | 33.1845 | 7.2663 | 5.3007 | 12.7524 | 33.2383 | 7.0985 | 5.1783 | 12.1471 | 33.2853 | 7.069 | 5.1568 | 12.3162 | 33.3262 | 7.034 | 5.1312 | 12.4239 | 33.3609 | 6.9668 | 5.0822 | 12.2001 | 33.4841 | 6.9342 | 5.0584 | 12.0562 | 33.5193 | 7.7162 | 5.6288 | 11.9327 | 33.4884 | 9.1848 | 6.7002 | 11.8773 | 33.4066 | 9.7608 | 7.1204 | 12.1087 | 32.9216 | 10.8183 | 7.8918 | 13.3737 | 33.074 | 9.9935 | 7.2901 | 13.1132 | 33.0289 | 9.1565 | 6.6795 | 13.0372 | 33.0282 | 8.5489 | 6.2363 | 13.0234 | 33.049 | 7.8199 | 5.7045 | 12.902 | 33.0948 | 7.2274 | 5.2723 | 12.9468 | 33.1371 | 7.0725 | 5.1593 | 12.3841 | 33.1733 | 7.0519 | 5.1443 | 12.5851 | 33.2044 | 7.0267 | 5.1259 | 12.7255 | 33.23 | 6.9417 | 5.0639 | 12.5493 | 33.2632 | 6.773 | 4.9408 | 12.5165 | 33.1932 | 7.4242 | 5.4158 | 11.9966 | 33.038 | 8.694 | 6.3422 | 11.5803 | 32.8282 | 9.0236 | 6.5826 | 11.5802 | 32.9261 | 10.8185 | 7.892 | 13.3672 | 33.082 | 10.6042 | 7.7356 | 13.1 | 33.0367 | 10.3585 | 7.5564 | 13.0221 | 33.0352 | 10.2983 | 7.5125 | 13.0075 | 33.0554 | 10.1225 | 7.3842 | 12.8855 | 33.1001 | 10.0571 | 7.3365 | 12.9316 | 33.1416 | 9.8753 | 7.2039 | 12.3697 | 33.1761 | 9.8467 | 7.1831 | 12.5739 | 33.2047 | 9.8227 | 7.1655 | 12.7188 | 33.2272 | 9.6613 | 7.0478 | 12.4056 | 33.2446 | 9.3554 | 6.8246 | 11.8382 | 33.1565 | 9.1257 | 6.657 | 11.3313 | 32.9849 | 8.9829 | 6.5529 | 11.0566 | 32.761 | 9.0321 | 6.5888 | 11.5979
MARPLE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 5.7927 | 5.7927 | 5.7927 | 0.04804 | 5.8028 | 5.8028 | 5.8028 | -0.025933 | 5.816 | 5.816 | 5.816 | -0.11408 | 5.836 | 5.836 | 5.836 | -0.21444 | 5.8616 | 5.8616 | 5.8616 | -0.30271 | 5.8913 | 5.8913 | 5.8913 | -0.41448 | 5.9252 | 5.9252 | 5.9252 | -0.62726 | 5.9624 | 5.9624 | 5.9624 | -0.69997 | 6.0033 | 6.0033 | 6.0033 | -0.80644 | 6.0501 | 6.0501 | 6.0501 | -0.98932 | 6.2144 | 6.2144 | 6.2144 | -1.5277 | 6.328 | 6.328 | 6.328 | -1.7911 | 6.3941 | 6.3941 | 6.3941 | -1.8734 | 6.4318 | 6.4318 | 6.4318 | -1.7862 | 5.7977 | 5.7977 | 5.7977 | 0.082092 | 5.8135 | 5.8135 | 5.8135 | 0.028422 | 5.8351 | 5.8351 | 5.8351 | -0.077552 | 5.8596 | 5.8596 | 5.8596 | -0.18717 | 5.8886 | 5.8886 | 5.8886 | -0.25995 | 5.9218 | 5.9218 | 5.9218 | -0.36575 | 5.9594 | 5.9594 | 5.9594 | -0.57092 | 6.0007 | 6.0007 | 6.0007 | -0.6407 | 6.046 | 6.046 | 6.046 | -0.74702 | 6.0949 | 6.0949 | 6.0949 | -0.91054 | 6.1738 | 6.1738 | 6.1738 | -1.2891 | 6.2351 | 6.2351 | 6.2351 | -1.563 | 6.2763 | 6.2763 | 6.2763 | -1.7489 | 6.3062 | 6.3062 | 6.3062 | -1.823 | 5.7927 | 5.7927 | 5.7927 | 0.048189 | 5.8028 | 5.8028 | 5.8028 | -0.0078475 | 5.816 | 5.816 | 5.816 | -0.10209 | 5.836 | 5.836 | 5.836 | -0.18861 | 5.8615 | 5.8615 | 5.8615 | -0.28138 | 5.891 | 5.891 | 5.891 | -0.38802 | 5.9247 | 5.9247 | 5.9247 | -0.59424 | 5.9619 | 5.9619 | 5.9619 | -0.66303 | 6.0022 | 6.0022 | 6.0022 | -0.76267 | 6.0468 | 6.0468 | 6.0468 | -0.92863 | 6.2015 | 6.2015 | 6.2015 | -1.4159 | 6.3074 | 6.3074 | 6.3074 | -1.6473 | 6.3698 | 6.3698 | 6.3698 | -1.7192 | 6.4066 | 6.4066 | 6.4066 | -1.638 | 5.7924 | 5.7924 | 5.7924 | 0.052778 | 5.8033 | 5.8033 | 5.8033 | -0.016934 | 5.8193 | 5.8193 | 5.8193 | -0.097041 | 5.8447 | 5.8447 | 5.8447 | -0.19063 | 5.8782 | 5.8782 | 5.8782 | -0.26621 | 5.9196 | 5.9196 | 5.9196 | -0.36686 | 5.9701 | 5.9701 | 5.9701 | -0.57362 | 6.0278 | 6.0278 | 6.0278 | -0.64073 | 6.0905 | 6.0905 | 6.0905 | -0.72212 | 6.1611 | 6.1611 | 6.1611 | -0.85868 | 6.4379 | 6.4379 | 6.4379 | -1.6743 | 6.8464 | 6.8464 | 6.8464 | -3.575 | 7.1492 | 7.1492 | 7.1492 | -5.1303 | 7.2028 | 7.2028 | 7.2028 | -6.1151 | 5.7889 | 5.7889 | 5.7889 | 0.053911 | 5.7991 | 5.7991 | 5.7991 | -0.020709 | 5.8135 | 5.8135 | 5.8135 | -0.10416 | 5.8349 | 5.8349 | 5.8349 | -0.18412 | 5.8648 | 5.8648 | 5.8648 | -0.24984 | 5.9003 | 5.9003 | 5.9003 | -0.33148 | 5.9444 | 5.9444 | 5.9444 | -0.51535 | 5.9934 | 5.9934 | 5.9934 | -0.55651 | 6.0575 | 6.0575 | 6.0575 | -0.67653 | 6.175 | 6.175 | 6.175 | -1.1541 | 6.6298 | 6.6298 | 6.6298 | -3.2704 | 6.9599 | 6.9599 | 6.9599 | -4.984 | 7.0094 | 7.0094 | 7.0094 | -6.0153 | 6.9658 | 6.9658 | 6.9658 | -5.6637
MARTON | BLACKPOOL | PENWORTHAM WEST / STANAH | 333341 | 433485 | 24.451 | 8.7984 | 6.4183 | 14.2889 | 24.5278 | 8.6178 | 6.2866 | 14.0196 | 24.6073 | 8.4429 | 6.159 | 13.9065 | 24.7104 | 8.3374 | 6.082 | 13.6892 | 24.8423 | 8.2742 | 6.0359 | 13.4131 | 24.9992 | 8.2821 | 6.0417 | 13.119 | 25.182 | 8.1618 | 5.9539 | 12.7795 | 25.3809 | 8.0652 | 5.8834 | 12.4219 | 25.5945 | 7.9032 | 5.7652 | 12.0596 | 25.8366 | 7.681 | 5.6032 | 11.693 | 26.4687 | 7.2188 | 5.266 | 10.091 | 26.8758 | 6.7 | 4.8875 | 9.2699 | 27.13 | 6.8024 | 4.9623 | 9.1637 | 27.2959 | 6.7985 | 4.9594 | 9.3849 | 24.4503 | 8.8376 | 6.4469 | 14.5045 | 24.4951 | 8.8422 | 6.4503 | 14.408 | 24.5684 | 8.821 | 6.4348 | 14.1933 | 24.6527 | 8.7622 | 6.3919 | 13.927 | 24.749 | 8.6729 | 6.3267 | 13.6337 | 24.8626 | 8.5494 | 6.2367 | 13.3395 | 24.9935 | 8.4393 | 6.1563 | 12.9919 | 25.1339 | 8.3917 | 6.1216 | 12.6129 | 25.2831 | 8.3233 | 6.0718 | 12.2117 | 25.4369 | 8.2416 | 6.0122 | 11.8362 | 25.8906 | 8.076 | 5.8913 | 11.052 | 26.1911 | 7.8749 | 5.7446 | 10.5743 | 26.3749 | 7.9856 | 5.8254 | 10.2489 | 26.4803 | 7.828 | 5.7104 | 10.1121 | 24.4511 | 8.8452 | 6.4525 | 14.3064 | 24.528 | 8.8809 | 6.4785 | 14.0373 | 24.6076 | 8.9567 | 6.5338 | 13.9576 | 24.7108 | 8.8783 | 6.4766 | 13.742 | 24.8421 | 8.7247 | 6.3646 | 13.494 | 24.9979 | 8.7474 | 6.3811 | 13.1977 | 25.1798 | 8.6171 | 6.2861 | 12.8745 | 25.3781 | 8.4832 | 6.1884 | 12.5375 | 25.5883 | 8.3272 | 6.0746 | 12.1814 | 25.8156 | 8.1723 | 5.9616 | 11.8159 | 26.4179 | 7.7504 | 5.6538 | 10.3743 | 26.7426 | 7.3413 | 5.3554 | 9.6929 | 26.9549 | 7.445 | 5.431 | 9.6372 | 27.0739 | 7.3843 | 5.3868 | 9.8905 | 24.4543 | 8.8005 | 6.4198 | 14.3132 | 24.5346 | 8.6179 | 6.2866 | 14.0719 | 24.6072 | 8.7129 | 6.3559 | 13.9914 | 24.7126 | 8.5591 | 6.2437 | 13.8095 | 24.8498 | 8.463 | 6.1736 | 13.5745 | 25.0172 | 8.4661 | 6.1759 | 13.3219 | 25.2199 | 8.3605 | 6.0988 | 13.0239 | 25.4459 | 8.2265 | 6.0011 | 12.7134 | 25.6926 | 8.013 | 5.8453 | 12.392 | 25.969 | 7.8959 | 5.76 | 12.0524 | 27.0539 | 6.9161 | 5.0452 | 9.9092 | 28.0548 | 5.8254 | 4.2496 | 5.8855 | 28.5005 | 5.0091 | 3.6541 | 2.7275 | 26.4856 | 4.2962 | 3.134 | 0.14918 | 24.4769 | 8.7932 | 6.4145 | 14.2729 | 24.5805 | 8.5428 | 6.2318 | 13.9625 | 24.6582 | 8.4306 | 6.15 | 13.8913 | 24.7598 | 8.3811 | 6.1139 | 13.741 | 24.8938 | 8.3628 | 6.1005 | 13.5386 | 25.0503 | 8.2732 | 6.0352 | 13.3357 | 25.2468 | 8.0809 | 5.8949 | 13.081 | 25.4583 | 8.0262 | 5.855 | 12.7957 | 25.7005 | 7.9235 | 5.7801 | 12.4049 | 26.0991 | 7.6263 | 5.5633 | 11.4411 | 27.3965 | 6.3295 | 4.6173 | 6.9204 | 27.9557 | 5.0003 | 3.6477 | 3.0773 | 26.6641 | 4.3252 | 3.1552 | 0.66842 | 26.7679 | 4.342 | 3.1674 | 1.1808
MARYPORT | STAINBURN & SIDDICK | HARKER / HUTTON | 303716 | 535313 | 29.1836 | 17.2989 | 12.4331 | 17.7409 | 29.2295 | 17.229 | 12.3829 | 17.5146 | 29.2767 | 17.1216 | 12.3056 | 17.2178 | 29.3441 | 16.9602 | 12.1896 | 16.7535 | 29.4317 | 16.8175 | 12.0871 | 16.4189 | 29.5355 | 16.621 | 11.9458 | 15.8881 | 29.6583 | 16.4243 | 11.8045 | 15.2981 | 29.7953 | 16.2313 | 11.6658 | 14.7318 | 29.9396 | 16.0418 | 11.5296 | 14.2076 | 30.1101 | 15.818 | 11.3687 | 13.4909 | 30.7601 | 14.913 | 10.7183 | 10.8864 | 31.2229 | 14.2449 | 10.2381 | 9.6015 | 31.4971 | 13.6582 | 9.8164 | 9.3883 | 31.7062 | 13.1779 | 9.4712 | 9.8019 | 29.1885 | 17.3127 | 12.443 | 17.7879 | 29.2369 | 17.2749 | 12.4158 | 17.603 | 29.3075 | 17.1959 | 12.359 | 17.2811 | 29.368 | 17.0856 | 12.2797 | 16.9321 | 29.4465 | 16.9957 | 12.2151 | 16.7237 | 29.5356 | 16.8656 | 12.1217 | 16.3217 | 29.6372 | 16.7292 | 12.0236 | 15.8672 | 29.7472 | 16.6001 | 11.9308 | 15.4343 | 29.8641 | 16.4733 | 11.8397 | 14.9902 | 29.9744 | 16.3425 | 11.7457 | 14.5174 | 30.2475 | 15.8493 | 11.3912 | 13.0757 | 30.4892 | 15.3848 | 11.0574 | 12.0752 | 30.6818 | 14.8319 | 10.66 | 11.5059 | 30.8335 | 14.6631 | 10.5386 | 11.1688 | 29.1836 | 17.3122 | 12.4426 | 17.7471 | 29.2297 | 17.2675 | 12.4105 | 17.5335 | 29.277 | 17.1619 | 12.3346 | 17.2523 | 29.3447 | 17.0023 | 12.2199 | 16.8108 | 29.4321 | 16.8609 | 12.1183 | 16.4982 | 29.5356 | 16.6406 | 11.9599 | 15.9933 | 29.658 | 16.4017 | 11.7882 | 15.4298 | 29.7948 | 16.1388 | 11.5993 | 14.8887 | 29.9374 | 15.9495 | 11.4632 | 14.3912 | 30.1003 | 15.7027 | 11.2858 | 13.7439 | 30.7053 | 14.8211 | 10.6522 | 11.3982 | 31.0902 | 14.5985 | 10.4922 | 10.2965 | 31.3244 | 14.5575 | 10.4627 | 10.1332 | 31.4752 | 14.3028 | 10.2797 | 10.5336 | 29.1839 | 17.2966 | 12.4314 | 17.7439 | 29.2342 | 17.2143 | 12.3722 | 17.4886 | 29.2934 | 17.079 | 12.275 | 17.1623 | 29.3828 | 16.8925 | 12.1409 | 16.6906 | 29.5066 | 16.7221 | 12.0185 | 16.3474 | 29.6646 | 16.4884 | 11.8506 | 15.782 | 29.8644 | 16.2425 | 11.6738 | 15.1199 | 30.0988 | 15.9937 | 11.495 | 14.4676 | 30.3144 | 15.7564 | 11.3244 | 13.9329 | 30.543 | 15.5022 | 11.1418 | 13.3584 | 31.3575 | 14.3267 | 10.2969 | 10.6337 | 32.0869 | 12.775 | 9.1816 | 6.0604 | 32.4964 | 11.2778 | 8.1056 | 3.159 | 32.7355 | 10.521 | 7.5616 | 0.90128 | 29.1755 | 17.3017 | 12.4351 | 17.7647 | 29.22 | 17.2327 | 12.3855 | 17.4848 | 29.2814 | 17.0944 | 12.2861 | 17.1393 | 29.3682 | 16.9046 | 12.1496 | 16.6666 | 29.4876 | 16.7353 | 12.028 | 16.3437 | 29.6358 | 16.5104 | 11.8664 | 15.8416 | 29.8292 | 16.2748 | 11.697 | 15.2723 | 30.0244 | 16.0478 | 11.5339 | 14.7537 | 30.207 | 15.829 | 11.3766 | 14.3077 | 30.4447 | 15.487 | 11.1308 | 13.1679 | 31.3178 | 13.9332 | 10.0141 | 7.8585 | 31.8729 | 12.4926 | 8.9787 | 4.1976 | 32.0701 | 11.3787 | 8.1781 | 2.407 | 32.0326 | 11.1661 | 8.0253 | 3.1379
MELLING | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 360144 | 471643 | 6.6234 | 6.6234 | 6.6234 | 3.4263 | 6.6565 | 6.6565 | 6.6565 | 3.3423 | 6.6981 | 6.6981 | 6.6981 | 3.2563 | 6.743 | 6.743 | 6.743 | 3.1459 | 6.7948 | 6.7948 | 6.7948 | 3.0715 | 6.841 | 6.841 | 6.841 | 2.9611 | 6.8794 | 6.8794 | 6.8794 | 2.824 | 6.9215 | 6.9215 | 6.9215 | 2.6838 | 6.9672 | 6.9672 | 6.9672 | 2.5426 | 7.0097 | 7.0097 | 7.0097 | 2.3437 | 7.1535 | 7.1535 | 7.1535 | 1.708 | 7.2481 | 7.2481 | 7.2481 | 1.4289 | 7.2981 | 7.2981 | 7.2981 | 1.3538 | 7.32 | 7.32 | 7.32 | 1.4828 | 6.6241 | 6.6241 | 6.6241 | 3.4497 | 6.6574 | 6.6574 | 6.6574 | 3.3875 | 6.6998 | 6.6998 | 6.6998 | 3.2946 | 6.74 | 6.74 | 6.74 | 3.2013 | 6.7805 | 6.7805 | 6.7805 | 3.1485 | 6.8263 | 6.8263 | 6.8263 | 3.0424 | 6.8775 | 6.8775 | 6.8775 | 2.9202 | 6.9129 | 6.9129 | 6.9129 | 2.8021 | 6.9507 | 6.9507 | 6.9507 | 2.6775 | 6.9905 | 6.9905 | 6.9905 | 2.5339 | 7.0795 | 7.0795 | 7.0795 | 2.1489 | 7.1484 | 7.1484 | 7.1484 | 1.7846 | 7.1913 | 7.1913 | 7.1913 | 1.5091 | 7.2079 | 7.2079 | 7.2079 | 1.3591 | 6.6234 | 6.6234 | 6.6234 | 3.4284 | 6.6565 | 6.6565 | 6.6565 | 3.3483 | 6.6981 | 6.6981 | 6.6981 | 3.2666 | 6.743 | 6.743 | 6.743 | 3.1559 | 6.7945 | 6.7945 | 6.7945 | 3.0895 | 6.8407 | 6.8407 | 6.8407 | 2.9836 | 6.8789 | 6.8789 | 6.8789 | 2.8474 | 6.9209 | 6.9209 | 6.9209 | 2.715 | 6.966 | 6.966 | 6.966 | 2.5811 | 7.0069 | 7.0069 | 7.0069 | 2.398 | 7.1421 | 7.1421 | 7.1421 | 1.8231 | 7.2297 | 7.2297 | 7.2297 | 1.5735 | 7.2762 | 7.2762 | 7.2762 | 1.486 | 7.2972 | 7.2972 | 7.2972 | 1.6004 | 6.6241 | 6.6241 | 6.6241 | 3.4291 | 6.6616 | 6.6616 | 6.6616 | 3.3427 | 6.7136 | 6.7136 | 6.7136 | 3.2571 | 6.7743 | 6.7743 | 6.7743 | 3.1501 | 6.8321 | 6.8321 | 6.8321 | 3.0741 | 6.8794 | 6.8794 | 6.8794 | 2.9561 | 6.9335 | 6.9335 | 6.9335 | 2.8117 | 6.9827 | 6.9827 | 6.9827 | 2.6732 | 7.037 | 7.037 | 7.037 | 2.5532 | 7.0975 | 7.0975 | 7.0975 | 2.4201 | 7.2796 | 7.2796 | 7.2796 | 1.8975 | 7.3908 | 7.3908 | 7.3908 | 1.4187 | 7.4308 | 7.4308 | 7.4308 | 1.2244 | 7.4438 | 7.4438 | 7.4438 | 1.1373 | 6.6365 | 6.6365 | 6.6365 | 3.4096 | 6.6935 | 6.6935 | 6.6935 | 3.3002 | 6.7491 | 6.7491 | 6.7491 | 3.2158 | 6.7925 | 6.7925 | 6.7925 | 3.1149 | 6.8259 | 6.8259 | 6.8259 | 3.0412 | 6.8669 | 6.8669 | 6.8669 | 2.9374 | 6.9188 | 6.9188 | 6.9188 | 2.8096 | 6.9614 | 6.9614 | 6.9614 | 2.6914 | 7.0076 | 7.0076 | 7.0076 | 2.5898 | 7.0607 | 7.0607 | 7.0607 | 2.4081 | 7.2167 | 7.2167 | 7.2167 | 1.6673 | 7.2841 | 7.2841 | 7.2841 | 1.2921 | 7.2845 | 7.2845 | 7.2845 | 1.2096 | 7.2588 | 7.2588 | 7.2588 | 1.3977
MERESIDE | PEEL | PENWORTHAM WEST / STANAH | 334431 | 434843 | 29.9582 | 13.9745 | 10.1942 | 18.727 | 30.0034 | 13.8619 | 10.1121 | 18.5503 | 30.0146 | 13.6127 | 9.9303 | 18.4785 | 30.0437 | 13.6188 | 9.9347 | 18.3338 | 30.0836 | 13.5387 | 9.8763 | 18.2014 | 30.1351 | 13.5799 | 9.9064 | 18.0539 | 30.1925 | 13.4921 | 9.8423 | 17.8576 | 30.2525 | 13.3752 | 9.757 | 17.6541 | 30.3146 | 13.334 | 9.7269 | 17.4852 | 30.3836 | 13.2596 | 9.6727 | 17.2513 | 30.6744 | 12.8536 | 9.3765 | 16.4864 | 30.9354 | 12.7705 | 9.3159 | 16.0284 | 31.1041 | 15.4622 | 11.2795 | 15.8714 | 31.2435 | 18.254 | 13.316 | 15.8593 | 29.9176 | 13.997 | 10.2106 | 18.8944 | 29.9331 | 13.9886 | 10.2045 | 18.8548 | 29.9672 | 13.9616 | 10.1848 | 18.712 | 30.0111 | 13.8972 | 10.1378 | 18.5394 | 30.0614 | 13.8327 | 10.0908 | 18.3972 | 30.1175 | 13.7695 | 10.0447 | 18.2565 | 30.1802 | 13.7073 | 9.9993 | 18.0621 | 30.2468 | 13.6528 | 9.9596 | 17.8554 | 30.3179 | 13.5933 | 9.9161 | 17.6704 | 30.3927 | 13.5231 | 9.8649 | 17.4436 | 30.5451 | 13.2429 | 9.6605 | 16.9684 | 30.6821 | 13.2973 | 9.7002 | 16.6255 | 30.7928 | 15.478 | 11.291 | 16.4381 | 30.8696 | 17.648 | 12.8739 | 16.3528 | 29.9583 | 13.9962 | 10.21 | 18.7335 | 30.0035 | 13.932 | 10.1632 | 18.565 | 30.0149 | 13.7422 | 10.0248 | 18.5026 | 30.0441 | 13.6149 | 9.9319 | 18.3674 | 30.0841 | 13.4796 | 9.8332 | 18.245 | 30.1355 | 13.3682 | 9.7519 | 18.1075 | 30.1928 | 13.2564 | 9.6703 | 17.9219 | 30.2529 | 13.1934 | 9.6244 | 17.7291 | 30.3143 | 13.13 | 9.5782 | 17.572 | 30.3803 | 13.0813 | 9.5426 | 17.3638 | 30.6433 | 12.8867 | 9.4007 | 16.6779 | 30.8434 | 12.7832 | 9.3252 | 16.2602 | 30.9815 | 15.472 | 11.2866 | 16.115 | 31.071 | 18.2167 | 13.2889 | 16.1633 | 29.9547 | 13.9753 | 10.1948 | 18.7396 | 29.9983 | 13.8553 | 10.1073 | 18.5725 | 30.0112 | 13.9792 | 10.1976 | 18.5084 | 30.0458 | 13.9686 | 10.1899 | 18.3712 | 30.0959 | 13.9024 | 10.1416 | 18.2423 | 30.1656 | 13.7438 | 10.0259 | 18.0897 | 30.2511 | 13.6839 | 9.9822 | 17.8748 | 30.347 | 13.6123 | 9.93 | 17.6452 | 30.45 | 13.5454 | 9.8812 | 17.4595 | 30.5638 | 13.4707 | 9.8267 | 17.2306 | 31.0238 | 13.1285 | 9.5771 | 16.275 | 31.5126 | 12.7531 | 9.3032 | 14.4924 | 31.789 | 15.042 | 10.9729 | 13.161 | 31.9177 | 17.4375 | 12.7204 | 12.1032 | 29.9539 | 13.9734 | 10.1934 | 18.7287 | 29.9992 | 13.847 | 10.1012 | 18.5459 | 30.0101 | 13.5547 | 9.888 | 18.485 | 30.0413 | 13.6619 | 9.9661 | 18.3602 | 30.0886 | 13.5741 | 9.9021 | 18.2444 | 30.1532 | 13.5403 | 9.8775 | 18.1134 | 30.2363 | 13.3904 | 9.7681 | 17.9213 | 30.3278 | 13.269 | 9.6796 | 17.7232 | 30.4291 | 13.1512 | 9.5937 | 17.5533 | 30.5662 | 12.9937 | 9.4787 | 17.1248 | 31.1114 | 12.5559 | 9.1594 | 15.2492 | 31.4978 | 12.5665 | 9.1671 | 13.5962 | 31.6358 | 17.6099 | 12.8462 | 12.6964 | 31.5745 | 17.5823 | 12.8261 | 12.9541
MIDDLETON JUNCTION | CHADDERTON | WHITEGATE | 388606 | 405292 | 31.2485 | 12.8346 | 9.2245 | 11.1467 | 31.3079 | 10.7026 | 7.6922 | 10.2185 | 31.3373 | 8.6498 | 6.2168 | 10.044 | 31.3919 | 6.5394 | 4.7 | 9.6946 | 26.3671 | 4.3411 | 3.1201 | 9.5019 | 14.398 | 2.3705 | 1.7037 | 9.0988 | 13.926 | 2.2928 | 1.6479 | 8.8444 | 13.1754 | 2.1692 | 1.5591 | 8.4408 | 12.201 | 2.0088 | 1.4438 | 7.9309 | 10.9003 | 1.7946 | 1.2898 | 7.455 | 10.4821 | 1.7258 | 1.2404 | 5.6492 | 28.2213 | 4.6464 | 3.3395 | 4.5543 | 33.6465 | 9.5629 | 6.873 | 4.0745 | 34.0779 | 10.7065 | 7.695 | 3.9314 | 31.2013 | 13.0086 | 9.3496 | 11.5476 | 31.2304 | 10.9156 | 7.8453 | 11.0016 | 31.2858 | 8.8623 | 6.3695 | 10.8045 | 31.3502 | 6.8046 | 4.8906 | 10.4343 | 29.1296 | 4.796 | 3.447 | 10.2424 | 16.8464 | 2.7736 | 1.9935 | 9.8631 | 16.3751 | 2.696 | 1.9377 | 9.6191 | 15.7013 | 2.5851 | 1.858 | 9.2344 | 14.8659 | 2.4475 | 1.7591 | 8.7455 | 14.0174 | 2.3079 | 1.6587 | 8.3507 | 14.5995 | 2.4037 | 1.7276 | 6.972 | 26.1373 | 4.3033 | 3.0929 | 5.8778 | 32.9578 | 7.3899 | 5.3113 | 5.1185 | 33.231 | 8.0035 | 5.7523 | 4.5712 | 31.2486 | 13.0051 | 9.347 | 11.1545 | 31.3083 | 10.8796 | 7.8194 | 10.2498 | 31.338 | 8.7657 | 6.3001 | 10.0781 | 31.3932 | 6.6183 | 4.7567 | 9.74 | 28.6853 | 4.7228 | 3.3944 | 9.5608 | 16.4029 | 2.7006 | 1.941 | 9.1727 | 16.0087 | 2.6357 | 1.8943 | 8.9313 | 15.3775 | 2.5318 | 1.8196 | 8.5545 | 14.6097 | 2.4054 | 1.7288 | 8.0671 | 13.9253 | 2.2927 | 1.6478 | 7.6357 | 14.0172 | 2.3078 | 1.6587 | 6.0117 | 32.6044 | 5.3681 | 3.8581 | 5.0998 | 33.3476 | 10.4287 | 7.4953 | 4.6978 | 33.6437 | 11.3809 | 8.1796 | 4.6288 | 31.2445 | 12.8341 | 9.2241 | 11.1621 | 31.3029 | 10.7136 | 7.7001 | 10.2528 | 31.3377 | 8.6302 | 6.2027 | 10.0972 | 31.4015 | 6.5099 | 4.6788 | 9.7697 | 26.751 | 4.4043 | 3.1655 | 9.6152 | 14.3155 | 2.3569 | 1.694 | 9.2495 | 13.665 | 2.2498 | 1.617 | 9.0059 | 12.6666 | 2.0855 | 1.4989 | 8.6288 | 10.8339 | 1.7837 | 1.282 | 8.2022 | 10.7789 | 1.7747 | 1.2755 | 7.8442 | 8.6755 | 1.4284 | 1.0266 | 5.381 | 20.7708 | 3.4198 | 2.4578 | 0.1932 | 34.9498 | 7.5871 | 5.453 | -3.9576 | 35.2869 | 8.0096 | 5.7567 | -7.1033 | 31.2332 | 12.8415 | 9.2294 | 11.1966 | 31.2883 | 10.7963 | 7.7595 | 10.2795 | 31.3236 | 8.8061 | 6.3291 | 10.1302 | 31.3875 | 6.6511 | 4.7803 | 9.8586 | 28.2922 | 4.6581 | 3.3479 | 9.712 | 14.7263 | 2.4246 | 1.7426 | 9.3628 | 15.2346 | 2.5083 | 1.8027 | 9.1689 | 15.5459 | 2.5595 | 1.8396 | 8.829 | 15.9526 | 2.6265 | 1.8877 | 8.273 | 16.192 | 2.6659 | 1.916 | 7.0861 | 33.4719 | 10.5491 | 7.5818 | 1.4364 | 34.3193 | 9.2964 | 6.6815 | -3.2822 | 34.6876 | 8.4993 | 6.1086 | -6.2757 | 34.6893 | 8.4263 | 6.0561 | -5.8774
MIDWAY | EGREMONT | HARKER / HUTTON | 304525 | 501993 | 18.2185 | 18.2185 | 18.2185 | 11.4041 | 18.2601 | 18.2601 | 18.2601 | 11.1931 | 18.2875 | 18.2875 | 18.2875 | 11.0919 | 18.3323 | 18.3323 | 18.241 | 10.8864 | 18.3912 | 18.3912 | 17.7518 | 10.7357 | 18.4653 | 18.4653 | 18.4653 | 10.452 | 18.5532 | 18.5532 | 18.5532 | 10.167 | 18.6512 | 18.6512 | 18.5397 | 10.0058 | 18.7571 | 18.7571 | 18.4211 | 9.6929 | 18.8645 | 18.8645 | 18.296 | 9.361 | 19.3011 | 19.3011 | 17.9999 | 8.1249 | 19.6804 | 19.6804 | 17.7908 | 7.5079 | 19.9179 | 19.9179 | 17.6406 | 7.3295 | 20.0578 | 20.0578 | 17.5442 | 7.6447 | 18.203 | 18.203 | 18.203 | 11.4691 | 18.2355 | 18.2355 | 18.2355 | 11.3305 | 18.2895 | 18.2895 | 18.2895 | 11.2111 | 18.3511 | 18.3511 | 18.3511 | 11.0481 | 18.4216 | 18.4216 | 18.4216 | 10.9391 | 18.5031 | 18.5031 | 18.5031 | 10.7222 | 18.5968 | 18.5968 | 18.5968 | 10.4834 | 18.7009 | 18.7009 | 18.7009 | 10.3142 | 18.8134 | 18.8134 | 18.6693 | 10.0257 | 18.8943 | 18.8943 | 18.6239 | 9.7398 | 19.1293 | 19.1293 | 18.1035 | 9.2448 | 19.3398 | 19.3398 | 18.4259 | 8.6256 | 19.4666 | 19.4666 | 18.3821 | 8.153 | 19.5321 | 19.5321 | 18.3244 | 7.9326 | 18.2195 | 18.2195 | 18.2195 | 11.4089 | 18.2615 | 18.2615 | 18.2615 | 11.2008 | 18.2892 | 18.2892 | 18.2892 | 11.1156 | 18.3342 | 18.3342 | 18.3342 | 10.917 | 18.3929 | 18.3929 | 18.3929 | 10.7759 | 18.4661 | 18.4661 | 18.4661 | 10.5041 | 18.5526 | 18.5526 | 18.5526 | 10.2301 | 18.6489 | 18.6489 | 18.4124 | 10.076 | 18.7516 | 18.7516 | 18.2314 | 9.7811 | 18.8536 | 18.8536 | 18.0408 | 9.4887 | 19.2511 | 19.2511 | 17.8402 | 8.3979 | 19.5528 | 19.5528 | 17.6164 | 7.8991 | 19.7313 | 19.7313 | 17.3853 | 7.7917 | 19.8324 | 19.8324 | 17.1967 | 8.119 | 18.2176 | 18.2176 | 18.2176 | 11.4081 | 18.2603 | 18.2603 | 18.2603 | 11.1866 | 18.2952 | 18.2952 | 18.2952 | 11.0764 | 18.3553 | 18.3553 | 18.3553 | 10.8716 | 18.4396 | 18.4396 | 18.4396 | 10.7082 | 18.5518 | 18.5518 | 18.5518 | 10.4003 | 18.6895 | 18.6895 | 18.5933 | 10.073 | 18.8298 | 18.8298 | 18.4829 | 9.8644 | 18.9866 | 18.9866 | 18.3546 | 9.5635 | 19.1634 | 19.1634 | 18.2296 | 9.3287 | 19.8149 | 19.8149 | 17.8856 | 8.1877 | 20.2771 | 20.2771 | 17.5072 | 6.7252 | 20.4771 | 20.4771 | 17.2273 | 5.942 | 20.5407 | 20.5407 | 17.006 | 5.444 | 18.2161 | 18.2161 | 18.2161 | 11.3959 | 18.2647 | 18.2647 | 18.2647 | 11.1339 | 18.3025 | 18.3025 | 18.3025 | 11.0256 | 18.3617 | 18.3617 | 18.3617 | 10.8093 | 18.4445 | 18.4445 | 18.4445 | 10.6387 | 18.5533 | 18.5533 | 18.5533 | 10.3459 | 18.6793 | 18.6793 | 18.5799 | 10.0524 | 18.8146 | 18.8146 | 18.4706 | 9.904 | 18.9639 | 18.9639 | 18.3438 | 9.6394 | 19.138 | 19.138 | 18.1979 | 9.2509 | 19.741 | 19.741 | 17.7684 | 7.4075 | 20.1361 | 20.1361 | 17.3868 | 6.2754 | 20.2051 | 20.2051 | 17.1727 | 5.8491 | 20.1474 | 20.1474 | 17.0743 | 6.2776
MILNROW | CASTLETON | ROCHDALE | 392351 | 413056 | 29.3048 | 10.7856 | 7.8679 | 15.7942 | 29.3443 | 10.4284 | 7.6073 | 15.6771 | 29.382 | 9.9656 | 7.2698 | 15.486 | 29.4422 | 10.0376 | 7.3223 | 15.3255 | 29.5213 | 10.0668 | 7.3436 | 15.0268 | 29.6161 | 9.9546 | 7.2617 | 14.7822 | 29.7248 | 9.8669 | 7.1978 | 14.3571 | 29.8446 | 9.7963 | 7.1463 | 14.0189 | 29.9745 | 9.7231 | 7.0929 | 13.7689 | 30.1186 | 9.5866 | 6.9933 | 13.3362 | 30.7466 | 9.1881 | 6.7026 | 11.8415 | 31.317 | 8.9147 | 6.5032 | 10.8812 | 31.728 | 8.885 | 6.4815 | 10.4098 | 32.0914 | 8.8405 | 6.449 | 10.2887 | 29.3024 | 10.8389 | 7.9068 | 15.8901 | 29.3427 | 10.8001 | 7.8785 | 15.8498 | 29.4025 | 10.7024 | 7.8072 | 15.5855 | 29.4746 | 10.569 | 7.7099 | 15.4034 | 29.5575 | 10.3748 | 7.5683 | 15.1043 | 29.6509 | 10.2254 | 7.4593 | 14.8679 | 29.7556 | 10.1492 | 7.4037 | 14.4475 | 29.8698 | 10.0961 | 7.365 | 14.1125 | 29.9934 | 10.0501 | 7.3314 | 13.8648 | 30.1257 | 9.9771 | 7.2782 | 13.4969 | 30.4233 | 9.7024 | 7.0778 | 12.3975 | 30.699 | 9.5322 | 6.9536 | 11.4504 | 30.9451 | 9.5589 | 6.9731 | 10.7658 | 31.1536 | 9.541 | 6.96 | 10.2752 | 29.3049 | 10.8404 | 7.9079 | 15.8057 | 29.3445 | 10.8222 | 7.8947 | 15.7002 | 29.3824 | 10.7027 | 7.8074 | 15.5223 | 29.4429 | 10.5221 | 7.6757 | 15.3713 | 29.522 | 10.2819 | 7.5005 | 15.0873 | 29.6165 | 10.1843 | 7.4293 | 14.8568 | 29.725 | 10.0912 | 7.3614 | 14.448 | 29.8448 | 10.003 | 7.297 | 14.1247 | 29.9733 | 9.9334 | 7.2463 | 13.8938 | 30.1108 | 9.8289 | 7.1701 | 13.5029 | 30.6857 | 9.4619 | 6.9023 | 12.172 | 31.1511 | 9.2852 | 6.7734 | 11.3638 | 31.5078 | 9.3809 | 6.8432 | 10.9652 | 31.7897 | 9.2595 | 6.7547 | 10.8902 | 29.3036 | 10.7846 | 7.8672 | 15.8001 | 29.3451 | 10.3642 | 7.5605 | 15.6902 | 29.394 | 10.0208 | 7.31 | 15.5074 | 29.4757 | 10.1867 | 7.4311 | 15.3508 | 29.588 | 10.1074 | 7.3732 | 15.0722 | 29.732 | 9.9813 | 7.2812 | 14.8421 | 29.9094 | 9.8877 | 7.2129 | 14.3998 | 30.115 | 9.7896 | 7.1414 | 14.0422 | 30.3454 | 9.6765 | 7.0589 | 13.8227 | 30.6035 | 9.5372 | 6.9573 | 13.4818 | 31.6026 | 8.9224 | 6.5087 | 11.4184 | 32.5036 | 7.8981 | 5.7615 | 7.0319 | 33.0504 | 7.2584 | 5.2949 | 3.561 | 33.3322 | 6.7479 | 4.9225 | 1.1789 | 29.2935 | 10.8026 | 7.8803 | 15.8321 | 29.3352 | 10.598 | 7.7311 | 15.7331 | 29.3857 | 10.2056 | 7.4448 | 15.564 | 29.4619 | 10.3599 | 7.5574 | 15.4353 | 29.5687 | 10.4874 | 7.6504 | 15.1669 | 29.7038 | 10.451 | 7.6239 | 14.9655 | 29.8767 | 10.3434 | 7.5453 | 14.5723 | 30.0731 | 10.2531 | 7.4795 | 14.2681 | 30.2972 | 10.1471 | 7.4022 | 13.978 | 30.5713 | 9.9233 | 7.2389 | 12.9219 | 31.5907 | 8.7531 | 6.3853 | 8.0832 | 32.2898 | 7.6906 | 5.6102 | 4.1033 | 32.5724 | 7.1481 | 5.2144 | 1.7475 | 32.5798 | 7.0131 | 5.1159 | 2.2091
MINTSFEET | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351827 | 494315 | 19.3621 | 3.1878 | 2.2912 | 7.8276 | 18.0089 | 2.965 | 2.131 | 7.1086 | 17.141 | 2.8221 | 2.0283 | 7.2 | 15.5599 | 2.5618 | 1.8412 | 6.7956 | 14.473 | 2.3829 | 1.7126 | 6.7834 | 12.8524 | 2.116 | 1.5208 | 6.2996 | 11.1026 | 1.828 | 1.3138 | 5.8708 | 10.4137 | 1.7145 | 1.2323 | 5.7237 | 8.7719 | 1.4442 | 1.038 | 4.841 | 7.2927 | 1.2007 | 0.86296 | 4.3273 | 2.4642 | 0.40571 | 0.29159 | 1.7727 | 2.6844 | 0.44197 | 0.31765 | -3.5387 | 14.8603 | 2.4466 | 1.7584 | -7.0862 | 32.7124 | 6.2996 | 4.5276 | -6.8987 | 19.7913 | 3.2585 | 2.3419 | 8.1799 | 19.0604 | 3.1381 | 2.2554 | 7.6536 | 18.7047 | 3.0796 | 2.2134 | 7.6271 | 17.7608 | 2.9242 | 2.1017 | 7.1806 | 17.1898 | 2.8302 | 2.0341 | 7.1042 | 16.1836 | 2.6645 | 1.915 | 6.6543 | 15.7049 | 2.5857 | 1.8584 | 6.2011 | 15.0553 | 2.4787 | 1.7815 | 5.7191 | 14.2233 | 2.3418 | 1.6831 | 5.2136 | 12.9757 | 2.1363 | 1.5354 | 4.6652 | 11.3274 | 1.865 | 1.3404 | 3.1359 | 9.614 | 1.5829 | 1.1376 | 1.9934 | 24.1211 | 4.4055 | 3.1663 | 1.0595 | 24.5004 | 7.2532 | 5.213 | 0.35931 | 19.7597 | 3.2533 | 2.3382 | 7.9242 | 18.9366 | 3.1178 | 2.2408 | 7.145 | 18.4012 | 3.0296 | 2.1774 | 7.2553 | 16.9075 | 2.7837 | 2.0007 | 6.8721 | 16.7621 | 2.7598 | 1.9835 | 6.8731 | 15.6484 | 2.5764 | 1.8517 | 6.4111 | 15.1898 | 2.5009 | 1.7974 | 6.001 | 14.1775 | 2.3342 | 1.6776 | 5.7946 | 13.028 | 2.145 | 1.5416 | 4.9135 | 12.3316 | 2.0303 | 1.4592 | 4.4797 | 8.7836 | 1.4462 | 1.0394 | 2.298 | 6.2059 | 1.0218 | 0.73435 | -2.7261 | 27.3508 | 4.5031 | 3.2365 | -6.2596 | 32.0209 | 8.0757 | 5.8042 | -5.8784 | 19.3768 | 3.1902 | 2.2929 | 7.8577 | 16.7657 | 2.7604 | 1.9839 | 7.1208 | 15.7088 | 2.5863 | 1.8589 | 7.2091 | 14.0361 | 2.3109 | 1.6609 | 6.791 | 12.8902 | 2.1223 | 1.5253 | 6.7359 | 11.3303 | 1.8654 | 1.3407 | 6.2013 | 9.8775 | 1.6262 | 1.1688 | 5.6677 | 8.3451 | 1.3739 | 0.98748 | 5.4004 | 7.0289 | 1.1573 | 0.83174 | 4.4158 | 5.2078 | 0.85743 | 0.61625 | 3.6295 | 2.6844 | 0.44197 | 0.31765 | -8.902 | 2.6844 | 0.44197 | 0.31765 | -13.7277 | 0.3404 | 0.056045 | 0.04028 | -16.5569 | 20.9121 | 3.443 | 2.4746 | -18.2591 | 19.3698 | 3.1891 | 2.2921 | 7.8469 | 17.8883 | 2.9452 | 2.1168 | 7.086 | 16.7367 | 2.7556 | 1.9805 | 7.1791 | 14.8084 | 2.4381 | 1.7523 | 6.783 | 13.352 | 2.1983 | 1.58 | 6.7265 | 6.4189 | 1.0568 | 0.75956 | 1.4272 | 5.22 | 0.85944 | 0.61769 | 1.2233 | 3.9267 | 0.64651 | 0.46466 | 0.88523 | 1.8707 | 0.308 | 0.22137 | 0.11328 | 0.5205 | 0.085697 | 0.061592 | -0.68144 | 2.6844 | 0.44197 | 0.31765 | -6.7882 | 2.6844 | 0.44197 | 0.31765 | -10.8649 | 27.4515 | 4.5197 | 3.2484 | -12.869 | 27.0845 | 4.4592 | 3.205 | -11.9607
MONSALL | STUART ST | STALYBRIDGE | 386332 | 401003 | 16.9952 | 8.2637 | 6.0283 | 16.3044 | 16.9993 | 7.811 | 5.698 | 16.1142 | 17.0057 | 7.3333 | 5.3496 | 16.0822 | 17.0126 | 6.8165 | 4.9725 | 16.0491 | 17.0201 | 6.3076 | 4.6013 | 16.0406 | 17.0284 | 5.8288 | 4.252 | 16.0173 | 17.0372 | 5.7854 | 4.2204 | 15.9615 | 17.0464 | 5.7497 | 4.1944 | 15.9466 | 17.0558 | 5.6886 | 4.1497 | 15.9047 | 17.0674 | 5.4902 | 4.005 | 15.9002 | 17.1127 | 5.4224 | 3.9556 | 15.7741 | 17.1425 | 5.4626 | 3.9849 | 15.7878 | 17.1592 | 5.4237 | 3.9565 | 15.8108 | 17.1646 | 5.4137 | 3.9492 | 15.8765 | 16.9962 | 8.2641 | 6.0286 | 16.4892 | 17.0002 | 8.1614 | 5.9537 | 16.4606 | 17.0058 | 8.0155 | 5.8472 | 16.4094 | 17.0107 | 7.8073 | 5.6953 | 16.3499 | 17.0158 | 7.6768 | 5.6001 | 16.3226 | 17.0219 | 7.5089 | 5.4776 | 16.2954 | 17.0285 | 7.3909 | 5.3916 | 16.234 | 17.0352 | 7.3291 | 5.3465 | 16.2091 | 17.0421 | 7.2511 | 5.2896 | 16.1572 | 17.0492 | 7.2962 | 5.3225 | 16.1406 | 17.0742 | 7.2475 | 5.2869 | 15.9902 | 17.0952 | 7.1856 | 5.2418 | 15.9554 | 17.1108 | 7.3988 | 5.3973 | 15.9425 | 17.1227 | 7.4402 | 5.4275 | 15.9912 | 16.9952 | 8.2637 | 6.0282 | 16.3044 | 16.9993 | 7.8007 | 5.6905 | 16.1143 | 17.0057 | 7.2598 | 5.2959 | 16.0824 | 17.0126 | 6.7206 | 4.9026 | 16.0493 | 17.02 | 6.1392 | 4.4784 | 16.041 | 17.0283 | 5.6036 | 4.0877 | 16.0178 | 17.0371 | 5.5633 | 4.0583 | 15.9622 | 17.0462 | 5.5216 | 4.028 | 15.9474 | 17.0555 | 5.4535 | 3.9783 | 15.9057 | 17.0666 | 5.3873 | 3.93 | 15.9019 | 17.11 | 5.4187 | 3.9528 | 15.7778 | 17.1385 | 5.3873 | 3.9299 | 15.7926 | 17.1551 | 5.5844 | 4.0737 | 15.8159 | 17.1607 | 5.5686 | 4.0622 | 15.8814 | 16.9964 | 8.2648 | 6.0291 | 16.3143 | 17.0019 | 7.8167 | 5.7022 | 16.1344 | 17.0095 | 7.3298 | 5.347 | 16.1125 | 17.0174 | 6.7919 | 4.9546 | 16.0901 | 17.0262 | 6.3224 | 4.6121 | 16.0921 | 17.0356 | 5.8532 | 4.2698 | 16.0794 | 17.0463 | 5.7772 | 4.2144 | 16.0347 | 17.0571 | 5.7158 | 4.1696 | 16.0304 | 17.0676 | 5.5816 | 4.0717 | 16.0003 | 17.0779 | 5.6046 | 4.0885 | 16.009 | 17.1427 | 5.4835 | 4.0001 | 15.9392 | 17.2843 | 5.3709 | 3.918 | 15.9371 | 17.404 | 5.3419 | 3.8968 | 15.9512 | 17.4956 | 5.231 | 3.8159 | 16.0231 | 16.9972 | 8.2651 | 6.0293 | 16.3136 | 17.0041 | 7.9155 | 5.7743 | 16.1323 | 17.0126 | 7.5305 | 5.4934 | 16.1096 | 17.0214 | 7.0662 | 5.1547 | 16.0865 | 17.0314 | 6.6306 | 4.8369 | 16.0878 | 17.0413 | 6.1461 | 4.4835 | 16.075 | 17.0518 | 6.0198 | 4.3914 | 16.0305 | 17.062 | 5.9786 | 4.3613 | 16.027 | 17.072 | 5.8784 | 4.2882 | 15.9977 | 17.1057 | 5.7229 | 4.1748 | 15.9886 | 17.2627 | 5.667 | 4.134 | 15.8476 | 17.3938 | 5.4706 | 3.9907 | 15.8518 | 17.487 | 5.3563 | 3.9074 | 15.8884 | 17.4875 | 5.2829 | 3.8538 | 16.0347
MONTON | BARTON | CARRINGTON | 376321 | 399494 | 24.1709 | 11.1455 | 8.1305 | 10.2037 | 24.2468 | 10.7408 | 7.8352 | 9.7199 | 24.2933 | 10.4636 | 7.6331 | 9.599 | 24.3635 | 10.1428 | 7.399 | 9.2845 | 24.4559 | 9.8453 | 7.182 | 8.9501 | 24.5628 | 9.5547 | 6.97 | 8.529 | 24.6833 | 9.3986 | 6.8562 | 8.0126 | 24.812 | 9.2267 | 6.7308 | 7.5136 | 24.9496 | 9.0157 | 6.5768 | 6.957 | 25.1022 | 8.7929 | 6.4143 | 6.391 | 25.8199 | 8.4221 | 6.1438 | 4.3115 | 26.5683 | 8.2556 | 6.0224 | 3.0285 | 27.1206 | 8.345 | 6.0876 | 2.4916 | 27.6616 | 8.454 | 6.1671 | 2.2925 | 24.1429 | 11.009 | 8.0309 | 10.282 | 24.1961 | 10.9669 | 8.0002 | 9.8492 | 24.2726 | 10.5921 | 7.7268 | 9.684 | 24.3628 | 10.276 | 7.4962 | 9.4032 | 24.4648 | 10.1422 | 7.3986 | 9.1351 | 24.5773 | 9.9602 | 7.2658 | 8.7459 | 24.7031 | 9.8657 | 7.1969 | 8.2863 | 24.8374 | 9.7673 | 7.1251 | 7.8262 | 24.9811 | 9.6544 | 7.0428 | 7.2888 | 25.1331 | 9.5494 | 6.9662 | 6.8087 | 25.5738 | 9.2459 | 6.7447 | 5.1735 | 26.0111 | 9.1423 | 6.6692 | 3.9065 | 26.3922 | 9.1431 | 6.6698 | 3.0941 | 26.7119 | 9.0142 | 6.5757 | 2.4462 | 24.171 | 11.0114 | 8.0327 | 10.2133 | 24.2472 | 10.9731 | 8.0048 | 9.7549 | 24.2942 | 10.5438 | 7.6915 | 9.6525 | 24.365 | 10.2659 | 7.4888 | 9.3525 | 24.4577 | 10.0886 | 7.3595 | 9.0355 | 24.5648 | 9.8784 | 7.2062 | 8.6377 | 24.6855 | 9.7689 | 7.1263 | 8.1412 | 24.8145 | 9.6431 | 7.0345 | 7.6628 | 24.9512 | 9.5213 | 6.9457 | 7.1382 | 25.098 | 9.3971 | 6.8551 | 6.6274 | 25.7427 | 8.9855 | 6.5548 | 4.7787 | 26.3002 | 8.9444 | 6.5248 | 3.6166 | 26.7567 | 9.2458 | 6.7447 | 3.2311 | 27.1284 | 9.2661 | 6.7595 | 3.0198 | 24.169 | 11.1465 | 8.1312 | 10.2175 | 24.2472 | 10.7451 | 7.8384 | 9.7488 | 24.3039 | 10.4421 | 7.6174 | 9.6488 | 24.3941 | 10.146 | 7.4014 | 9.3483 | 24.5125 | 9.8424 | 7.1799 | 9.0599 | 24.6632 | 9.5456 | 6.9634 | 8.6723 | 24.8503 | 9.3822 | 6.8442 | 8.1873 | 25.063 | 9.2059 | 6.7156 | 7.7202 | 25.2948 | 9.0004 | 6.5657 | 7.2416 | 25.5528 | 8.8057 | 6.4236 | 6.8187 | 26.8122 | 8.2186 | 5.9954 | 4.2718 | 28.1748 | 7.4674 | 5.4474 | 0.27576 | 29.0264 | 7.1574 | 5.2212 | -2.596 | 29.4882 | 6.7697 | 4.9384 | -4.5896 | 24.1774 | 11.1282 | 8.1178 | 10.0882 | 24.2628 | 10.9126 | 7.9606 | 9.558 | 24.3168 | 10.7738 | 7.8594 | 9.4987 | 24.4013 | 10.5954 | 7.7292 | 9.2476 | 24.5152 | 10.3593 | 7.557 | 8.9972 | 24.6638 | 10.1879 | 7.432 | 8.6739 | 24.8581 | 10.0151 | 7.3059 | 8.2329 | 25.0789 | 9.8597 | 7.1925 | 7.8258 | 25.3356 | 9.6644 | 7.0501 | 7.3409 | 25.701 | 9.3432 | 6.8158 | 6.3562 | 27.2625 | 8.5145 | 6.2112 | 1.6669 | 28.3446 | 7.5564 | 5.5123 | -1.9352 | 28.7838 | 7.1013 | 5.1803 | -3.8275 | 28.8083 | 7.0091 | 5.1131 | -3.4212
MOORSIDE | RIBBLE | PENWORTHAM EAST / ROCHDALE | 349331 | 435746 | 21.745 | 11.6408 | 8.4918 | 11.8215 | 21.7978 | 11.5047 | 8.3925 | 11.0867 | 21.8269 | 11.4233 | 8.3331 | 10.5505 | 21.8737 | 11.3372 | 8.2703 | 10.1607 | 21.9346 | 11.2674 | 8.2194 | 10.0299 | 22.0099 | 11.2515 | 8.2078 | 9.6718 | 22.0968 | 11.173 | 8.1506 | 9.2749 | 22.1911 | 11.0631 | 8.0704 | 8.8943 | 22.2915 | 10.9624 | 7.9969 | 8.5299 | 22.4059 | 10.858 | 7.9207 | 7.9698 | 22.8953 | 10.3703 | 7.565 | 6.2487 | 23.3392 | 10.3685 | 7.5636 | 5.4103 | 23.6399 | 10.5579 | 7.7018 | 5.1455 | 23.9044 | 10.5923 | 7.727 | 5.4135 | 21.7169 | 11.7084 | 8.5411 | 12.1509 | 21.7501 | 11.6564 | 8.5032 | 11.7351 | 21.8033 | 11.5381 | 8.4169 | 11.3127 | 21.8635 | 11.4494 | 8.3522 | 10.9869 | 21.9316 | 11.5153 | 8.4003 | 10.9031 | 22.0087 | 11.4551 | 8.3563 | 10.6071 | 22.096 | 11.3536 | 8.2823 | 10.2743 | 22.1905 | 11.2994 | 8.2428 | 9.9527 | 22.2922 | 11.24 | 8.1994 | 9.6351 | 22.4005 | 11.1618 | 8.1423 | 9.229 | 22.6416 | 10.9858 | 8.014 | 8.1789 | 22.867 | 11.065 | 8.0718 | 7.2908 | 23.067 | 11.3405 | 8.2727 | 6.6087 | 23.2234 | 11.3357 | 8.2692 | 6.2854 | 21.7451 | 11.7112 | 8.5431 | 11.826 | 21.7981 | 11.6621 | 8.5074 | 11.1005 | 21.8273 | 11.5802 | 8.4476 | 10.5756 | 21.8745 | 11.5443 | 8.4214 | 10.2002 | 21.9354 | 11.4986 | 8.388 | 10.0803 | 22.0107 | 11.439 | 8.3446 | 9.7363 | 22.0975 | 11.3269 | 8.2628 | 9.3533 | 22.1918 | 11.2118 | 8.1788 | 8.9856 | 22.2912 | 11.0991 | 8.0966 | 8.6389 | 22.4004 | 10.9703 | 8.0027 | 8.1281 | 22.842 | 10.6507 | 7.7695 | 6.5867 | 23.1799 | 10.755 | 7.8456 | 5.8976 | 23.4273 | 11.125 | 8.1155 | 5.6907 | 23.6046 | 10.8044 | 7.8817 | 5.9409 | 21.7416 | 11.6425 | 8.4931 | 11.8307 | 21.7936 | 11.5138 | 8.3991 | 11.0923 | 21.8267 | 11.4592 | 8.3593 | 10.5597 | 21.8836 | 11.3898 | 8.3087 | 10.1812 | 21.9619 | 11.3495 | 8.2793 | 10.0539 | 22.0663 | 11.2302 | 8.1923 | 9.6915 | 22.1964 | 11.1576 | 8.1393 | 9.2758 | 22.3464 | 11.0506 | 8.0612 | 8.8824 | 22.5133 | 10.946 | 7.9849 | 8.5585 | 22.7012 | 10.8214 | 7.894 | 8.1433 | 23.4517 | 10.2559 | 7.4816 | 6.6067 | 24.0911 | 9.9046 | 7.2253 | 4.824 | 24.4355 | 9.9666 | 7.2705 | 3.8675 | 24.5919 | 9.6766 | 7.0589 | 3.339 | 21.7416 | 11.637 | 8.489 | 11.7961 | 21.8008 | 11.4939 | 8.3846 | 11.0021 | 21.8362 | 11.423 | 8.3329 | 10.4636 | 21.891 | 11.3442 | 8.2754 | 10.0986 | 21.9672 | 11.3056 | 8.2473 | 9.9809 | 22.0691 | 11.2715 | 8.2224 | 9.6511 | 22.2016 | 11.1137 | 8.1073 | 9.2819 | 22.3515 | 11.0443 | 8.0567 | 8.9545 | 22.5168 | 10.9763 | 8.007 | 8.6961 | 22.7108 | 10.8632 | 7.9246 | 8.1185 | 23.4556 | 11.2458 | 8.2037 | 5.7728 | 23.9503 | 10.4401 | 7.6159 | 4.3762 | 24.1081 | 9.9382 | 7.2498 | 3.8336 | 24.0813 | 9.9055 | 7.226 | 4.3499
MORTON PARK & PIRELLI | CARLISLE | HARKER / HUTTON | 337826 | 553939 | 3.4354 | 0.56561 | 0.40652 | 3.4354 | 1.1574 | 0.19056 | 0.13696 | 1.1574 | 0.41238 | 0.067896 | 0.048798 | 0.41238 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.368 | 2.6844 | 0.44197 | 0.31765 | -2.2486 | 2.6844 | 0.44197 | 0.31765 | -4.5282 | 2.6844 | 0.44197 | 0.31765 | -7.7381 | 0.16479 | 0.062548 | 0.051108 | -10.4421 | 1.6795 | 0.44197 | 0.31765 | -15.6715 | 1.6795 | 0.44197 | 0.31765 | -18.1024 | 1.6795 | 0.44197 | 0.31765 | -18.7859 | 1.6795 | 0.44197 | 0.31765 | -18.4474 | 4.0818 | 0.67204 | 0.48301 | 4.0818 | 2.4482 | 0.40308 | 0.2897 | 2.4482 | 1.4399 | 0.23707 | 0.17039 | 1.4399 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.4103 | 2.6844 | 0.44197 | 0.31765 | 1.1877 | 2.6844 | 0.44197 | 0.31765 | 0.50276 | 2.6844 | 0.44197 | 0.31765 | 0.21552 | 4.0478 | 0.66644 | 0.47898 | 4.0478 | 2.3443 | 0.38596 | 0.2774 | 2.3443 | 1.1045 | 0.18185 | 0.1307 | 1.1045 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.5004 | 2.6844 | 0.44197 | 0.31765 | -2.089 | 2.6844 | 0.44197 | 0.31765 | -4.413 | 2.6844 | 0.44197 | 0.31765 | -7.5176 | 2.6844 | 0.44197 | 0.31765 | -10.1534 | 2.6844 | 0.44197 | 0.31765 | -15.2842 | 2.6844 | 0.44197 | 0.31765 | -17.526 | 2.6844 | 0.44197 | 0.31765 | -17.9589 | 2.6844 | 0.44197 | 0.31765 | -17.6098 | 3.4485 | 0.56777 | 0.40807 | 3.4485 | 0.7956 | 0.13099 | 0.094145 | 0.7956 | 0.56608 | 0.093201 | 0.066985 | 0.56608 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.435 | 2.6844 | 0.44197 | 0.31765 | -2.194 | 2.6844 | 0.44197 | 0.31765 | -4.4892 | 1.8592 | 0.44197 | 0.31765 | -7.6165 | 1.6795 | 0.44197 | 0.31765 | -11.9862 | 1.6795 | 0.44197 | 0.31765 | -20.3531 | 1.6795 | 0.44197 | 0.31765 | -26.8542 | 1.6795 | 0.44197 | 0.31765 | -31.0885 | 1.6795 | 0.44197 | 0.31765 | -33.7823 | 3.5535 | 0.58505 | 0.42049 | 3.5535 | 1.9047 | 0.31359 | 0.22538 | 1.9047 | 0.82695 | 0.13615 | 0.097854 | 0.82695 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.107 | 2.6844 | 0.44197 | 0.31765 | -6.4433 | 1.4139 | 0.44197 | 0.31765 | -11.6248 | 1.6795 | 0.44197 | 0.31765 | -15.541 | 1.6795 | 0.44197 | 0.31765 | -18.6606 | 1.6795 | 0.44197 | 0.31765 | -25.5558 | 1.6795 | 0.44197 | 0.31765 | -30.415 | 1.6795 | 0.44197 | 0.31765 | -33.2914 | 1.6795 | 0.44197 | 0.31765 | -32.1413
MOSLEY RD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 25.4218 | 11.5706 | 8.4406 | 7.0885 | 25.5635 | 11.4229 | 8.3329 | 6.5949 | 25.5884 | 11.3481 | 8.2783 | 6.5224 | 25.6194 | 11.2657 | 8.2182 | 6.428 | 25.6658 | 11.1496 | 8.1335 | 6.2633 | 25.7381 | 10.9938 | 8.0198 | 6.0503 | 25.8053 | 10.9979 | 8.0228 | 5.8427 | 25.8722 | 10.964 | 7.9981 | 5.6375 | 25.9416 | 10.8925 | 7.9459 | 5.4382 | 26.0121 | 10.8324 | 7.9021 | 5.2662 | 27.0353 | 10.4869 | 7.65 | 3.9488 | 29.1681 | 10.1838 | 7.429 | 1.6004 | 31.6283 | 10.204 | 7.4437 | -1.263 | 32.6964 | 10.2406 | 7.4704 | -2.7759 | 25.2769 | 11.6671 | 8.511 | 7.5764 | 25.3026 | 11.6029 | 8.4642 | 7.4848 | 25.3717 | 11.5501 | 8.4256 | 7.3187 | 25.4344 | 11.4783 | 8.3733 | 7.1413 | 25.5027 | 11.4023 | 8.3178 | 6.9313 | 25.5786 | 11.3471 | 8.2776 | 6.7157 | 25.6638 | 11.2916 | 8.237 | 6.4951 | 25.749 | 11.2287 | 8.1912 | 6.2711 | 25.8337 | 11.173 | 8.1506 | 6.0444 | 25.9199 | 11.1092 | 8.104 | 5.8459 | 26.6931 | 10.8594 | 7.9218 | 4.8149 | 27.6167 | 10.9044 | 7.9546 | 3.8017 | 28.4092 | 11.2039 | 8.1731 | 2.6845 | 29.1002 | 11.2898 | 8.2358 | 1.7908 | 25.4242 | 11.6688 | 8.5123 | 7.0905 | 25.5678 | 11.5853 | 8.4513 | 6.5983 | 25.595 | 11.522 | 8.4051 | 6.5268 | 25.6292 | 11.4509 | 8.3532 | 6.4329 | 25.6787 | 11.3734 | 8.2967 | 6.269 | 25.7531 | 11.3014 | 8.2442 | 6.0575 | 25.8237 | 11.2174 | 8.1829 | 5.8514 | 25.8927 | 11.1273 | 8.1172 | 5.6478 | 25.9631 | 11.0146 | 8.035 | 5.4525 | 26.0329 | 10.9926 | 8.0189 | 5.2925 | 26.8023 | 10.8854 | 7.9408 | 4.2057 | 28.4971 | 10.9013 | 7.9524 | 2.5885 | 30.7193 | 11.3822 | 8.3032 | 0.087155 | 31.3103 | 11.5483 | 8.4244 | -0.73104 | 25.4132 | 11.5744 | 8.4434 | 7.1154 | 25.5455 | 11.4268 | 8.3357 | 6.6496 | 25.5624 | 11.3304 | 8.2653 | 6.603 | 25.6024 | 11.25 | 8.2067 | 6.5344 | 25.6538 | 11.103 | 8.0994 | 6.3936 | 25.756 | 11.041 | 8.0543 | 6.1776 | 25.8993 | 11.025 | 8.0426 | 5.9392 | 26.0823 | 10.9658 | 7.9994 | 5.6773 | 26.3006 | 10.8929 | 7.9462 | 5.3974 | 26.5488 | 10.8128 | 7.8878 | 5.1309 | 30.7974 | 9.8581 | 7.1913 | 0.10466 | 33.3362 | 9.2886 | 6.7759 | -3.2945 | 34.6312 | 9.3721 | 6.8368 | -5.3896 | 35.145 | 9.4338 | 6.8818 | -6.2417 | 25.4384 | 11.5925 | 8.4566 | 7.0862 | 25.6037 | 11.4462 | 8.3499 | 6.5779 | 25.6384 | 11.3334 | 8.2675 | 6.5024 | 25.6969 | 11.2525 | 8.2085 | 6.4097 | 25.7829 | 11.2618 | 8.2153 | 6.2431 | 25.9712 | 11.1767 | 8.1533 | 5.971 | 26.2484 | 11.0916 | 8.0912 | 5.6373 | 26.8676 | 10.9317 | 7.9745 | 4.8859 | 28.6886 | 10.5875 | 7.7234 | 2.9083 | 29.119 | 10.4627 | 7.6324 | 2.3813 | 32.3326 | 10.121 | 7.3831 | -1.9347 | 34.138 | 9.3277 | 6.8044 | -4.7382 | 34.9696 | 9.3167 | 6.7964 | -6.0642 | 34.9935 | 9.3043 | 6.7873 | -5.9537
MOSS LANE | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 34.487 | 8.2873 | 5.9563 | 6.108 | 34.6194 | 8.122 | 5.8375 | 5.8214 | 34.6935 | 7.9695 | 5.7279 | 5.3624 | 34.8517 | 7.7856 | 5.5957 | 4.77 | 35.0683 | 7.5491 | 5.4257 | 4.1804 | 35.3022 | 7.3066 | 5.2514 | 3.3906 | 35.5368 | 7.0723 | 5.083 | 2.5051 | 35.7894 | 6.8589 | 4.9296 | 1.6842 | 36.0594 | 6.6212 | 4.7588 | 0.84745 | 36.3527 | 6.3325 | 4.5513 | -0.12354 | 31.3508 | 5.1617 | 3.7098 | -3.3504 | 28.7768 | 4.7379 | 3.4052 | -4.9442 | 29.6392 | 4.8799 | 3.5073 | -5.3002 | 30.2394 | 4.9787 | 3.5783 | -5.1844 | 34.3874 | 8.3085 | 5.9715 | 6.1844 | 34.4395 | 8.0807 | 5.8078 | 6.0194 | 34.5595 | 7.9499 | 5.7138 | 5.5188 | 34.7247 | 7.7483 | 5.5688 | 4.9916 | 34.9121 | 7.5429 | 5.4212 | 4.5356 | 35.1214 | 7.4068 | 5.3234 | 3.9038 | 35.3522 | 7.2495 | 5.2104 | 3.1975 | 35.5767 | 7.0934 | 5.0982 | 2.5195 | 35.807 | 6.9294 | 4.9803 | 1.8086 | 36.0465 | 6.7559 | 4.8556 | 1.0471 | 36.72 | 6.1848 | 4.4452 | -1.3412 | 34.7754 | 5.7255 | 4.115 | -2.9669 | 33.8909 | 5.5799 | 4.0104 | -3.9922 | 35.0051 | 5.7633 | 4.1422 | -4.6223 | 34.4872 | 8.3054 | 5.9693 | 6.1224 | 34.6201 | 8.0805 | 5.8076 | 5.8743 | 34.6949 | 7.8642 | 5.6522 | 5.4439 | 34.854 | 7.5711 | 5.4415 | 4.8705 | 35.0707 | 7.3319 | 5.2696 | 4.2749 | 35.3049 | 7.1417 | 5.1329 | 3.5093 | 35.5394 | 6.9455 | 4.9918 | 2.6471 | 35.7923 | 6.757 | 4.8564 | 1.8466 | 36.0593 | 6.5507 | 4.7081 | 1.045 | 36.3377 | 6.3226 | 4.5442 | 0.16442 | 33.9323 | 5.5867 | 4.0153 | -2.7092 | 32.1737 | 5.2972 | 3.8072 | -3.9525 | 31.2005 | 5.1369 | 3.692 | -4.1819 | 32.4438 | 5.3416 | 3.8391 | -3.839 | 34.479 | 8.2833 | 5.9534 | 6.118 | 34.6135 | 8.1255 | 5.84 | 5.857 | 34.7189 | 7.9864 | 5.74 | 5.4429 | 34.9414 | 7.7803 | 5.5918 | 4.9032 | 35.2016 | 7.55 | 5.4263 | 4.4197 | 35.517 | 7.3167 | 5.2586 | 3.7634 | 35.9003 | 7.0686 | 5.0803 | 2.9947 | 36.3341 | 6.8403 | 4.9162 | 2.3058 | 36.7493 | 6.6183 | 4.7567 | 1.697 | 37.2104 | 6.3386 | 4.5557 | 1.0491 | 30.2467 | 4.9799 | 3.5791 | -2.8517 | 19.7171 | 3.2463 | 2.3332 | -10.0629 | 15.2652 | 2.5133 | 1.8064 | -15.413 | 12.2898 | 2.0234 | 1.4543 | -18.9924 | 34.489 | 8.29 | 5.9582 | 6.0871 | 34.6589 | 8.1414 | 5.8514 | 5.741 | 34.7906 | 7.9737 | 5.7308 | 5.3225 | 35.0064 | 7.7312 | 5.5566 | 4.847 | 35.2408 | 7.4541 | 5.3574 | 4.3937 | 35.5561 | 7.1501 | 5.1389 | 3.8279 | 35.9571 | 6.8818 | 4.9461 | 3.1512 | 36.4 | 6.6179 | 4.7564 | 2.5788 | 36.8565 | 6.3147 | 4.5385 | 1.9005 | 34.955 | 5.7551 | 4.1363 | 0.13438 | 24.3331 | 4.0063 | 2.8794 | -8.1064 | 15.8711 | 2.6131 | 1.8781 | -14.5309 | 14.1648 | 2.3321 | 1.6761 | -18.0629 | 13.3194 | 2.1929 | 1.5761 | -16.8186
MOSS NOOK PRIMARY | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 31.4516 | 9.7731 | 7.0241 | 23.6536 | 31.5314 | 9.6941 | 6.9673 | 23.2158 | 31.632 | 9.6272 | 6.9193 | 23.1246 | 31.7528 | 9.5636 | 6.8735 | 22.9404 | 31.9122 | 9.4899 | 6.8206 | 22.7633 | 32.1004 | 9.3964 | 6.7534 | 22.4816 | 32.3104 | 9.3128 | 6.6933 | 22.2124 | 32.5368 | 9.234 | 6.6366 | 21.9426 | 32.7774 | 9.1256 | 6.5587 | 21.5132 | 33.0364 | 9.0111 | 6.4765 | 21.0246 | 34.0043 | 8.5172 | 6.1215 | 19.3836 | 34.4963 | 8.2439 | 5.925 | 18.6694 | 34.6587 | 14.0596 | 10.1049 | 18.5916 | 34.6886 | 19.9538 | 14.3412 | 18.8372 | 31.3853 | 9.871 | 7.0945 | 24.0498 | 31.4299 | 9.8379 | 7.0707 | 23.9523 | 31.5227 | 9.7788 | 7.0282 | 23.7694 | 31.6316 | 9.734 | 6.996 | 23.515 | 31.7536 | 9.6794 | 6.9568 | 23.3038 | 31.8866 | 9.6109 | 6.9076 | 23.0287 | 32.031 | 9.5474 | 6.8619 | 22.7573 | 32.1825 | 9.4681 | 6.8049 | 22.3613 | 32.3409 | 9.3713 | 6.7353 | 21.8687 | 32.5021 | 9.2666 | 6.6601 | 21.3425 | 32.9666 | 9.0368 | 6.4949 | 20.2186 | 33.3002 | 8.9261 | 6.4153 | 19.6545 | 33.5196 | 13.4535 | 9.6693 | 19.4247 | 33.6521 | 17.9987 | 12.9361 | 19.457 | 31.4517 | 9.8663 | 7.0911 | 23.6594 | 31.5314 | 9.8339 | 7.0678 | 23.2275 | 31.6321 | 9.767 | 7.0198 | 23.1426 | 31.753 | 9.697 | 6.9694 | 22.9656 | 31.9116 | 9.6367 | 6.9261 | 22.7965 | 32.0984 | 9.564 | 6.8738 | 22.5244 | 32.3072 | 9.4991 | 6.8272 | 22.2648 | 32.5329 | 9.4104 | 6.7634 | 22.0045 | 32.7697 | 9.3004 | 6.6844 | 21.6866 | 33.0127 | 9.1715 | 6.5918 | 21.2604 | 33.9278 | 8.8195 | 6.3387 | 19.6653 | 34.3411 | 8.619 | 6.1946 | 19.0345 | 34.4845 | 14.3735 | 10.3305 | 18.9739 | 34.5051 | 20.2135 | 14.5278 | 19.2139 | 31.4469 | 9.7747 | 7.0252 | 23.6831 | 31.5322 | 9.6952 | 6.9681 | 23.2773 | 31.6399 | 9.6147 | 6.9103 | 23.2178 | 31.7914 | 9.5605 | 6.8713 | 23.0642 | 31.9731 | 9.4914 | 6.8217 | 22.9182 | 32.1749 | 9.3925 | 6.7506 | 22.6666 | 32.3948 | 9.2996 | 6.6838 | 22.4229 | 32.6201 | 9.2122 | 6.621 | 22.1749 | 32.8439 | 9.1266 | 6.5595 | 21.9101 | 33.0653 | 9.0203 | 6.4831 | 21.6256 | 34.0361 | 8.3891 | 6.0294 | 19.8835 | 34.9846 | 7.6131 | 5.4717 | 16.6047 | 35.5524 | 12.828 | 9.2197 | 13.6556 | 35.878 | 18.2713 | 13.1319 | 11.6181 | 31.4574 | 9.7734 | 7.0243 | 23.6765 | 31.5792 | 9.6657 | 6.9469 | 23.2465 | 31.6969 | 9.6204 | 6.9144 | 23.1827 | 31.8337 | 9.5564 | 6.8684 | 23.044 | 31.9961 | 9.4825 | 6.8152 | 22.9162 | 32.1656 | 9.3905 | 6.7491 | 22.6949 | 32.3595 | 9.3117 | 6.6925 | 22.4777 | 32.5472 | 9.229 | 6.6331 | 22.268 | 32.734 | 9.1383 | 6.5679 | 22.0345 | 33.0145 | 8.9867 | 6.4589 | 21.5115 | 34.2039 | 7.9398 | 5.7065 | 17.3603 | 34.9476 | 8.2663 | 5.9412 | 13.9155 | 35.242 | 18.5727 | 13.3486 | 11.9613 | 35.0568 | 18.5606 | 13.3399 | 12.6199
MOSS SIDE (Leyland) & SEVEN STARS | LEYLAND | PENWORTHAM WEST / STANAH | 352170 | 422970 | 24.6089 | 14.3827 | 10.3371 | 10.3957 | 24.7257 | 14.1246 | 10.1516 | 9.7511 | 24.8195 | 13.9504 | 10.0264 | 9.6207 | 24.9454 | 13.651 | 9.8112 | 9.1797 | 25.1107 | 13.3381 | 9.5863 | 8.9377 | 25.307 | 12.6899 | 9.1205 | 8.3621 | 25.5283 | 12.5689 | 9.0335 | 7.8841 | 25.7671 | 12.4587 | 8.9543 | 7.1967 | 26.0241 | 12.298 | 8.8388 | 6.5211 | 26.3301 | 12.0741 | 8.6779 | 5.7565 | 27.8372 | 11.004 | 7.9088 | 3.0375 | 29.3295 | 10.067 | 7.2353 | 1.4147 | 30.4506 | 9.424 | 6.7732 | 0.87104 | 31.4951 | 9.1559 | 6.5805 | 0.41982 | 24.5735 | 14.4406 | 10.3787 | 10.7539 | 24.6542 | 14.3144 | 10.2881 | 10.3615 | 24.7715 | 14.1989 | 10.205 | 10.1523 | 24.8804 | 14.0522 | 10.0996 | 9.7046 | 25.0168 | 13.9324 | 10.0135 | 9.489 | 25.1766 | 13.7605 | 9.89 | 8.9766 | 25.3561 | 13.6234 | 9.7914 | 8.5743 | 25.5465 | 13.4576 | 9.6723 | 8.0909 | 25.7487 | 13.2724 | 9.5391 | 7.5099 | 25.9581 | 13.0786 | 9.3998 | 6.9042 | 26.9124 | 12.3232 | 8.8569 | 4.8339 | 27.8632 | 11.5327 | 8.2888 | 3.3529 | 28.6762 | 11.362 | 8.1661 | 2.4466 | 29.3083 | 11.1417 | 8.0077 | 1.8736 | 24.6099 | 14.4317 | 10.3723 | 10.4021 | 24.7276 | 14.1636 | 10.1796 | 9.8191 | 24.8226 | 13.781 | 9.9047 | 9.7025 | 24.9499 | 13.5118 | 9.7112 | 9.2743 | 25.1162 | 13.5944 | 9.7706 | 9.0467 | 25.3126 | 13.437 | 9.6575 | 8.4891 | 25.5337 | 13.2789 | 9.5438 | 8.0021 | 25.7724 | 13.1108 | 9.423 | 7.3321 | 26.0265 | 12.9146 | 9.282 | 6.6841 | 26.3206 | 12.6399 | 9.0846 | 5.9866 | 27.6616 | 11.7727 | 8.4613 | 3.584 | 28.6588 | 10.9909 | 7.8994 | 2.4101 | 29.5261 | 10.3865 | 7.465 | 2.1084 | 30.2173 | 9.7914 | 7.0373 | 1.9774 | 24.6162 | 14.3832 | 10.3375 | 10.4138 | 24.7477 | 14.1181 | 10.147 | 9.7832 | 24.8685 | 13.7513 | 9.8833 | 9.674 | 25.0362 | 13.3088 | 9.5653 | 9.2526 | 25.2495 | 13.0044 | 9.3465 | 9.0469 | 25.5282 | 12.9939 | 9.339 | 8.5012 | 25.8764 | 12.8281 | 9.2198 | 8.0605 | 26.2787 | 12.6321 | 9.0789 | 7.6049 | 26.7051 | 12.392 | 8.9064 | 7.0875 | 27.1824 | 12.1293 | 8.7176 | 6.5845 | 29.5812 | 10.4702 | 7.5251 | 3.279 | 31.9751 | 8.5172 | 6.1214 | -2.1704 | 33.3553 | 6.7917 | 4.8814 | -6.2738 | 33.2175 | 5.469 | 3.9307 | -9.2434 | 24.6158 | 14.3808 | 10.3358 | 10.4013 | 24.7621 | 14.1044 | 10.1371 | 9.7174 | 24.8958 | 13.8707 | 9.9692 | 9.6023 | 25.0734 | 13.3602 | 9.6023 | 9.2067 | 25.2963 | 13.279 | 9.5438 | 9.0336 | 25.5962 | 13.1723 | 9.4672 | 8.5275 | 25.9848 | 12.9748 | 9.3252 | 8.1087 | 26.4373 | 12.7442 | 9.1595 | 7.6146 | 26.9935 | 12.482 | 8.9711 | 7.0094 | 27.7914 | 11.9962 | 8.6219 | 5.6873 | 30.4651 | 9.8226 | 7.0597 | -0.31499 | 32.3797 | 7.9749 | 5.7317 | -5.1998 | 33.223 | 6.7588 | 4.8577 | -8.1955 | 33.243 | 6.3266 | 4.5471 | -7.8881
MOSS SIDE (Longsight) | LONGSIGHT | BREDBURY | 384007 | 395893 | 34.258 | 11.4535 | 8.3552 | 10.7381 | 34.4065 | 11.0897 | 8.0898 | 10.5021 | 34.416 | 10.1738 | 7.4216 | 8.1606 | 34.4704 | 9.7887 | 7.1408 | 6.0068 | 34.5606 | 9.2065 | 6.716 | 3.852 | 34.678 | 8.6395 | 6.3024 | 1.646 | 34.7969 | 8.1092 | 5.9155 | -1.0366 | 34.9165 | 7.8632 | 5.7361 | -2.1672 | 35.048 | 7.6138 | 5.5542 | -3.19 | 36.8971 | 6.9619 | 5.0786 | -6.4434 | 38.0818 | 6.1772 | 4.5062 | -9.2947 | 35.9894 | 5.8378 | 4.2586 | -10.2687 | 36.7022 | 5.9535 | 4.343 | -11.1233 | 36.9046 | 5.9863 | 4.3669 | -10.9663 | 34.1159 | 11.2984 | 8.242 | 10.9716 | 34.145 | 10.7375 | 7.8329 | 10.9298 | 34.2182 | 10.0773 | 7.3513 | 8.4895 | 34.3028 | 9.4504 | 6.8939 | 6.2721 | 34.4102 | 8.8617 | 6.4645 | 4.0756 | 34.5267 | 8.2995 | 6.0544 | 1.8453 | 34.6497 | 7.7697 | 5.6679 | -0.87157 | 34.7748 | 7.5351 | 5.4968 | -2.0449 | 34.9011 | 7.3221 | 5.3414 | -3.1071 | 35.029 | 7.0212 | 5.1219 | -4.631 | 35.5153 | 6.7604 | 4.9316 | -5.663 | 36.0363 | 6.6032 | 4.817 | -6.6601 | 36.236 | 6.5589 | 4.7846 | -7.6178 | 36.2967 | 6.5075 | 4.7471 | -8.0834 | 34.258 | 11.2788 | 8.2278 | 10.7469 | 34.4065 | 11.1286 | 8.1182 | 10.5224 | 34.4162 | 10.4744 | 7.6409 | 8.1953 | 34.4707 | 9.8 | 7.1489 | 6.0518 | 34.5608 | 9.1686 | 6.6883 | 3.9089 | 34.6781 | 8.6321 | 6.297 | 1.715 | 34.7969 | 8.0973 | 5.9069 | -0.95199 | 34.9165 | 7.8407 | 5.7197 | -2.0709 | 35.0474 | 7.5903 | 5.537 | -3.0771 | 36.8932 | 7.2639 | 5.2989 | -6.2887 | 38.8718 | 6.8847 | 5.0223 | -8.9983 | 39.0149 | 6.7246 | 4.9055 | -9.8539 | 39.1811 | 6.6815 | 4.8741 | -10.6469 | 39.0624 | 6.767 | 4.9364 | -10.4876 | 34.247 | 11.4562 | 8.3571 | 10.7537 | 34.3894 | 11.0817 | 8.084 | 10.5347 | 34.4018 | 10.3358 | 7.5398 | 8.2119 | 34.4688 | 9.7998 | 7.1489 | 6.0678 | 34.576 | 9.1663 | 6.6867 | 3.9314 | 34.7327 | 8.6242 | 6.2913 | 1.7311 | 34.9297 | 8.0784 | 5.8931 | -0.99636 | 35.1417 | 7.7936 | 5.6854 | -2.1797 | 35.3505 | 7.5307 | 5.4936 | -3.1977 | 37.1953 | 6.8931 | 5.0284 | -6.3228 | 35.8285 | 5.8117 | 4.2396 | -9.907 | 27.8808 | 4.5225 | 3.2991 | -15.5307 | 24.1937 | 3.9245 | 2.8628 | -19.2417 | 21.5067 | 3.4886 | 2.5449 | -21.188 | 34.2324 | 11.465 | 8.3635 | 10.7921 | 34.3637 | 11.255 | 8.2104 | 10.6071 | 34.3687 | 10.6427 | 7.7637 | 8.3219 | 34.4339 | 10.2125 | 7.4499 | 6.221 | 34.5584 | 9.6781 | 7.06 | 4.0922 | 34.723 | 9.2133 | 6.721 | 1.921 | 34.9083 | 8.653 | 6.3122 | -0.74002 | 35.107 | 8.369 | 6.1051 | -1.8583 | 35.3404 | 8.1034 | 5.9113 | -2.9301 | 39.1683 | 6.9609 | 5.0779 | -8.8074 | 33.7768 | 5.4789 | 3.9968 | -14.4702 | 27.748 | 4.501 | 3.2834 | -18.1977 | 23.4435 | 3.8028 | 2.7741 | -20.7158 | 23.5121 | 3.8139 | 2.7822 | -19.781
MOSSLEY | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 25.8231 | 4.3348 | 3.1155 | 14.3164 | 24.5919 | 4.0489 | 2.91 | 14.0454 | 23.8894 | 3.9332 | 2.8269 | 13.7534 | 21.1349 | 3.4797 | 2.5009 | 13.3463 | 21.0823 | 3.471 | 2.4947 | 12.9959 | 20.095 | 3.3085 | 2.3779 | 12.4735 | 18.9025 | 3.1121 | 2.2368 | 11.8632 | 18.0481 | 2.9715 | 2.1357 | 11.2809 | 17.0313 | 2.8041 | 2.0153 | 10.6731 | 15.9861 | 2.632 | 1.8917 | 9.9595 | 11.4368 | 1.883 | 1.3533 | 7.5924 | 8.935 | 1.4711 | 1.0573 | 6.5396 | 13.4769 | 2.2189 | 1.5947 | 6.4378 | 13.1992 | 2.1731 | 1.5619 | 6.6997 | 25.7763 | 4.3527 | 3.1284 | 14.3724 | 25.8124 | 4.2786 | 3.0751 | 14.1433 | 24.8204 | 4.0865 | 2.937 | 13.7998 | 23.7296 | 3.9069 | 2.808 | 13.4356 | 22.5132 | 3.7066 | 2.664 | 13.2244 | 21.2189 | 3.4935 | 2.5109 | 12.7863 | 20.6471 | 3.3994 | 2.4432 | 12.3378 | 20.0023 | 3.2932 | 2.3669 | 11.8634 | 19.322 | 3.1812 | 2.2864 | 11.3493 | 18.6149 | 3.0648 | 2.2027 | 10.8219 | 16.1184 | 2.6538 | 1.9073 | 9.2014 | 14.1945 | 2.337 | 1.6797 | 8.1081 | 16.5981 | 2.7327 | 1.9641 | 7.4943 | 20.2958 | 3.3415 | 2.4016 | 7.1872 | 25.8231 | 4.3406 | 3.1197 | 14.3238 | 25.8974 | 4.2744 | 3.0721 | 14.0651 | 24.4755 | 4.0297 | 2.8962 | 13.7866 | 23.223 | 3.8235 | 2.748 | 13.3946 | 21.8426 | 3.5962 | 2.5847 | 13.0457 | 20.7448 | 3.4155 | 2.4548 | 12.5422 | 19.8814 | 3.2733 | 2.3526 | 11.9508 | 19.1426 | 3.1517 | 2.2652 | 11.3858 | 18.0061 | 2.9646 | 2.1307 | 10.8046 | 17.1576 | 2.8249 | 2.0303 | 10.1576 | 14.3463 | 2.362 | 1.6976 | 8.0308 | 11.3329 | 1.8659 | 1.341 | 7.1432 | 16.8176 | 2.7689 | 1.9901 | 7.0913 | 16.0455 | 2.6418 | 1.8987 | 7.3895 | 25.819 | 4.3325 | 3.1139 | 14.3253 | 24.7267 | 4.0711 | 2.926 | 14.0584 | 23.5733 | 3.8812 | 2.7895 | 13.7805 | 21.7417 | 3.5796 | 2.5727 | 13.3996 | 21.3204 | 3.5102 | 2.5229 | 13.132 | 19.697 | 3.243 | 2.3308 | 12.6728 | 18.6425 | 3.0693 | 2.206 | 12.1136 | 17.7229 | 2.9179 | 2.0972 | 11.5928 | 16.6912 | 2.7481 | 1.9751 | 11.1232 | 15.6226 | 2.5721 | 1.8486 | 10.6456 | 9.0068 | 1.4829 | 1.0658 | 7.786 | 2.6844 | 0.44197 | 0.31765 | 2.1873 | 0.14618 | 0.024067 | 0.017298 | -1.9395 | 2.6844 | 0.44197 | 0.31765 | -4.6583 | 25.8183 | 4.3365 | 3.1168 | 14.3353 | 25.0369 | 4.1221 | 2.9627 | 14.0383 | 24.9655 | 4.1104 | 2.9542 | 13.7603 | 22.8589 | 3.7635 | 2.7049 | 13.4148 | 23.1612 | 3.8133 | 2.7407 | 13.1012 | 22.4752 | 3.7004 | 2.6595 | 12.7074 | 21.406 | 3.5243 | 2.533 | 12.2261 | 20.5663 | 3.3861 | 2.4336 | 11.8086 | 19.6001 | 3.227 | 2.3193 | 11.2685 | 17.5905 | 2.8961 | 2.0815 | 9.8521 | 11.4816 | 1.8904 | 1.3586 | 3.3817 | 2.3681 | 0.3899 | 0.28023 | -1.5127 | 2.6844 | 0.44197 | 0.31765 | -4.1334 | 2.6844 | 0.44197 | 0.31765 | -2.9874
MOUNT ST | BARTON | CARRINGTON | 376250 | 397574 | 30.5943 | 6.1749 | 4.5045 | 15.8366 | 30.719 | 5.6344 | 4.1102 | 14.6386 | 30.7879 | 5.4662 | 3.9875 | 14.079 | 30.8865 | 5.2604 | 3.8374 | 13.69 | 31.0162 | 5.0695 | 3.6981 | 13.4885 | 29.7662 | 4.8284 | 3.5222 | 12.8999 | 28.8501 | 4.6798 | 3.4138 | 12.2541 | 28.083 | 4.5553 | 3.3231 | 11.7148 | 27.2345 | 4.4177 | 3.2227 | 11.078 | 26.3043 | 4.2668 | 3.1126 | 10.4437 | 21.9089 | 3.5538 | 2.5925 | 7.9962 | 20.5928 | 3.3403 | 2.4367 | 6.5143 | 22.5217 | 3.6532 | 2.665 | 6.1417 | 22.2886 | 3.6154 | 2.6374 | 5.4622 | 30.5271 | 6.3913 | 4.6623 | 16.4591 | 30.5916 | 5.9674 | 4.3531 | 15.8543 | 30.6959 | 5.5314 | 4.0351 | 15.2808 | 30.8121 | 5.1855 | 3.7828 | 14.8681 | 30.4659 | 4.9419 | 3.605 | 14.7191 | 28.7473 | 4.6631 | 3.4017 | 14.1912 | 28.0211 | 4.5453 | 3.3157 | 13.5988 | 27.3693 | 4.4396 | 3.2386 | 13.0952 | 26.615 | 4.3172 | 3.1493 | 12.4965 | 25.9315 | 4.2063 | 3.0685 | 11.9591 | 23.7171 | 3.8471 | 2.8064 | 10.0247 | 23.0917 | 3.7457 | 2.7324 | 8.5074 | 24.6505 | 3.9985 | 2.9169 | 7.7696 | 24.6335 | 3.9958 | 2.9149 | 7.2027 | 30.5971 | 6.3882 | 4.6601 | 15.8511 | 30.7227 | 5.9711 | 4.3559 | 14.6644 | 30.7923 | 5.5333 | 4.0365 | 14.1316 | 30.8914 | 5.1586 | 3.7631 | 13.7164 | 30.1114 | 4.8844 | 3.5631 | 13.5272 | 28.2809 | 4.5874 | 3.3465 | 12.9563 | 27.533 | 4.4661 | 3.258 | 12.3288 | 26.8185 | 4.3502 | 3.1734 | 11.8062 | 25.9604 | 4.211 | 3.0719 | 11.1961 | 25.1842 | 4.0851 | 2.98 | 10.6183 | 22.2361 | 3.6069 | 2.6312 | 8.3766 | 21.9056 | 3.5533 | 2.5921 | 7.0861 | 24.8261 | 4.027 | 2.9377 | 6.7725 | 24.9861 | 4.053 | 2.9566 | 6.6904 | 30.5926 | 6.1754 | 4.5048 | 15.8559 | 30.7186 | 5.6528 | 4.1237 | 14.6711 | 30.8021 | 5.4749 | 3.9938 | 14.1056 | 30.9285 | 5.2636 | 3.8397 | 13.7473 | 31.1008 | 5.0648 | 3.6947 | 13.6067 | 29.6549 | 4.8103 | 3.5091 | 13.0653 | 28.6995 | 4.6553 | 3.396 | 12.4443 | 27.9039 | 4.5263 | 3.3019 | 11.932 | 26.9989 | 4.3795 | 3.1948 | 11.3831 | 25.9667 | 4.2121 | 3.0726 | 10.9028 | 19.6185 | 3.1823 | 2.3215 | 7.4768 | 14.2937 | 2.3186 | 1.6914 | 2.5757 | 12.043 | 1.9535 | 1.425 | -1.1133 | 9.2275 | 1.4968 | 1.0919 | -3.893 | 30.5981 | 6.1698 | 4.5008 | 15.8323 | 30.7432 | 5.7358 | 4.1842 | 14.6014 | 30.8415 | 5.6792 | 4.1429 | 13.9989 | 30.9767 | 5.5874 | 4.076 | 13.5619 | 31.1562 | 5.5355 | 4.0381 | 13.3988 | 31.384 | 5.4255 | 3.9578 | 12.8719 | 31.6658 | 5.2828 | 3.8538 | 12.2764 | 31.8436 | 5.1653 | 3.7681 | 11.8072 | 30.826 | 5.0003 | 3.6476 | 11.1957 | 28.9355 | 4.6936 | 3.4239 | 9.9283 | 21.8593 | 3.5458 | 2.5866 | 3.9501 | 14.7584 | 2.394 | 1.7464 | -0.65846 | 11.4869 | 1.8633 | 1.3592 | -3.4372 | 11.0393 | 1.7907 | 1.3063 | -2.8857
MUSGRAVE RD | BOLTON | KEARSLEY | 370045 | 409863 | 31.5712 | 6.1257 | 4.4686 | 14.2258 | 31.6307 | 5.9675 | 4.3532 | 13.9522 | 31.6458 | 5.8505 | 4.2679 | 13.8211 | 31.693 | 5.5845 | 4.0738 | 13.4731 | 31.7614 | 5.5123 | 4.0211 | 13.2992 | 31.8506 | 5.414 | 3.9495 | 12.9358 | 31.9511 | 5.2164 | 3.8053 | 12.5406 | 32.0608 | 5.2193 | 3.8074 | 12.1714 | 31.9478 | 5.1823 | 3.7804 | 11.7925 | 31.4235 | 5.0972 | 3.7183 | 11.3424 | 27.5096 | 4.4623 | 3.2552 | 9.7658 | 30.4861 | 4.9452 | 3.6074 | 8.9457 | 34.0286 | 5.5198 | 4.0266 | 8.6265 | 34.49 | 5.7089 | 4.1646 | 8.6969 | 31.5209 | 6.1171 | 4.4624 | 14.3039 | 31.5417 | 6.0275 | 4.397 | 14.0949 | 31.5919 | 5.9843 | 4.3654 | 13.9178 | 31.6579 | 5.8811 | 4.2902 | 13.586 | 31.7332 | 5.8136 | 4.2409 | 13.4497 | 31.8137 | 5.7058 | 4.1623 | 13.1276 | 31.8981 | 5.5832 | 4.0729 | 12.7694 | 31.9885 | 5.5054 | 4.0161 | 12.4359 | 32.0844 | 5.4789 | 3.9968 | 12.0868 | 32.1845 | 5.439 | 3.9677 | 11.724 | 32.4871 | 5.3414 | 3.8965 | 10.6196 | 32.7948 | 5.4648 | 3.9865 | 9.8563 | 33.0918 | 5.7207 | 4.1732 | 9.2806 | 33.3345 | 5.8777 | 4.2877 | 8.9898 | 31.5714 | 6.1047 | 4.4533 | 14.2351 | 31.6311 | 6.038 | 4.4046 | 13.9687 | 31.6465 | 5.913 | 4.3134 | 13.8521 | 31.6943 | 5.883 | 4.2916 | 13.5166 | 31.7629 | 5.8581 | 4.2734 | 13.3553 | 31.8522 | 5.7774 | 4.2145 | 13.0066 | 31.9528 | 5.7132 | 4.1677 | 12.6256 | 32.0627 | 5.639 | 4.1136 | 12.2693 | 32.1793 | 5.5578 | 4.0543 | 11.9105 | 32.3039 | 5.456 | 3.9801 | 11.5065 | 31.102 | 5.045 | 3.6803 | 10.111 | 33.2704 | 5.3968 | 3.9369 | 9.4782 | 33.707 | 6.1263 | 4.4691 | 9.2378 | 34.0146 | 6.2304 | 4.545 | 9.3956 | 31.566 | 6.1239 | 4.4673 | 14.2358 | 31.6241 | 5.9491 | 4.3398 | 13.9751 | 31.6468 | 5.8035 | 4.2336 | 13.8632 | 31.7115 | 5.5402 | 4.0415 | 13.536 | 31.808 | 5.5322 | 4.0357 | 13.3944 | 31.9434 | 5.3791 | 3.924 | 13.0599 | 32.11 | 5.2631 | 3.8394 | 12.6758 | 32.3042 | 5.2434 | 3.825 | 12.3169 | 31.954 | 5.1833 | 3.7811 | 12.0051 | 31.3184 | 5.0802 | 3.7059 | 11.6779 | 26.9086 | 4.3648 | 3.1841 | 9.2819 | 23.3458 | 3.7869 | 2.7625 | 4.1044 | 21.8894 | 3.5507 | 2.5902 | -0.044356 | 19.3856 | 3.1445 | 2.2939 | -2.5315 | 31.5599 | 6.1273 | 4.4698 | 14.2434 | 31.6228 | 5.9326 | 4.3278 | 13.9439 | 31.6475 | 5.7144 | 4.1686 | 13.8417 | 31.7067 | 5.5974 | 4.0833 | 13.5596 | 31.7979 | 5.7183 | 4.1714 | 13.4579 | 31.9291 | 5.6915 | 4.1519 | 13.1805 | 32.1006 | 5.5749 | 4.0668 | 12.8511 | 32.299 | 5.481 | 3.9983 | 12.5543 | 32.5312 | 5.3641 | 3.913 | 12.1356 | 30.9253 | 5.0164 | 3.6594 | 10.8975 | 31.8129 | 5.1604 | 3.7644 | 5.0488 | 24.446 | 3.9654 | 2.8927 | 0.40369 | 21.0846 | 3.4201 | 2.4949 | -2.2994 | 21.2098 | 3.4404 | 2.5098 | -1.2066
NELSON | NELSON | PADIHAM | 386020 | 438507 | 32.8121 | 12.1719 | 8.8793 | 9.3448 | 32.9186 | 11.8608 | 8.6523 | 8.1227 | 32.9288 | 11.6155 | 8.4734 | 7.6922 | 32.9768 | 11.4967 | 8.3867 | 7.4807 | 33.0514 | 11.3611 | 8.2878 | 7.2702 | 33.1539 | 11.1929 | 8.1651 | 6.9614 | 33.2675 | 11.0564 | 8.0655 | 6.6337 | 33.3894 | 10.9163 | 7.9633 | 6.2959 | 33.5192 | 10.7468 | 7.8397 | 5.9539 | 33.6622 | 10.5441 | 7.6918 | 5.5393 | 34.2645 | 9.8053 | 7.1528 | 4.1102 | 34.9017 | 9.3255 | 6.8028 | 3.193 | 35.3662 | 9.2685 | 6.7612 | 2.9006 | 35.8142 | 9.1676 | 6.6876 | 2.9024 | 32.7167 | 12.2804 | 8.9584 | 10.0463 | 32.7534 | 12.1883 | 8.8912 | 9.5087 | 32.8343 | 12.0362 | 8.7803 | 9.0561 | 32.9361 | 11.9033 | 8.6833 | 8.7478 | 33.0522 | 11.7325 | 8.5587 | 8.4648 | 33.1829 | 11.5757 | 8.4443 | 8.1095 | 33.3237 | 11.5215 | 8.4048 | 7.7165 | 33.4459 | 11.4428 | 8.3474 | 7.2979 | 33.5765 | 11.3454 | 8.2763 | 6.8642 | 33.7142 | 11.2282 | 8.1908 | 6.41 | 34.0272 | 10.9346 | 7.9766 | 5.4817 | 34.363 | 10.6042 | 7.7356 | 4.669 | 34.6829 | 10.562 | 7.7048 | 4.2095 | 34.9233 | 10.2864 | 7.5038 | 3.9395 | 32.8123 | 12.2768 | 8.9557 | 9.3569 | 32.9191 | 12.1731 | 8.8801 | 8.1503 | 32.9298 | 11.978 | 8.7378 | 7.7349 | 32.9784 | 11.8151 | 8.619 | 7.5492 | 33.0535 | 11.6821 | 8.5219 | 7.4032 | 33.1563 | 11.5229 | 8.4058 | 7.1148 | 33.2701 | 11.3461 | 8.2768 | 6.8076 | 33.3923 | 11.2416 | 8.2006 | 6.4905 | 33.5211 | 11.1256 | 8.116 | 6.1757 | 33.6579 | 10.9768 | 8.0074 | 5.8097 | 34.1863 | 10.1538 | 7.4071 | 4.5423 | 34.6182 | 9.9915 | 7.2887 | 3.8304 | 34.9791 | 10.0074 | 7.3003 | 3.633 | 35.2427 | 9.8302 | 7.171 | 3.7415 | 32.802 | 12.1735 | 8.8804 | 9.3657 | 32.902 | 11.8447 | 8.6405 | 8.1599 | 32.9144 | 11.6168 | 8.4743 | 7.7329 | 32.9731 | 11.47 | 8.3672 | 7.5302 | 33.0697 | 11.3304 | 8.2654 | 7.325 | 33.2138 | 11.1367 | 8.124 | 7.0104 | 33.3918 | 11.0038 | 8.0271 | 6.6512 | 33.5981 | 10.8124 | 7.8875 | 6.2752 | 33.8198 | 10.6112 | 7.7407 | 5.9311 | 34.0375 | 10.3611 | 7.5583 | 5.5821 | 35.1589 | 9.2745 | 6.7656 | 3.2002 | 36.3278 | 7.8936 | 5.7583 | -2.1554 | 36.965 | 7.1897 | 5.2448 | -6.1124 | 37.204 | 6.5888 | 4.8064 | -8.4704 | 32.7894 | 12.1805 | 8.8855 | 9.3861 | 32.8853 | 11.8791 | 8.6656 | 8.1839 | 32.8946 | 11.7168 | 8.5472 | 7.7796 | 32.9438 | 11.6379 | 8.4897 | 7.6174 | 33.0317 | 11.4521 | 8.3541 | 7.4773 | 33.1699 | 11.1803 | 8.1559 | 7.2098 | 33.3527 | 10.9524 | 7.9896 | 6.9033 | 33.5643 | 10.7487 | 7.8411 | 6.5853 | 33.8124 | 10.4488 | 7.6222 | 6.1331 | 34.1249 | 9.9635 | 7.2682 | 4.8188 | 35.3631 | 8.507 | 6.2057 | -1.2128 | 36.2546 | 7.0844 | 5.168 | -6.0319 | 36.5672 | 6.5346 | 4.7669 | -8.4587 | 36.4491 | 6.5528 | 4.7801 | -7.2367
NEW MOSTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 30.6128 | 15.2198 | 11.1026 | 15.2276 | 30.6648 | 14.8911 | 10.8629 | 14.935 | 30.6962 | 14.5275 | 10.5976 | 14.7331 | 30.7527 | 14.5108 | 10.5854 | 14.3761 | 30.8321 | 14.3464 | 10.4655 | 14.0166 | 30.9297 | 14.1489 | 10.3214 | 13.5436 | 31.0375 | 14.0357 | 10.2388 | 13.0792 | 31.1547 | 13.887 | 10.1304 | 12.5622 | 31.2807 | 13.7472 | 10.0284 | 12.0003 | 31.4229 | 13.5639 | 9.8947 | 11.3414 | 31.9942 | 12.9086 | 9.4167 | 8.906 | 32.4472 | 12.6813 | 9.2509 | 7.5267 | 32.7358 | 12.878 | 9.3944 | 7.0417 | 32.9249 | 12.8475 | 9.3721 | 7.1856 | 30.5909 | 15.287 | 11.1517 | 15.3331 | 30.6295 | 15.1362 | 11.0417 | 15.1261 | 30.6945 | 14.98 | 10.9277 | 14.8572 | 30.7721 | 14.8146 | 10.8071 | 14.5222 | 30.8601 | 14.6651 | 10.698 | 14.2156 | 30.9542 | 14.498 | 10.5761 | 13.8028 | 31.0572 | 14.4007 | 10.5051 | 13.3938 | 31.1676 | 14.2955 | 10.4283 | 12.9322 | 31.2849 | 14.18 | 10.3441 | 12.4384 | 31.4085 | 14.0618 | 10.2579 | 11.9618 | 31.7215 | 13.7346 | 10.0192 | 10.274 | 31.9653 | 13.5583 | 9.8906 | 8.7991 | 32.1481 | 13.6614 | 9.9658 | 7.8191 | 32.2828 | 13.5443 | 9.8804 | 7.1515 | 30.6129 | 15.2854 | 11.1505 | 15.2379 | 30.6649 | 15.1259 | 11.0341 | 14.9556 | 30.6964 | 14.9473 | 10.9038 | 14.7634 | 30.7529 | 14.7494 | 10.7595 | 14.4164 | 30.8322 | 14.5656 | 10.6254 | 14.0691 | 30.9294 | 14.4214 | 10.5202 | 13.6099 | 31.0368 | 14.3136 | 10.4416 | 13.1586 | 31.1538 | 14.2078 | 10.3644 | 12.6546 | 31.2784 | 14.0857 | 10.2753 | 12.1149 | 31.4144 | 13.961 | 10.1843 | 11.5112 | 31.9481 | 13.4854 | 9.8374 | 9.2769 | 32.346 | 13.3406 | 9.7318 | 8.0436 | 32.6143 | 13.5676 | 9.8974 | 7.6132 | 32.7744 | 13.4125 | 9.7842 | 7.7513 | 30.6098 | 15.2179 | 11.1012 | 15.2351 | 30.6615 | 14.8823 | 10.8565 | 14.9474 | 30.7008 | 14.5741 | 10.6316 | 14.752 | 30.7746 | 14.4949 | 10.5738 | 14.3989 | 30.8816 | 14.3292 | 10.4529 | 14.0726 | 31.0199 | 14.1346 | 10.311 | 13.6144 | 31.1857 | 13.9666 | 10.1884 | 13.0968 | 31.3742 | 13.8109 | 10.0748 | 12.5309 | 31.5813 | 13.6313 | 9.9438 | 12.0075 | 31.8113 | 13.4638 | 9.8216 | 11.505 | 32.5802 | 12.5814 | 9.178 | 8.673 | 33.244 | 11.5699 | 8.4401 | 3.8312 | 33.6343 | 11.0592 | 8.0675 | 0.42791 | 33.8632 | 10.4703 | 7.638 | -2.0151 | 30.5945 | 15.2255 | 11.1068 | 15.2658 | 30.6409 | 14.9448 | 10.902 | 14.959 | 30.6788 | 14.7083 | 10.7295 | 14.7477 | 30.7445 | 14.6424 | 10.6814 | 14.3978 | 30.8448 | 14.5014 | 10.5786 | 14.0312 | 30.9699 | 14.3052 | 10.4354 | 13.5802 | 31.122 | 14.1618 | 10.3309 | 13.1267 | 31.2906 | 14.0681 | 10.2625 | 12.64 | 31.4795 | 13.9276 | 10.16 | 12.0816 | 31.7193 | 13.6519 | 9.9589 | 10.8714 | 32.5229 | 12.8529 | 9.376 | 5.2115 | 33.0257 | 11.6482 | 8.4972 | 0.96316 | 33.2169 | 10.991 | 8.0178 | -1.2582 | 33.1785 | 10.9206 | 7.9664 | -0.64592
NEWBIGGIN ON LUNE | PENRITH & SHAP | HARKER / HUTTON | 369770 | 505803 | 3.1255 | 3.1255 | 3.1255 | 2.0688 | 3.1403 | 3.1403 | 3.1403 | 1.9933 | 3.1642 | 3.1642 | 3.1642 | 1.9656 | 3.1898 | 3.1898 | 3.1898 | 1.906 | 3.2177 | 3.2177 | 3.2177 | 1.8812 | 3.2484 | 3.2484 | 3.2484 | 1.8204 | 3.266 | 3.266 | 3.266 | 1.7487 | 3.2811 | 3.2811 | 3.2811 | 1.7063 | 3.2978 | 3.2978 | 3.2978 | 1.6252 | 3.3177 | 3.3177 | 3.3177 | 1.5231 | 3.3887 | 3.3887 | 3.3887 | 1.1614 | 3.4362 | 3.4362 | 3.4362 | 0.98327 | 3.4613 | 3.4613 | 3.4613 | 0.90075 | 3.4705 | 3.4705 | 3.4705 | 0.984 | 3.1266 | 3.1266 | 3.1266 | 2.0871 | 3.1413 | 3.1413 | 3.1413 | 2.0299 | 3.1616 | 3.1616 | 3.1616 | 1.9999 | 3.179 | 3.179 | 3.179 | 1.955 | 3.198 | 3.198 | 3.198 | 1.9341 | 3.22 | 3.22 | 3.22 | 1.8798 | 3.2474 | 3.2474 | 3.2474 | 1.8178 | 3.276 | 3.276 | 3.276 | 1.7795 | 3.3056 | 3.3056 | 3.3056 | 1.7111 | 3.3352 | 3.3352 | 3.3352 | 1.6496 | 3.3647 | 3.3647 | 3.3647 | 1.4591 | 3.3908 | 3.3908 | 3.3908 | 1.2172 | 3.4085 | 3.4085 | 3.4085 | 1.0079 | 3.4187 | 3.4187 | 3.4187 | 0.8828 | 3.1255 | 3.1255 | 3.1255 | 2.0698 | 3.1403 | 3.1403 | 3.1403 | 1.9982 | 3.1642 | 3.1642 | 3.1642 | 1.9684 | 3.1898 | 3.1898 | 3.1898 | 1.9115 | 3.2175 | 3.2175 | 3.2175 | 1.8883 | 3.2479 | 3.2479 | 3.2479 | 1.8298 | 3.2658 | 3.2658 | 3.2658 | 1.7603 | 3.2809 | 3.2809 | 3.2809 | 1.7189 | 3.2974 | 3.2974 | 3.2974 | 1.6422 | 3.3163 | 3.3163 | 3.3163 | 1.5519 | 3.3831 | 3.3831 | 3.3831 | 1.2348 | 3.4271 | 3.4271 | 3.4271 | 1.0867 | 3.4505 | 3.4505 | 3.4505 | 1.024 | 3.4593 | 3.4593 | 3.4593 | 1.1027 | 3.1258 | 3.1258 | 3.1258 | 2.0699 | 3.1427 | 3.1427 | 3.1427 | 1.9903 | 3.1698 | 3.1698 | 3.1698 | 1.9589 | 3.1999 | 3.1999 | 3.1999 | 1.8977 | 3.2355 | 3.2355 | 3.2355 | 1.8643 | 3.2642 | 3.2642 | 3.2642 | 1.7917 | 3.2854 | 3.2854 | 3.2854 | 1.7043 | 3.3092 | 3.3092 | 3.3092 | 1.6515 | 3.3358 | 3.3358 | 3.3358 | 1.5728 | 3.3658 | 3.3658 | 3.3658 | 1.5063 | 3.4572 | 3.4572 | 3.4572 | 1.2311 | 3.5083 | 3.5083 | 3.5083 | 1.082 | 3.5226 | 3.5226 | 3.5226 | 0.99607 | 3.5254 | 3.5254 | 3.5254 | 0.95626 | 3.1346 | 3.1346 | 3.1346 | 2.0617 | 3.1602 | 3.1602 | 3.1602 | 1.9749 | 3.1891 | 3.1891 | 3.1891 | 1.94 | 3.2194 | 3.2194 | 3.2194 | 1.8781 | 3.2467 | 3.2467 | 3.2467 | 1.8374 | 3.2614 | 3.2614 | 3.2614 | 1.7632 | 3.2809 | 3.2809 | 3.2809 | 1.6811 | 3.3019 | 3.3019 | 3.3019 | 1.637 | 3.3247 | 3.3247 | 3.3247 | 1.5679 | 3.35 | 3.35 | 3.35 | 1.4978 | 3.4236 | 3.4236 | 3.4236 | 1.2022 | 3.4536 | 3.4536 | 3.4536 | 1.0977 | 3.4507 | 3.4507 | 3.4507 | 1.1256 | 3.4403 | 3.4403 | 3.4403 | 1.2165
NEWBY | PENRITH & SHAP | HARKER / HUTTON | 360520 | 521151 | 15.6588 | 15.6588 | 15.6588 | 8.3792 | 15.6991 | 15.6991 | 15.6991 | 8.2117 | 15.7355 | 15.7355 | 15.7355 | 8.1545 | 15.787 | 15.787 | 15.787 | 8.069 | 15.8515 | 15.8515 | 15.8515 | 7.9686 | 15.9274 | 15.9274 | 15.9274 | 7.8089 | 16.0178 | 16.0178 | 16.0178 | 7.6505 | 16.1151 | 16.1151 | 16.1151 | 7.5057 | 16.2177 | 16.2177 | 16.2177 | 7.3523 | 16.3323 | 16.3323 | 16.3323 | 7.1577 | 16.625 | 16.625 | 16.625 | 6.22 | 16.8146 | 16.8146 | 16.8146 | 5.6424 | 16.9158 | 16.9158 | 16.9158 | 5.3176 | 16.9803 | 16.9803 | 16.9803 | 5.4186 | 15.6465 | 15.6465 | 15.6465 | 8.4479 | 15.6785 | 15.6785 | 15.6785 | 8.3363 | 15.7289 | 15.7289 | 15.7289 | 8.2048 | 15.7848 | 15.7848 | 15.7848 | 8.05 | 15.8477 | 15.8477 | 15.8477 | 7.8851 | 15.9181 | 15.9181 | 15.9181 | 7.6577 | 15.9994 | 15.9994 | 15.9994 | 7.3557 | 16.0843 | 16.0843 | 16.0843 | 7.0392 | 16.1664 | 16.1664 | 16.1664 | 6.6988 | 16.253 | 16.253 | 16.253 | 6.2676 | 16.4859 | 16.4859 | 16.4859 | 5.9763 | 16.6315 | 16.6315 | 16.6315 | 5.783 | 16.707 | 16.707 | 16.707 | 5.5182 | 16.7504 | 16.7504 | 16.7504 | 5.1655 | 15.6588 | 15.6588 | 15.6588 | 8.3911 | 15.6991 | 15.6991 | 15.6991 | 8.2297 | 15.7356 | 15.7356 | 15.7356 | 8.1816 | 15.7872 | 15.7872 | 15.7872 | 8.1057 | 15.8515 | 15.8515 | 15.8515 | 8.0156 | 15.9269 | 15.9269 | 15.9269 | 7.8662 | 16.0169 | 16.0169 | 16.0169 | 7.7091 | 16.114 | 16.114 | 16.114 | 7.5997 | 16.215 | 16.215 | 16.215 | 7.4414 | 16.3234 | 16.3234 | 16.3234 | 7.2177 | 16.6034 | 16.6034 | 16.6034 | 6.3769 | 16.7567 | 16.7567 | 16.7567 | 5.8835 | 16.8464 | 16.8464 | 16.8464 | 5.6215 | 16.8842 | 16.8842 | 16.8842 | 5.7178 | 15.6567 | 15.6567 | 15.6567 | 8.3901 | 15.697 | 15.697 | 15.697 | 8.2338 | 15.7382 | 15.7382 | 15.7382 | 8.1947 | 15.802 | 15.802 | 15.802 | 8.0994 | 15.8872 | 15.8872 | 15.8872 | 7.9817 | 15.9936 | 15.9936 | 15.9936 | 7.7657 | 16.1283 | 16.1283 | 16.1283 | 7.5095 | 16.2807 | 16.2807 | 16.2807 | 7.3107 | 16.4455 | 16.4455 | 16.4455 | 7.1211 | 16.5403 | 16.5403 | 16.5403 | 6.8949 | 16.8552 | 16.8552 | 16.8552 | 5.9375 | 17.0768 | 17.0768 | 17.0768 | 4.6011 | 17.1692 | 17.1692 | 17.1692 | 3.7798 | 17.1911 | 17.1911 | 17.1911 | 3.2169 | 15.6594 | 15.6594 | 15.6594 | 8.3971 | 15.7103 | 15.7103 | 15.7103 | 8.2392 | 15.7571 | 15.7571 | 15.7571 | 8.2096 | 15.8204 | 15.8204 | 15.8204 | 8.1249 | 15.9046 | 15.9046 | 15.9046 | 8 | 16.0052 | 16.0052 | 16.0052 | 7.7929 | 16.1361 | 16.1361 | 16.1361 | 7.5653 | 16.2781 | 16.2781 | 16.2781 | 7.402 | 16.3495 | 16.3495 | 16.3495 | 7.2431 | 16.4653 | 16.4653 | 16.4653 | 6.8573 | 16.7871 | 16.7871 | 16.7871 | 5.1569 | 16.9494 | 16.9494 | 16.9494 | 4.0101 | 16.9699 | 16.9699 | 16.9699 | 3.4723 | 16.9148 | 16.9148 | 16.9148 | 3.7082
NEWTON | HYDE | STALYBRIDGE | 396385 | 396464 | 13.1221 | 13.1221 | 9.931 | 13.1221 | 13.136 | 13.136 | 9.8802 | 13.136 | 13.1678 | 13.1678 | 9.8231 | 13.1678 | 13.2035 | 13.2035 | 9.7402 | 13.2035 | 13.2465 | 13.2465 | 9.6533 | 13.2465 | 13.2946 | 13.2946 | 9.5992 | 13.2946 | 13.3505 | 13.3117 | 9.5674 | 13.3505 | 13.4119 | 13.2327 | 9.5106 | 13.4119 | 13.4782 | 13.1215 | 9.4307 | 13.4782 | 13.5542 | 12.9987 | 9.3424 | 13.5542 | 13.8513 | 12.8557 | 9.2397 | 13.8513 | 14.0673 | 13.0081 | 9.3492 | 14.0673 | 14.1909 | 13.5329 | 9.7263 | 14.1909 | 14.281 | 13.5637 | 9.7485 | 14.281 | 13.1294 | 13.1294 | 9.939 | 13.1294 | 13.1477 | 13.1477 | 9.8879 | 13.1477 | 13.1742 | 13.1742 | 9.9447 | 13.1742 | 13.1991 | 13.1991 | 9.9522 | 13.1991 | 13.2273 | 13.2273 | 9.93 | 13.2273 | 13.26 | 13.26 | 9.8934 | 13.26 | 13.2973 | 13.2973 | 9.8631 | 13.2973 | 13.3374 | 13.3374 | 9.833 | 13.3374 | 13.3801 | 13.3801 | 9.7998 | 13.3801 | 13.4244 | 13.4244 | 9.7653 | 13.4244 | 13.5697 | 13.4615 | 9.675 | 13.5697 | 13.6761 | 13.5678 | 9.7515 | 13.6761 | 13.7567 | 13.7567 | 9.9989 | 13.7567 | 13.8199 | 13.8199 | 10.0413 | 13.8199 | 13.1221 | 13.1221 | 9.9358 | 13.1221 | 13.1361 | 13.1361 | 9.9135 | 13.1361 | 13.1679 | 13.1679 | 9.9626 | 13.1679 | 13.2038 | 13.2038 | 9.9494 | 13.2038 | 13.2466 | 13.2466 | 9.9108 | 13.2466 | 13.2944 | 13.2944 | 9.8699 | 13.2944 | 13.3501 | 13.3501 | 9.8328 | 13.3501 | 13.4113 | 13.4113 | 9.7936 | 13.4113 | 13.4766 | 13.4766 | 9.753 | 13.4766 | 13.5483 | 13.5133 | 9.7123 | 13.5483 | 13.82 | 13.317 | 9.5712 | 13.82 | 13.9968 | 13.4876 | 9.6938 | 13.9968 | 14.1025 | 14.1025 | 10.148 | 14.1025 | 14.1669 | 14.1624 | 10.1788 | 14.1669 | 13.1238 | 13.1238 | 9.9311 | 13.1238 | 13.1402 | 13.1402 | 9.8764 | 13.1402 | 13.1758 | 13.1758 | 9.8101 | 13.1758 | 13.2166 | 13.2166 | 9.7018 | 13.2166 | 13.2666 | 13.2666 | 9.6552 | 13.2666 | 13.3248 | 13.3248 | 9.613 | 13.3248 | 13.3957 | 13.2801 | 9.5446 | 13.3957 | 13.4761 | 13.1911 | 9.4807 | 13.4761 | 13.5643 | 13.0509 | 9.3799 | 13.5643 | 13.6635 | 12.9912 | 9.337 | 13.6635 | 14.0841 | 12.7405 | 9.1568 | 14.0841 | 14.4623 | 12.5306 | 9.006 | 13.6303 | 14.4674 | 12.6997 | 9.1275 | 12.5382 | 14.3914 | 12.5868 | 9.0464 | 11.8584 | 13.1295 | 13.1295 | 9.9297 | 13.1295 | 13.1567 | 13.1567 | 9.8909 | 13.1567 | 13.1988 | 13.1988 | 9.8383 | 13.1988 | 13.2433 | 13.2433 | 9.7436 | 13.2433 | 13.2963 | 13.2963 | 9.6551 | 13.2963 | 13.3555 | 13.3555 | 9.6231 | 13.3555 | 13.4291 | 13.3194 | 9.5729 | 13.4291 | 13.5096 | 13.2431 | 9.5181 | 13.5096 | 13.6016 | 13.1347 | 9.4402 | 13.6016 | 13.7464 | 13.0145 | 9.3538 | 13.7464 | 14.3144 | 13.7186 | 9.8598 | 13.8459 | 14.4729 | 13.1808 | 9.4733 | 12.489 | 14.4257 | 12.854 | 9.2384 | 11.779 | 14.2574 | 12.8012 | 9.2005 | 12.1706
NEWTON HEATH | CHADDERTON | WHITEGATE | 388030 | 400511 | 12.1385 | 12.1385 | 12.1385 | 1.9018 | 12.1873 | 12.1873 | 12.1873 | 1.4188 | 12.2259 | 12.2259 | 12.2259 | 1.1667 | 12.2746 | 12.2746 | 12.2746 | 0.977 | 12.3374 | 12.3374 | 12.3374 | 0.81301 | 12.3975 | 12.3975 | 12.3975 | 0.57689 | 12.4649 | 12.4649 | 12.4649 | 0.33598 | 12.5376 | 12.5376 | 12.5376 | 0.064591 | 12.615 | 12.615 | 12.615 | -0.22432 | 12.7014 | 12.7014 | 12.7014 | -0.55015 | 13.0004 | 13.0004 | 13.0004 | -1.7576 | 13.2198 | 13.2198 | 13.2198 | -2.449 | 13.3496 | 13.3496 | 13.3496 | -2.6849 | 13.4376 | 13.4376 | 13.4376 | -2.6655 | 12.1249 | 12.1249 | 12.1249 | 2.1345 | 12.1623 | 12.1623 | 12.1623 | 1.8621 | 12.2138 | 12.2138 | 12.2138 | 1.6384 | 12.2562 | 12.2562 | 12.2562 | 1.4435 | 12.3169 | 12.3169 | 12.3169 | 1.2946 | 12.3837 | 12.3837 | 12.3837 | 1.0733 | 12.4505 | 12.4505 | 12.4505 | 0.84362 | 12.522 | 12.522 | 12.522 | 0.58267 | 12.5983 | 12.5983 | 12.5983 | 0.30252 | 12.6791 | 12.6791 | 12.6791 | 0.030104 | 12.8548 | 12.8548 | 12.8548 | -0.84778 | 12.9969 | 12.9969 | 12.9969 | -1.5187 | 13.0978 | 13.0978 | 13.0978 | -1.9183 | 13.1666 | 13.1666 | 13.1666 | -2.1929 | 12.1385 | 12.1385 | 12.1385 | 1.9152 | 12.1874 | 12.1874 | 12.1874 | 1.4409 | 12.226 | 12.226 | 12.226 | 1.2059 | 12.2748 | 12.2748 | 12.2748 | 1.0269 | 12.3374 | 12.3374 | 12.3374 | 0.871 | 12.3973 | 12.3973 | 12.3973 | 0.64881 | 12.4645 | 12.4645 | 12.4645 | 0.42146 | 12.537 | 12.537 | 12.537 | 0.16392 | 12.6136 | 12.6136 | 12.6136 | -0.10626 | 12.6961 | 12.6961 | 12.6961 | -0.39693 | 12.9762 | 12.9762 | 12.9762 | -1.4869 | 13.1673 | 13.1673 | 13.1673 | -2.0838 | 13.2834 | 13.2834 | 13.2834 | -2.2649 | 13.354 | 13.354 | 13.354 | -2.2184 | 12.1398 | 12.1398 | 12.1398 | 1.9037 | 12.1959 | 12.1959 | 12.1959 | 1.4202 | 12.2532 | 12.2532 | 12.2532 | 1.1635 | 12.3011 | 12.3011 | 12.3011 | 0.96206 | 12.3652 | 12.3652 | 12.3652 | 0.80575 | 12.4436 | 12.4436 | 12.4436 | 0.56577 | 12.5266 | 12.5266 | 12.5266 | 0.2975 | 12.6193 | 12.6193 | 12.6193 | -0.0062914 | 12.7198 | 12.7198 | 12.7198 | -0.28357 | 12.8313 | 12.8313 | 12.8313 | -0.55257 | 13.2359 | 13.2359 | 13.2359 | -2.2243 | 13.6721 | 13.6721 | 13.6721 | -5.725 | 13.9488 | 13.9488 | 13.9488 | -8.4461 | 14.1142 | 14.1142 | 14.1142 | -10.3845 | 12.1341 | 12.1341 | 12.1341 | 1.9149 | 12.1898 | 12.1898 | 12.1898 | 1.4183 | 12.2484 | 12.2484 | 12.2484 | 1.1842 | 12.2939 | 12.2939 | 12.2939 | 0.99927 | 12.3438 | 12.3438 | 12.3438 | 0.83612 | 12.4035 | 12.4035 | 12.4035 | 0.62216 | 12.4773 | 12.4773 | 12.4773 | 0.38972 | 12.5581 | 12.5581 | 12.5581 | 0.12934 | 12.6495 | 12.6495 | 12.6495 | -0.18924 | 12.7872 | 12.7872 | 12.7872 | -1.0294 | 13.3035 | 13.3035 | 13.3035 | -4.984 | 13.6591 | 13.6591 | 13.6591 | -8.1425 | 13.8134 | 13.8134 | 13.8134 | -9.9783 | 13.7636 | 13.7636 | 13.7636 | -9.5763
NEWTON LE WILLOWS | GOLBORNE | BOLD | 357891 | 395944 | 27.5985 | 12.141 | 8.726 | 13.0347 | 27.7292 | 11.9073 | 8.558 | 12.7289 | 27.9276 | 11.5376 | 8.2923 | 12.4628 | 27.9919 | 11.1132 | 7.9873 | 12.1037 | 28.0805 | 10.6788 | 7.6751 | 11.7125 | 28.1913 | 10.3241 | 7.4201 | 11.164 | 28.3178 | 10.1687 | 7.3084 | 10.6041 | 28.4559 | 10.0129 | 7.1964 | 10.0531 | 28.6041 | 9.8572 | 7.0846 | 9.5121 | 28.7672 | 9.6637 | 6.9455 | 8.8271 | 29.6512 | 9.0932 | 6.5355 | 6.4966 | 30.7039 | 9.0839 | 6.5288 | 5.1665 | 31.5333 | 10.0713 | 7.2384 | 4.7156 | 32.4074 | 10.3371 | 7.4295 | 4.4435 | 27.6085 | 12.2246 | 8.786 | 13.1979 | 27.7515 | 11.9528 | 8.5907 | 13.023 | 27.874 | 11.6729 | 8.3896 | 12.6771 | 27.9619 | 11.3967 | 8.191 | 12.3243 | 28.0628 | 11.1439 | 8.0093 | 11.976 | 28.1764 | 11.0089 | 7.9123 | 11.4836 | 28.3032 | 10.8968 | 7.8318 | 10.9786 | 28.439 | 10.7888 | 7.7542 | 10.4803 | 28.585 | 10.6777 | 7.6742 | 9.9816 | 28.7398 | 10.5522 | 7.5841 | 9.3982 | 29.2168 | 10.2262 | 7.3498 | 7.7551 | 29.7353 | 10.2584 | 7.3729 | 6.6063 | 30.2837 | 10.8532 | 7.8004 | 5.8968 | 30.7686 | 11.0644 | 7.9522 | 5.4575 | 27.5988 | 12.2192 | 8.7822 | 13.048 | 27.7299 | 11.7706 | 8.4598 | 12.7542 | 27.9292 | 11.2915 | 8.1154 | 12.5005 | 27.9946 | 10.8372 | 7.7889 | 12.1528 | 28.0842 | 10.4102 | 7.482 | 11.7761 | 28.1956 | 10.073 | 7.2397 | 11.2449 | 28.3228 | 9.9354 | 7.1408 | 10.7015 | 28.4616 | 9.8017 | 7.0447 | 10.1661 | 28.6089 | 9.6623 | 6.9445 | 9.6491 | 28.7652 | 9.5233 | 6.8446 | 9.0225 | 29.529 | 9.0822 | 6.5275 | 6.9936 | 30.2393 | 9.2223 | 6.6283 | 5.992 | 30.8959 | 10.2902 | 7.3957 | 5.6766 | 31.4575 | 10.4896 | 7.5391 | 5.7079 | 27.597 | 12.1474 | 8.7306 | 13.0439 | 27.7277 | 11.8969 | 8.5505 | 12.7494 | 27.9329 | 11.505 | 8.2688 | 12.4979 | 28.0171 | 11.071 | 7.957 | 12.1524 | 28.1369 | 10.6503 | 7.6546 | 11.8043 | 28.3043 | 10.2899 | 7.3955 | 11.3037 | 28.5159 | 10.1136 | 7.2688 | 10.7875 | 28.7656 | 9.9331 | 7.1391 | 10.2789 | 29.0477 | 9.7228 | 6.988 | 9.8449 | 29.3659 | 9.5694 | 6.8777 | 9.3256 | 31.0598 | 8.7788 | 6.3095 | 6.2201 | 32.8895 | 7.7873 | 5.5969 | -0.027101 | 34.0071 | 7.7977 | 5.6044 | -4.9821 | 34.5327 | 7.4092 | 5.3251 | -8.2657 | 27.6156 | 12.155 | 8.7361 | 13.0394 | 27.8045 | 11.7233 | 8.4258 | 12.6955 | 27.9481 | 11.4033 | 8.1958 | 12.4252 | 28.0359 | 11.0807 | 7.9639 | 12.1009 | 28.159 | 10.7268 | 7.7096 | 11.7933 | 28.3391 | 10.4156 | 7.4859 | 11.3481 | 28.5817 | 10.2682 | 7.38 | 10.8671 | 28.8682 | 10.1384 | 7.2867 | 10.4044 | 29.2025 | 9.9915 | 7.1811 | 9.8468 | 29.619 | 9.694 | 6.9673 | 8.3154 | 31.5586 | 9.6499 | 6.9356 | 1.3451 | 33.1295 | 8.2207 | 5.9083 | -4.2912 | 33.7831 | 7.8092 | 5.6126 | -7.5802 | 33.812 | 7.7214 | 5.5495 | -6.7928
NEWTONGATE T11 & T12 | PENRITH & SHAP | HARKER / HUTTON | 349973 | 530340 | 33.2076 | 8.2758 | 5.948 | 9.9 | 33.3384 | 7.938 | 5.7052 | 9.3438 | 33.3618 | 7.5301 | 5.412 | 8.9619 | 33.4345 | 7.2503 | 5.2109 | 8.6524 | 33.5375 | 6.7619 | 4.8599 | 8.3501 | 33.6754 | 6.5981 | 4.7422 | 8.0584 | 33.8348 | 6.3145 | 4.5383 | 7.4847 | 34.0086 | 6.0225 | 4.3285 | 7.2336 | 34.1908 | 5.7461 | 4.1299 | 6.8924 | 31.7148 | 5.2216 | 3.7529 | 6.2847 | 21.8148 | 3.5916 | 2.5814 | -0.83291 | 12.6441 | 2.0818 | 1.4962 | -6.4498 | 8.2786 | 1.363 | 0.97962 | -8.3836 | 5.3088 | 0.87406 | 0.6282 | -9.3145 | 33.1124 | 8.3723 | 6.0174 | 10.4024 | 33.1772 | 8.2528 | 5.9314 | 10.2738 | 33.2918 | 8.1345 | 5.8464 | 9.824 | 33.4421 | 7.9828 | 5.7374 | 9.4567 | 33.6021 | 7.8217 | 5.6216 | 9.1315 | 33.7636 | 7.7154 | 5.5452 | 8.8458 | 33.9473 | 7.5875 | 5.4533 | 8.2773 | 34.147 | 7.4818 | 5.3773 | 7.9707 | 34.3605 | 7.3795 | 5.3038 | 7.5912 | 34.5786 | 7.2109 | 5.1826 | 6.9952 | 35.4478 | 6.6949 | 4.8117 | 5.3687 | 36.3651 | 5.9872 | 4.3031 | 3.5858 | 33.367 | 5.4936 | 3.9484 | 2.0528 | 30.7299 | 5.0594 | 3.6363 | 0.95167 | 33.2091 | 8.3629 | 6.0106 | 9.9082 | 33.3418 | 8.1272 | 5.8412 | 9.3674 | 33.3677 | 7.7865 | 5.5963 | 9.0037 | 33.4436 | 7.4725 | 5.3706 | 8.7094 | 33.55 | 7.087 | 5.0935 | 8.4224 | 33.6904 | 6.7311 | 4.8378 | 8.145 | 33.8519 | 6.366 | 4.5754 | 7.5887 | 34.0273 | 6.1302 | 4.4059 | 7.3506 | 34.21 | 5.8758 | 4.223 | 7.0328 | 32.0451 | 5.276 | 3.792 | 6.4651 | 29.7804 | 4.9031 | 3.524 | -0.25312 | 24.9614 | 4.1097 | 2.9537 | -5.0088 | 20.9247 | 3.4451 | 2.4761 | -6.4918 | 17.4465 | 2.8724 | 2.0645 | -6.7414 | 33.1985 | 8.2742 | 5.9468 | 9.9167 | 33.3231 | 7.9385 | 5.7056 | 9.3666 | 33.3488 | 7.5007 | 5.3909 | 8.9847 | 33.4363 | 6.992 | 5.0253 | 8.6614 | 33.5665 | 6.8265 | 4.9063 | 8.3278 | 33.7826 | 6.4246 | 4.6175 | 7.9601 | 34.0677 | 5.9649 | 4.2871 | 7.2433 | 33.9505 | 5.5897 | 4.0174 | 6.8251 | 29.2708 | 4.8192 | 3.4637 | 6.328 | 29.6234 | 4.8773 | 3.5054 | 5.5716 | 11.4513 | 1.8854 | 1.3551 | -6.5334 | 2.6844 | 0.44197 | 0.31765 | -15.7211 | 2.6844 | 0.44197 | 0.31765 | -20.1361 | 2.6844 | 0.44197 | 0.31765 | -22.0072 | 33.1936 | 8.2739 | 5.9466 | 9.8985 | 33.3257 | 7.9732 | 5.7305 | 9.3015 | 33.3646 | 7.5867 | 5.4527 | 8.8924 | 33.4639 | 7.2295 | 5.1959 | 8.5543 | 33.6122 | 6.8329 | 4.911 | 8.1798 | 33.8876 | 6.2657 | 4.5032 | 7.7665 | 34.2711 | 5.729 | 4.1176 | 6.9898 | 33.5832 | 5.5292 | 3.974 | 6.5008 | 31.5234 | 5.1901 | 3.7302 | 5.8563 | 27.3073 | 4.4959 | 3.2313 | 3.461 | 3.6932 | 0.60806 | 0.43702 | -13.8476 | 2.6844 | 0.44197 | 0.31765 | -18.8472 | 2.6844 | 0.44197 | 0.31765 | -21.9144 | 2.6844 | 0.44197 | 0.31765 | -20.8848
NEWTONGATE T13 | PENRITH & SHAP | HARKER / HUTTON | 349973 | 530340 | 14.5235 | 14.5235 | 14.5235 | 10.9647 | 14.547 | 14.547 | 14.547 | 10.6193 | 14.5549 | 14.5549 | 14.5549 | 10.6391 | 14.5782 | 14.5782 | 14.5782 | 10.4826 | 14.6102 | 14.6102 | 14.6102 | 10.5001 | 14.6526 | 14.6526 | 14.6526 | 10.2842 | 14.7028 | 14.7028 | 14.6751 | 10.1059 | 14.7589 | 14.7589 | 14.4954 | 10.0638 | 14.8199 | 14.8199 | 14.4853 | 9.8301 | 14.8887 | 14.8887 | 14.4138 | 9.6256 | 15.3722 | 15.3722 | 14.2521 | 8.8196 | 16.0694 | 16.0694 | 15.2601 | 8.0488 | 16.6166 | 16.6166 | 16.6166 | 7.4652 | 17.2162 | 17.2162 | 17.2162 | 7.0708 | 14.5196 | 14.5196 | 14.5196 | 11.0436 | 14.5446 | 14.5446 | 14.5446 | 10.7651 | 14.5809 | 14.5809 | 14.5809 | 10.7359 | 14.6302 | 14.6302 | 14.6302 | 10.5421 | 14.6874 | 14.6874 | 14.6874 | 10.5263 | 14.7542 | 14.7542 | 14.7542 | 10.2789 | 14.8316 | 14.8316 | 14.8316 | 10.0615 | 14.901 | 14.901 | 14.901 | 9.9767 | 14.976 | 14.976 | 14.976 | 9.6919 | 15.0575 | 15.0575 | 15.0575 | 9.4641 | 15.419 | 15.419 | 15.419 | 8.914 | 15.8498 | 15.8498 | 15.8498 | 8.344 | 16.2542 | 16.2542 | 16.2542 | 7.7952 | 16.6095 | 16.6095 | 16.6095 | 7.3983 | 14.5248 | 14.5248 | 14.5248 | 10.9703 | 14.5492 | 14.5492 | 14.5492 | 10.6406 | 14.558 | 14.558 | 14.558 | 10.671 | 14.5824 | 14.5824 | 14.5824 | 10.526 | 14.6154 | 14.6154 | 14.6154 | 10.5529 | 14.6582 | 14.6582 | 14.6582 | 10.3514 | 14.7082 | 14.7082 | 14.6121 | 10.1866 | 14.7636 | 14.7636 | 14.6188 | 10.1547 | 14.8231 | 14.8231 | 14.5421 | 9.939 | 14.8885 | 14.8885 | 14.4752 | 9.7592 | 15.2867 | 15.2867 | 14.409 | 9.0676 | 15.7105 | 15.7105 | 15.465 | 8.5109 | 16.1276 | 16.1276 | 16.1276 | 8.0468 | 16.4783 | 16.4783 | 16.4783 | 7.8194 | 14.5233 | 14.5233 | 14.5233 | 10.9672 | 14.5463 | 14.5463 | 14.5463 | 10.6237 | 14.5552 | 14.5552 | 14.5552 | 10.6434 | 14.5827 | 14.5827 | 14.5827 | 10.4792 | 14.6208 | 14.6208 | 14.6208 | 10.4947 | 14.6849 | 14.6849 | 14.6767 | 10.266 | 14.7729 | 14.7729 | 14.4398 | 10.0541 | 14.8782 | 14.8782 | 14.433 | 9.9714 | 14.9984 | 14.9984 | 14.3161 | 9.7132 | 15.1365 | 15.1365 | 14.1903 | 9.512 | 16.1345 | 16.1345 | 13.8403 | 8.1227 | 17.3699 | 17.3699 | 14.4739 | 5.3123 | 18.2157 | 18.2157 | 15.9307 | 2.9943 | 18.6326 | 18.6326 | 16.0287 | 1.4823 | 14.5167 | 14.5167 | 14.5167 | 10.9935 | 14.5364 | 14.5364 | 14.5364 | 10.6694 | 14.5455 | 14.5455 | 14.5455 | 10.7021 | 14.5727 | 14.5727 | 14.5727 | 10.5571 | 14.6126 | 14.6126 | 14.6126 | 10.5842 | 14.6914 | 14.6914 | 14.6914 | 10.369 | 14.8056 | 14.8056 | 14.8056 | 10.1686 | 14.951 | 14.951 | 14.951 | 10.0906 | 15.1274 | 15.1274 | 15.1274 | 9.7789 | 15.3448 | 15.3448 | 15.3448 | 9.1714 | 16.5611 | 16.5611 | 16.5611 | 6.2296 | 17.7004 | 17.7004 | 16.7794 | 3.6526 | 18.2735 | 18.2735 | 16.3869 | 2.0124 | 18.3836 | 18.3836 | 16.2647 | 2.1217
NORBRECK | BISPHAM | PENWORTHAM WEST / STANAH | 331831 | 441463 | 28.4553 | 12.8477 | 9.3722 | 22.9069 | 28.4617 | 12.7333 | 9.2887 | 22.8442 | 28.4689 | 12.2371 | 8.9268 | 22.7904 | 28.4864 | 12.0285 | 8.7746 | 22.6827 | 28.5115 | 11.7118 | 8.5436 | 22.5873 | 28.542 | 11.5083 | 8.3952 | 22.4467 | 28.5776 | 11.4269 | 8.3357 | 22.3057 | 28.6172 | 11.3588 | 8.2861 | 22.148 | 28.6615 | 11.3049 | 8.2468 | 21.9984 | 28.7131 | 11.2318 | 8.1935 | 21.8028 | 28.9244 | 10.9726 | 8.0044 | 21.2128 | 29.0517 | 11.0476 | 8.059 | 20.9765 | 29.1188 | 11.8988 | 8.68 | 21.0099 | 29.1511 | 12.0302 | 8.7759 | 21.1987 | 28.4478 | 13.0914 | 9.55 | 22.9544 | 28.4491 | 12.5486 | 9.154 | 22.9319 | 28.4591 | 12.3881 | 9.0369 | 22.8574 | 28.4734 | 12.002 | 8.7553 | 22.7622 | 28.4908 | 11.6748 | 8.5166 | 22.6933 | 28.5109 | 11.5264 | 8.4083 | 22.5827 | 28.5337 | 11.4843 | 8.3776 | 22.4716 | 28.558 | 11.4407 | 8.3458 | 22.3449 | 28.5839 | 11.3988 | 8.3153 | 22.2275 | 28.6106 | 11.3528 | 8.2817 | 22.0949 | 28.6897 | 11.2239 | 8.1877 | 21.7115 | 28.7527 | 11.2938 | 8.2387 | 21.4287 | 28.7927 | 11.8362 | 8.6343 | 21.2903 | 28.8157 | 12.233 | 8.9238 | 21.2305 | 28.4553 | 13.0896 | 9.5487 | 22.908 | 28.4617 | 12.6569 | 9.2331 | 22.85 | 28.4689 | 12.3592 | 9.0159 | 22.801 | 28.4864 | 11.9461 | 8.7145 | 22.6962 | 28.5114 | 11.6257 | 8.4808 | 22.604 | 28.5416 | 11.4315 | 8.3391 | 22.467 | 28.577 | 11.3604 | 8.2873 | 22.3291 | 28.6165 | 11.2848 | 8.2321 | 22.1742 | 28.6601 | 11.2464 | 8.2041 | 22.0305 | 28.7087 | 11.2154 | 8.1815 | 21.8529 | 28.9062 | 11.1062 | 8.1018 | 21.3282 | 29.0234 | 11.2998 | 8.243 | 21.1324 | 29.0849 | 12.3079 | 8.9784 | 21.1778 | 29.1156 | 12.3893 | 9.0378 | 21.3578 | 28.4544 | 12.8436 | 9.3692 | 22.9133 | 28.461 | 12.7356 | 9.2904 | 22.8581 | 28.4713 | 12.2881 | 8.964 | 22.8169 | 28.4953 | 11.9986 | 8.7528 | 22.7259 | 28.5311 | 11.6997 | 8.5348 | 22.6529 | 28.5779 | 11.4833 | 8.3769 | 22.5348 | 28.6377 | 11.4147 | 8.3269 | 22.4073 | 28.7066 | 11.3467 | 8.2773 | 22.2681 | 28.7827 | 11.2754 | 8.2253 | 22.1602 | 28.8668 | 11.2007 | 8.1708 | 22.0387 | 29.1287 | 10.8311 | 7.9012 | 21.2053 | 29.3609 | 10.555 | 7.6997 | 19.2138 | 29.4877 | 10.9407 | 7.9811 | 17.6455 | 29.5559 | 10.8199 | 7.893 | 16.5779 | 28.4528 | 12.8433 | 9.369 | 22.9127 | 28.4616 | 12.8438 | 9.3694 | 22.8427 | 28.4743 | 12.2119 | 8.9084 | 22.7944 | 28.4986 | 12.349 | 9.0084 | 22.7073 | 28.5366 | 12.0802 | 8.8123 | 22.6298 | 28.5822 | 11.9565 | 8.7221 | 22.5201 | 28.6392 | 11.8881 | 8.6722 | 22.4105 | 28.7023 | 11.8366 | 8.6347 | 22.2956 | 28.7747 | 11.7762 | 8.5905 | 22.1405 | 28.8626 | 11.6398 | 8.4911 | 21.6481 | 29.1433 | 11.7117 | 8.5435 | 19.422 | 29.3082 | 11.1776 | 8.1539 | 17.6193 | 29.3541 | 10.9115 | 7.9598 | 16.6104 | 29.3058 | 10.9318 | 7.9746 | 16.9847
NORBURY | HAZEL GROVE | BREDBURY | 392447 | 385492 | 24.4303 | 4.0223 | 2.8909 | 16.2298 | 23.4511 | 3.861 | 2.775 | 15.8004 | 22.8766 | 3.7665 | 2.707 | 15.5959 | 22.0352 | 3.6279 | 2.6075 | 15.2817 | 21.1411 | 3.4807 | 2.5017 | 14.9341 | 19.6355 | 3.2328 | 2.3235 | 14.4879 | 18.5846 | 3.0598 | 2.1992 | 14.0239 | 17.2408 | 2.8386 | 2.0401 | 13.4204 | 16.5392 | 2.723 | 1.9571 | 12.9092 | 14.9972 | 2.4692 | 1.7746 | 12.2517 | 10.4286 | 1.717 | 1.234 | 10.4286 | 6.4095 | 1.0553 | 0.75845 | 6.4095 | 4.0226 | 0.66229 | 0.476 | 4.0226 | 3.4892 | 0.57447 | 0.41288 | 3.4892 | 24.7738 | 4.0788 | 2.9315 | 16.4997 | 24.0545 | 3.9604 | 2.8464 | 16.2781 | 23.3211 | 3.8396 | 2.7596 | 16.0284 | 22.3669 | 3.6825 | 2.6467 | 15.7288 | 21.521 | 3.5433 | 2.5466 | 15.4419 | 20.5538 | 3.384 | 2.4322 | 15.0771 | 19.5753 | 3.2229 | 2.3164 | 14.723 | 18.8616 | 3.1054 | 2.2319 | 14.2618 | 18.1957 | 2.9958 | 2.1531 | 13.8848 | 17.5644 | 2.8918 | 2.0784 | 13.4873 | 15.3043 | 2.5197 | 1.811 | 12.1629 | 13.6332 | 2.2446 | 1.6132 | 11.4478 | 13.1221 | 2.1605 | 1.5528 | 11.0671 | 12.6672 | 2.0856 | 1.4989 | 11.0254 | 24.7468 | 4.0744 | 2.9283 | 16.2334 | 24.0783 | 3.9643 | 2.8492 | 15.8076 | 23.2319 | 3.8249 | 2.7491 | 15.6121 | 22.1422 | 3.6455 | 2.6201 | 15.3021 | 20.7937 | 3.4235 | 2.4606 | 14.961 | 19.9926 | 3.2916 | 2.3658 | 14.5231 | 19.1327 | 3.1501 | 2.264 | 14.0503 | 18.2576 | 3.006 | 2.1604 | 13.4539 | 17.8974 | 2.9467 | 2.1178 | 12.9582 | 17.0362 | 2.8049 | 2.0159 | 12.3481 | 13.4271 | 2.2107 | 1.5889 | 10.7065 | 11.4166 | 1.8797 | 1.3509 | 9.1275 | 9.9919 | 1.6451 | 1.1824 | 9.1101 | 7.7144 | 1.2701 | 0.91286 | 7.7144 | 24.4527 | 4.026 | 2.8935 | 16.255 | 23.4352 | 3.8584 | 2.7731 | 15.8607 | 22.848 | 3.7617 | 2.7036 | 15.7121 | 22.0418 | 3.629 | 2.6082 | 15.477 | 21.0418 | 3.4644 | 2.4899 | 15.2331 | 19.8911 | 3.2749 | 2.3537 | 14.9149 | 18.7899 | 3.0936 | 2.2234 | 14.6206 | 18.1129 | 2.9822 | 2.1433 | 14.2425 | 17.1067 | 2.8165 | 2.0243 | 13.9832 | 15.3208 | 2.5225 | 1.8129 | 13.4563 | 5.231 | 0.86125 | 0.61899 | 5.231 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.181 | 24.4154 | 4.0198 | 2.8891 | 16.2191 | 23.3314 | 3.8413 | 2.7608 | 15.7505 | 22.9818 | 3.7838 | 2.7195 | 15.5796 | 21.8115 | 3.5911 | 2.581 | 15.367 | 20.7091 | 3.4096 | 2.4505 | 15.1469 | 19.9835 | 3.2901 | 2.3647 | 14.7631 | 13.7596 | 2.2654 | 1.6282 | 10.4101 | 12.0302 | 1.9807 | 1.4236 | 10.2787 | 12.4813 | 2.0549 | 1.4769 | 10.2087 | 11.3277 | 1.865 | 1.3404 | 9.8784 | 3.4 | 0.55978 | 0.40232 | 3.4 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5579 | 2.6844 | 0.44197 | 0.31765 | 2.6844
NORTHENDEN | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 21.4871 | 12.4798 | 9.1038 | 10.8994 | 21.5534 | 12.4059 | 9.0499 | 10.4944 | 21.5946 | 12.347 | 9.007 | 10.2167 | 21.6662 | 12.241 | 8.9297 | 10.0122 | 21.7465 | 12.0388 | 8.7822 | 9.7074 | 21.8488 | 11.808 | 8.6138 | 9.3699 | 21.9692 | 11.7213 | 8.5505 | 8.9612 | 22.1049 | 11.732 | 8.5583 | 8.5719 | 22.2553 | 11.6651 | 8.5095 | 8.1765 | 22.4278 | 11.5095 | 8.396 | 7.692 | 23.354 | 11.054 | 8.0637 | 5.7229 | 24.2156 | 10.6971 | 7.8034 | 4.418 | 24.6344 | 10.45 | 7.6231 | 3.8675 | 24.9297 | 10.2714 | 7.4929 | 3.3223 | 21.4585 | 12.6493 | 9.2275 | 11.0752 | 21.5004 | 12.5607 | 9.1629 | 10.8324 | 21.5711 | 12.4666 | 9.0942 | 10.5527 | 21.6544 | 12.428 | 9.0661 | 10.3561 | 21.7398 | 12.3882 | 9.037 | 10.0797 | 21.8389 | 12.3471 | 9.007 | 9.7734 | 21.953 | 12.3234 | 8.9898 | 9.3977 | 22.0794 | 12.2863 | 8.9627 | 9.0401 | 22.2169 | 12.2429 | 8.931 | 8.6744 | 22.3644 | 12.1789 | 8.8843 | 8.2736 | 23.0164 | 11.8434 | 8.6396 | 6.8334 | 23.5591 | 11.5196 | 8.4034 | 5.6539 | 23.9114 | 11.5703 | 8.4404 | 4.9673 | 24.154 | 11.5265 | 8.4084 | 4.5363 | 21.4947 | 12.6569 | 9.233 | 10.9098 | 21.5636 | 12.5961 | 9.1887 | 10.5181 | 21.6065 | 12.5242 | 9.1362 | 10.2542 | 21.6749 | 12.5196 | 9.1329 | 10.0605 | 21.7539 | 12.484 | 9.1069 | 9.7716 | 21.8535 | 12.4433 | 9.0772 | 9.4517 | 21.9691 | 12.3662 | 9.021 | 9.0625 | 22.0982 | 12.2683 | 8.9496 | 8.6928 | 22.2391 | 12.1524 | 8.865 | 8.3245 | 22.3969 | 11.9984 | 8.7527 | 7.8916 | 23.2381 | 11.7133 | 8.5447 | 6.1103 | 23.9458 | 11.4295 | 8.3376 | 5.082 | 24.2576 | 11.0769 | 8.0805 | 4.7456 | 24.4322 | 11.0316 | 8.0474 | 4.7724 | 21.4943 | 12.4761 | 9.1012 | 10.897 | 21.5633 | 12.3845 | 9.0343 | 10.4932 | 21.6136 | 12.2956 | 8.9695 | 10.2195 | 21.6924 | 12.2002 | 8.8999 | 10.0158 | 21.7895 | 11.9744 | 8.7352 | 9.7288 | 21.9272 | 11.6998 | 8.5349 | 9.4011 | 22.1052 | 11.7593 | 8.5782 | 8.9753 | 22.3148 | 11.7087 | 8.5414 | 8.5682 | 22.5474 | 11.5887 | 8.4538 | 8.2032 | 22.8091 | 11.3882 | 8.3075 | 7.8039 | 24.0275 | 10.8776 | 7.9351 | 5.417 | 25.0615 | 9.7177 | 7.0889 | 0.94508 | 25.4858 | 8.8407 | 6.4492 | -3.2556 | 25.6837 | 8.277 | 6.0379 | -5.7963 | 21.4912 | 12.4765 | 9.1015 | 10.9004 | 21.5678 | 12.3446 | 9.0052 | 10.474 | 21.6225 | 12.2004 | 8.9 | 10.1983 | 21.694 | 11.993 | 8.7487 | 10.0112 | 21.796 | 11.964 | 8.7276 | 9.7297 | 21.9472 | 11.9529 | 8.7195 | 9.4205 | 22.1496 | 11.8547 | 8.6478 | 9.0196 | 22.3908 | 11.7162 | 8.5468 | 8.641 | 22.6737 | 11.5247 | 8.4071 | 8.2389 | 23.0623 | 11.124 | 8.1148 | 7.2937 | 24.233 | 10.3997 | 7.5864 | 2.8445 | 24.9811 | 9.2168 | 6.7236 | -0.78588 | 25.1842 | 8.9361 | 6.5187 | -3.0675 | 25.0715 | 8.6126 | 6.2828 | -4.1352
NWGB PARTINGTON | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 22.1126 | 12.3962 | 9.0428 | 15.7981 | 22.1356 | 12.0449 | 8.7866 | 15.4237 | 22.1511 | 11.7145 | 8.5456 | 15.1784 | 22.1784 | 11.371 | 8.295 | 15.0809 | 22.2152 | 11.0344 | 8.0495 | 15.0379 | 22.2635 | 10.9346 | 7.9767 | 14.9014 | 22.3215 | 10.8793 | 7.9363 | 14.7472 | 22.3802 | 10.911 | 7.9594 | 14.6076 | 23.5544 | 10.7514 | 7.843 | 13.3232 | 23.6074 | 10.7482 | 7.8407 | 13.163 | 27.0072 | 10.237 | 7.4678 | 9.3727 | 29.7862 | 10.0454 | 7.328 | 6.4041 | 29.8317 | 11.744 | 8.5671 | 6.3093 | 30.1505 | 11.8066 | 8.6128 | 5.9375 | 22.1018 | 12.5767 | 9.1746 | 15.9832 | 22.1157 | 12.2404 | 8.9292 | 15.794 | 22.1408 | 11.9621 | 8.7262 | 15.6032 | 22.1723 | 11.6675 | 8.5113 | 15.5082 | 22.2089 | 11.4526 | 8.3545 | 15.4686 | 22.2524 | 11.422 | 8.3322 | 15.3438 | 22.3031 | 11.3898 | 8.3087 | 15.2005 | 22.3599 | 11.3546 | 8.283 | 15.0697 | 22.4222 | 11.3222 | 8.2594 | 14.917 | 22.4848 | 11.2906 | 8.2363 | 14.7767 | 22.8288 | 11.1924 | 8.1647 | 14.1767 | 23.2349 | 11.1742 | 8.1514 | 13.578 | 23.6033 | 12.2127 | 8.909 | 13.1019 | 23.9425 | 13.0663 | 9.5317 | 12.6539 | 22.1146 | 12.5756 | 9.1737 | 15.8028 | 22.1387 | 12.2199 | 8.9143 | 15.4136 | 22.1551 | 11.9347 | 8.7062 | 15.176 | 22.1835 | 11.4728 | 8.3693 | 15.0819 | 22.2212 | 11.398 | 8.3147 | 15.0339 | 22.2693 | 11.355 | 8.2833 | 14.9005 | 22.3261 | 11.3158 | 8.2547 | 14.7585 | 22.3845 | 11.2727 | 8.2233 | 14.6181 | 23.5568 | 11.228 | 8.1907 | 13.3418 | 23.6059 | 11.1881 | 8.1615 | 13.1895 | 26.9193 | 11.0996 | 8.097 | 9.5013 | 29.4668 | 11.3695 | 8.2939 | 6.7897 | 29.4034 | 13.3408 | 9.732 | 6.8604 | 29.5273 | 13.3237 | 9.7195 | 6.7003 | 22.1144 | 12.3962 | 9.0429 | 15.7948 | 22.1393 | 12.0374 | 8.7811 | 15.417 | 22.1605 | 11.6923 | 8.5294 | 15.1654 | 22.198 | 11.3518 | 8.281 | 15.0595 | 22.25 | 11.0022 | 8.0259 | 15.0109 | 22.3317 | 10.9034 | 7.9539 | 14.8567 | 22.4259 | 10.8686 | 7.9285 | 14.6618 | 22.5386 | 10.8843 | 7.94 | 14.4702 | 23.7717 | 10.7163 | 7.8174 | 13.1662 | 23.9032 | 10.7094 | 7.8123 | 12.9718 | 31.9851 | 9.3488 | 6.8198 | 4.2301 | 36.8928 | 8.4783 | 6.1848 | -2.3911 | 37.0088 | 9.8454 | 7.1821 | -4.0884 | 37.0652 | 9.75 | 7.1125 | -5.3746 | 22.1152 | 12.3982 | 9.0443 | 15.8066 | 22.1468 | 12.0351 | 8.7794 | 15.4174 | 22.1781 | 11.6749 | 8.5167 | 15.1604 | 22.2254 | 11.272 | 8.2228 | 15.0543 | 25.3317 | 10.5102 | 7.667 | 11.9515 | 25.2436 | 10.5768 | 7.7156 | 11.9772 | 25.1898 | 10.6024 | 7.7343 | 11.9576 | 25.1889 | 10.632 | 7.7559 | 11.9051 | 26.3364 | 10.4771 | 7.6429 | 10.6794 | 26.3745 | 10.4579 | 7.6289 | 10.3014 | 34.9152 | 11.0445 | 8.0568 | -0.080257 | 34.5814 | 10.3929 | 7.5815 | -1.5582 | 34.5758 | 10.2415 | 7.4711 | -2.6673 | 34.4319 | 10.2026 | 7.4427 | -2.586
OFFERTON | VERNON PARK | BREDBURY | 391010 | 389489 | 29.5089 | 13.0215 | 9.499 | 18.8126 | 29.5349 | 12.6437 | 9.2234 | 18.7322 | 29.5495 | 12.6531 | 9.2302 | 18.5179 | 29.5857 | 12.5328 | 9.1425 | 18.3498 | 29.636 | 12.165 | 8.8742 | 18.1647 | 29.6982 | 12.3199 | 8.9872 | 17.9317 | 29.77 | 12.2432 | 8.9312 | 17.551 | 29.8485 | 12.1882 | 8.8912 | 17.3124 | 29.9335 | 12.1506 | 8.8637 | 17.0763 | 30.0275 | 12.0539 | 8.7932 | 16.7039 | 30.4291 | 11.536 | 8.4153 | 15.486 | 30.7767 | 11.2229 | 8.187 | 14.9701 | 31.009 | 11.1105 | 8.105 | 14.9216 | 31.1786 | 10.8931 | 7.9464 | 15.1553 | 29.4935 | 13.0332 | 9.5076 | 18.8645 | 29.5092 | 12.7919 | 9.3315 | 18.8247 | 29.5408 | 12.6051 | 9.1952 | 18.5786 | 29.5854 | 12.6136 | 9.2015 | 18.4295 | 29.6372 | 12.5843 | 9.1801 | 18.2822 | 29.6961 | 12.5303 | 9.1407 | 18.0886 | 29.7626 | 12.4705 | 9.097 | 17.75 | 29.8346 | 12.4339 | 9.0703 | 17.551 | 29.9126 | 12.3899 | 9.0383 | 17.3493 | 29.9821 | 12.3216 | 8.9884 | 17.0494 | 30.1794 | 12.0835 | 8.8148 | 16.2424 | 30.3396 | 11.7282 | 8.5556 | 15.7498 | 30.4736 | 11.9358 | 8.707 | 15.3865 | 30.578 | 11.9575 | 8.7229 | 15.3045 | 29.5089 | 13.0256 | 9.502 | 18.8171 | 29.535 | 12.878 | 9.3943 | 18.7461 | 29.5497 | 12.6552 | 9.2318 | 18.5427 | 29.5861 | 12.6167 | 9.2037 | 18.3811 | 29.6363 | 12.5949 | 9.1878 | 18.2037 | 29.6983 | 12.5289 | 9.1397 | 17.9787 | 29.7699 | 12.449 | 9.0814 | 17.6071 | 29.8484 | 12.3883 | 9.0371 | 17.3753 | 29.9324 | 12.3097 | 8.9798 | 17.1155 | 30.0216 | 12.1869 | 8.8901 | 16.8102 | 30.3877 | 11.8473 | 8.6425 | 15.7333 | 30.6695 | 11.7461 | 8.5686 | 15.3189 | 30.8729 | 11.6698 | 8.513 | 15.3025 | 31.0027 | 11.5812 | 8.4484 | 15.4685 | 29.5064 | 13.0196 | 9.4976 | 18.8216 | 29.5317 | 12.6163 | 9.2034 | 18.7499 | 29.5511 | 12.6459 | 9.225 | 18.5498 | 29.5989 | 12.4995 | 9.1182 | 18.3977 | 29.6684 | 12.1891 | 8.8918 | 18.2395 | 29.7597 | 12.3096 | 8.9796 | 18.0332 | 29.8725 | 12.2002 | 8.8999 | 17.6786 | 30.0029 | 12.1675 | 8.876 | 17.4675 | 30.1491 | 12.1061 | 8.8312 | 17.2971 | 30.3133 | 11.9936 | 8.7492 | 17.0291 | 30.9139 | 11.2761 | 8.2258 | 15.4247 | 31.4744 | 10.2532 | 7.4796 | 11.8808 | 31.8013 | 9.4191 | 6.8711 | 8.9412 | 31.9666 | 8.8934 | 6.4876 | 7.2125 | 29.5024 | 13.0221 | 9.4995 | 18.8247 | 29.5307 | 12.5857 | 9.1811 | 18.7318 | 29.5529 | 12.7104 | 9.2721 | 18.5254 | 29.5985 | 12.4898 | 9.1111 | 18.3921 | 29.6649 | 12.4637 | 9.0921 | 18.2578 | 29.7508 | 12.4982 | 9.1173 | 18.0891 | 29.8618 | 12.439 | 9.0741 | 17.7693 | 29.9867 | 12.3752 | 9.0275 | 17.601 | 30.1313 | 12.2583 | 8.9423 | 17.3503 | 30.3186 | 12.0199 | 8.7684 | 16.4369 | 30.9733 | 10.9161 | 7.9631 | 12.3882 | 31.4106 | 9.9764 | 7.2776 | 9.2185 | 31.5653 | 9.4108 | 6.865 | 7.2716 | 31.505 | 9.2515 | 6.7489 | 8.0569
OPENSHAW | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 26.091 | 12.6559 | 9.2323 | 5.5172 | 26.1937 | 12.4253 | 9.0641 | 4.9241 | 26.2256 | 12.2196 | 8.914 | 4.7792 | 26.2954 | 11.9485 | 8.7163 | 4.5218 | 26.3972 | 11.7945 | 8.6039 | 4.3584 | 26.5298 | 11.5449 | 8.4219 | 3.9073 | 26.6827 | 11.4226 | 8.3326 | 3.5138 | 26.8494 | 11.2902 | 8.2361 | 3.1632 | 27.0286 | 11.0723 | 8.0771 | 2.6464 | 27.2268 | 10.932 | 7.9747 | 2.0973 | 28.1895 | 10.2258 | 7.4595 | -0.18006 | 29.1218 | 9.7956 | 7.1457 | -1.6362 | 29.8188 | 9.9579 | 7.2641 | -2.2545 | 30.5102 | 9.7386 | 7.1042 | -2.4443 | 26.0102 | 12.7071 | 9.2696 | 5.799 | 26.0531 | 12.476 | 9.1011 | 5.4407 | 26.1374 | 12.1333 | 8.8511 | 5.1985 | 26.2409 | 11.9513 | 8.7183 | 4.8954 | 26.3613 | 11.4832 | 8.3768 | 4.7092 | 26.4977 | 11.4667 | 8.3648 | 4.2597 | 26.6517 | 11.3758 | 8.2985 | 3.8571 | 26.8178 | 11.2932 | 8.2382 | 3.4839 | 26.9964 | 11.1797 | 8.1555 | 2.9553 | 27.1864 | 11.0773 | 8.0807 | 2.4581 | 27.7427 | 10.7375 | 7.8328 | 0.85225 | 28.3017 | 10.4038 | 7.5895 | -0.38176 | 28.8022 | 10.5945 | 7.7285 | -1.2066 | 29.2058 | 10.6953 | 7.8021 | -1.7563 | 26.0917 | 12.7062 | 9.269 | 5.5343 | 26.1951 | 12.463 | 9.0916 | 4.9607 | 26.2278 | 12.1385 | 8.8549 | 4.8325 | 26.2985 | 11.7992 | 8.6074 | 4.591 | 26.4009 | 11.644 | 8.4941 | 4.4456 | 26.5336 | 11.4232 | 8.3331 | 4.0163 | 26.6864 | 11.3236 | 8.2604 | 3.6434 | 26.8527 | 11.2158 | 8.1817 | 3.3024 | 27.0298 | 11.0784 | 8.0815 | 2.8138 | 27.2189 | 10.9152 | 7.9625 | 2.3163 | 28.0877 | 10.3898 | 7.5792 | 0.29012 | 28.7365 | 10.0469 | 7.3291 | -0.87691 | 29.2833 | 10.4346 | 7.6119 | -1.3645 | 29.7176 | 10.2049 | 7.4444 | -1.419 | 26.0847 | 12.6568 | 9.2329 | 5.52 | 26.1855 | 12.4275 | 9.0657 | 4.9256 | 26.2273 | 12.2049 | 8.9033 | 4.7725 | 26.3192 | 11.9068 | 8.6859 | 4.4957 | 26.4573 | 11.7417 | 8.5654 | 4.3228 | 26.6539 | 11.4836 | 8.3771 | 3.8461 | 26.9036 | 11.3085 | 8.2494 | 3.3939 | 27.1955 | 11.0757 | 8.0796 | 2.9742 | 27.525 | 10.9598 | 7.995 | 2.4523 | 27.8244 | 10.7656 | 7.8534 | 1.956 | 29.3497 | 9.8189 | 7.1627 | -1.0304 | 31.0803 | 8.3228 | 6.0714 | -7.3519 | 32.0827 | 7.568 | 5.5208 | -12.4878 | 32.5398 | 6.6513 | 4.852 | -15.9287 | 26.0769 | 12.663 | 9.2375 | 5.5452 | 26.1812 | 12.576 | 9.174 | 4.9594 | 26.228 | 12.4944 | 9.1145 | 4.8208 | 26.3179 | 12.311 | 8.9807 | 4.5727 | 26.4548 | 12.2613 | 8.9445 | 4.4242 | 26.6568 | 12.1088 | 8.8332 | 3.9841 | 26.9285 | 11.919 | 8.6948 | 3.5687 | 27.245 | 11.7566 | 8.5763 | 3.1882 | 27.6097 | 11.5839 | 8.4503 | 2.5758 | 28.0443 | 11.2075 | 8.1757 | 1.0978 | 29.8005 | 9.5399 | 6.9593 | -5.8679 | 31.1698 | 7.9976 | 5.8342 | -11.835 | 31.7424 | 7.2073 | 5.2577 | -15.2898 | 31.7454 | 7.0875 | 5.1703 | -14.6846
ORMSKIRK | SKELMERSDALE | WASHWAY FARM / KIRKBY | 341294 | 408158 | 29.5309 | 14.5148 | 10.432 | 13.2916 | 29.5844 | 14.0709 | 10.113 | 12.8569 | 29.6091 | 13.7367 | 9.8728 | 12.6703 | 29.6635 | 13.6591 | 9.8171 | 12.4716 | 29.7376 | 13.8631 | 9.9637 | 12.2104 | 29.8297 | 13.7708 | 9.8973 | 11.8993 | 29.9349 | 13.6914 | 9.8403 | 11.5578 | 30.0466 | 13.5868 | 9.7651 | 11.2304 | 30.1659 | 13.4664 | 9.6786 | 10.8734 | 30.2995 | 13.3291 | 9.5799 | 10.4239 | 30.7968 | 12.6678 | 9.1046 | 8.742 | 31.2122 | 12.1441 | 8.7282 | 7.851 | 31.4946 | 12.4246 | 8.9298 | 7.5451 | 31.7063 | 12.7143 | 9.138 | 7.7787 | 29.5082 | 14.6927 | 10.5599 | 13.5476 | 29.5508 | 14.6115 | 10.5016 | 13.3271 | 29.6198 | 14.5168 | 10.4335 | 13.0794 | 29.7092 | 14.4386 | 10.3773 | 12.8355 | 29.8126 | 14.298 | 10.2763 | 12.5481 | 29.9301 | 14.2038 | 10.2086 | 12.2189 | 30.0632 | 14.1158 | 10.1453 | 11.8467 | 30.2075 | 14.0291 | 10.083 | 11.472 | 30.3645 | 13.9285 | 10.0107 | 11.071 | 30.535 | 13.7528 | 9.8844 | 10.3118 | 30.7538 | 13.5782 | 9.7589 | 9.6605 | 30.9498 | 13.4088 | 9.6372 | 8.705 | 31.1147 | 13.7052 | 9.8502 | 8.021 | 31.2293 | 13.6311 | 9.797 | 7.6096 | 29.5309 | 14.6895 | 10.5576 | 13.3035 | 29.5846 | 14.5955 | 10.4901 | 12.8893 | 29.6094 | 14.5025 | 10.4232 | 12.7236 | 29.664 | 14.3614 | 10.3218 | 12.5423 | 29.7379 | 14.2706 | 10.2566 | 12.3007 | 29.8297 | 14.0334 | 10.0861 | 12.009 | 29.9346 | 14.0012 | 10.0629 | 11.687 | 30.0462 | 13.8664 | 9.9661 | 11.3784 | 30.1642 | 13.6711 | 9.8257 | 11.0447 | 30.2914 | 13.4591 | 9.6733 | 10.6495 | 30.7452 | 12.7496 | 9.1634 | 9.1675 | 31.0833 | 12.4252 | 8.9302 | 8.44 | 31.3258 | 12.9824 | 9.3307 | 8.2149 | 31.4814 | 13.0978 | 9.4137 | 8.4716 | 29.5276 | 14.5136 | 10.4312 | 13.3045 | 29.5811 | 14.0626 | 10.1071 | 12.8777 | 29.6133 | 13.808 | 9.9241 | 12.7003 | 29.6844 | 13.8229 | 9.9348 | 12.5044 | 29.7851 | 13.8355 | 9.9439 | 12.2445 | 29.9172 | 13.7622 | 9.8912 | 11.9196 | 30.0793 | 13.6197 | 9.7887 | 11.5272 | 30.2602 | 13.4416 | 9.6608 | 11.1501 | 30.4598 | 13.2233 | 9.5038 | 10.7918 | 30.6819 | 13.0406 | 9.3725 | 10.4393 | 31.4344 | 12.0008 | 8.6252 | 8.5822 | 32.0735 | 10.8605 | 7.8057 | 5.1062 | 32.3627 | 10.8822 | 7.8213 | 2.5458 | 32.4705 | 10.7178 | 7.7031 | 0.88249 | 29.5238 | 14.5144 | 10.4318 | 13.295 | 29.5773 | 14.075 | 10.116 | 12.8612 | 29.6022 | 13.8846 | 9.9791 | 12.7092 | 29.6598 | 13.9814 | 10.0487 | 12.5465 | 29.7478 | 14.0236 | 10.079 | 12.2889 | 29.8632 | 13.8732 | 9.971 | 11.9919 | 30.0111 | 13.6377 | 9.8017 | 11.6562 | 30.1719 | 13.606 | 9.7789 | 11.3459 | 30.3523 | 13.4293 | 9.6519 | 10.9707 | 30.5712 | 13.1565 | 9.4558 | 10.0557 | 31.3192 | 12.1623 | 8.7413 | 5.9511 | 31.7867 | 11.2124 | 8.0586 | 2.852 | 31.9143 | 11.1098 | 7.9848 | 1.229 | 31.8119 | 10.9983 | 7.9047 | 1.9244
PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 14.3264 | 2.3587 | 1.6953 | 14.3264 | 11.7932 | 1.9417 | 1.3955 | 11.7932 | 10.4577 | 1.7218 | 1.2375 | 10.4577 | 8.6326 | 1.4213 | 1.0215 | 8.6326 | 6.5778 | 1.083 | 0.77836 | 6.5778 | 5.3189 | 0.87571 | 0.62939 | 5.3189 | 5.096 | 0.83901 | 0.60301 | 5.096 | 4.3134 | 0.71016 | 0.51041 | 4.3134 | 3.0319 | 0.49917 | 0.35877 | 3.0319 | 1.5929 | 0.26226 | 0.18849 | 1.5929 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 15.8399 | 2.6079 | 1.8744 | 15.8399 | 15.01 | 2.4713 | 1.7762 | 15.01 | 14.2981 | 2.3541 | 1.6919 | 14.2981 | 14.0011 | 2.3052 | 1.6568 | 14.0011 | 13.5566 | 2.232 | 1.6042 | 13.5566 | 12.9946 | 2.1395 | 1.5377 | 12.9946 | 12.3938 | 2.0405 | 1.4666 | 12.3938 | 11.6602 | 1.9198 | 1.3798 | 11.6602 | 10.8922 | 1.7933 | 1.2889 | 10.8922 | 10.1263 | 1.6672 | 1.1983 | 10.1263 | 7.0611 | 1.1626 | 0.83555 | 7.0611 | 5.0148 | 0.82565 | 0.59341 | 5.0148 | 7.6889 | 1.2659 | 0.90984 | 7.6889 | 9.7336 | 1.6026 | 1.1518 | 9.7336 | 15.9235 | 2.6217 | 1.8843 | 15.9235 | 15.3158 | 2.5216 | 1.8123 | 15.3158 | 14.6799 | 2.4169 | 1.7371 | 14.6799 | 14.228 | 2.3425 | 1.6836 | 14.228 | 13.516 | 2.2253 | 1.5994 | 13.516 | 12.5327 | 2.0634 | 1.483 | 12.5327 | 11.49 | 1.8917 | 1.3596 | 11.49 | 10.3212 | 1.6993 | 1.2213 | 10.3212 | 8.9765 | 1.4779 | 1.0622 | 8.9765 | 7.4328 | 1.2237 | 0.87953 | 7.4328 | 5.5899 | 0.92034 | 0.66147 | 5.5899 | 3.808 | 0.62695 | 0.4506 | 3.808 | 6.9104 | 1.1377 | 0.81772 | 6.9104 | 5.7599 | 0.94832 | 0.68158 | 5.7599 | 14.3474 | 2.3622 | 1.6978 | 14.3474 | 11.8421 | 1.9497 | 1.4013 | 11.8421 | 10.2309 | 1.6844 | 1.2106 | 10.2309 | 8.3437 | 1.3737 | 0.98733 | 8.3437 | 5.7735 | 0.95056 | 0.68318 | 5.7735 | 5.8917 | 0.97002 | 0.69717 | 5.8917 | 5.291 | 0.87112 | 0.62609 | 5.291 | 4.1837 | 0.68881 | 0.49506 | 4.1837 | 2.61 | 0.42972 | 0.30884 | 2.61 | 0.7916 | 0.13033 | 0.093672 | 0.7916 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 14.3895 | 2.3691 | 1.7027 | 14.3895 | 12.0886 | 1.9903 | 1.4305 | 12.0886 | 10.5059 | 1.7297 | 1.2432 | 10.5059 | 8.4225 | 1.3867 | 0.99665 | 8.4225 | 5.9237 | 0.9753 | 0.70097 | 5.9237 | 6.466 | 1.0646 | 0.76514 | 6.466 | 5.5468 | 0.91324 | 0.65636 | 5.5468 | 4.3343 | 0.71361 | 0.51289 | 4.3343 | 2.8182 | 0.464 | 0.33348 | 2.8182 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
PEEL ST & RIBBLESDALE T13 | PADIHAM | PADIHAM | 374463 | 441514 | 22.1771 | 22.1771 | 22.1771 | 11.6574 | 22.2708 | 22.2708 | 22.2708 | 11.3081 | 22.3124 | 22.3124 | 22.2239 | 11.0346 | 22.3783 | 22.3783 | 22.1548 | 10.807 | 22.4643 | 22.4643 | 22.0786 | 10.5507 | 22.5708 | 22.5708 | 21.9951 | 10.2634 | 22.6914 | 22.6914 | 21.9104 | 9.9439 | 22.8212 | 22.8212 | 21.8145 | 9.5804 | 24.1896 | 24.1896 | 21.5755 | 7.9563 | 24.3289 | 24.3289 | 21.4728 | 7.5253 | 25.766 | 25.766 | 20.9144 | 5.2019 | 29.8258 | 27.9901 | 20.117 | 0.85951 | 30.2893 | 27.4345 | 19.7177 | 0.4658 | 30.628 | 27.0233 | 19.4222 | 0.31306 | 22.1189 | 22.1189 | 22.1189 | 11.7628 | 22.1633 | 22.1633 | 22.1633 | 11.5146 | 22.2361 | 22.2361 | 22.2361 | 11.2434 | 22.32 | 22.32 | 22.2376 | 11.0219 | 22.4128 | 22.4128 | 22.1888 | 10.7789 | 22.5148 | 22.5148 | 22.1299 | 10.5029 | 22.6282 | 22.6282 | 22.0692 | 10.1827 | 22.7485 | 22.7485 | 21.9896 | 9.7968 | 22.8765 | 22.8765 | 21.9263 | 9.3907 | 23.0108 | 23.0108 | 21.8675 | 8.9706 | 23.4073 | 23.4073 | 21.6676 | 7.8509 | 23.789 | 23.789 | 21.4644 | 7.0395 | 24.1181 | 24.1181 | 21.2807 | 6.489 | 24.3757 | 24.3757 | 21.0914 | 6.036 | 22.1777 | 22.1777 | 22.1777 | 11.6636 | 22.2719 | 22.2719 | 22.2719 | 11.3236 | 22.3139 | 22.3139 | 22.2608 | 11.06 | 22.3803 | 22.3803 | 22.1981 | 10.8423 | 22.4666 | 22.4666 | 22.1318 | 10.5972 | 22.5727 | 22.5727 | 22.0488 | 10.3217 | 22.6928 | 22.6928 | 21.9815 | 10.0141 | 22.8219 | 22.8219 | 21.8846 | 9.6686 | 24.188 | 24.188 | 21.7925 | 8.0713 | 24.3196 | 24.3196 | 21.6961 | 7.6832 | 25.6853 | 25.6853 | 21.3309 | 5.5339 | 29.582 | 29.2011 | 20.9874 | 1.2986 | 29.9543 | 28.7271 | 20.6467 | 0.94348 | 30.2142 | 28.2021 | 20.2694 | 0.87266 | 22.1731 | 22.1731 | 22.1731 | 11.6589 | 22.2669 | 22.2669 | 22.2669 | 11.3075 | 22.318 | 22.318 | 22.2065 | 11.0347 | 22.4026 | 22.4026 | 22.1272 | 10.8044 | 22.518 | 22.518 | 22.0405 | 10.556 | 22.6721 | 22.6721 | 21.9432 | 10.2749 | 22.8623 | 22.8623 | 21.8406 | 9.9535 | 23.0941 | 23.0941 | 21.7317 | 9.612 | 24.5393 | 24.5393 | 21.4817 | 8.1069 | 24.8845 | 24.8845 | 21.3564 | 7.7072 | 29.2 | 28.2258 | 20.2865 | 2.55 | 30.8596 | 27.0064 | 19.41 | -1.1196 | 31.4372 | 25.9542 | 18.6538 | -3.388 | 31.6721 | 25.0037 | 17.9706 | -4.9203 | 22.1746 | 22.1746 | 22.1746 | 11.658 | 22.2809 | 22.2809 | 22.2809 | 11.2879 | 22.339 | 22.339 | 22.2011 | 11.0234 | 22.4242 | 22.4242 | 22.1137 | 10.8193 | 22.5398 | 22.5398 | 22.0196 | 10.5952 | 22.7104 | 22.7104 | 21.9168 | 10.3361 | 22.9117 | 22.9117 | 21.8149 | 10.0528 | 23.2716 | 23.2716 | 21.6968 | 9.6376 | 24.1823 | 24.1823 | 21.4933 | 8.6368 | 24.4481 | 24.4481 | 21.3286 | 7.9172 | 30.1418 | 27.6997 | 19.9083 | -0.11292 | 30.8693 | 26.5541 | 19.085 | -2.9709 | 31.2059 | 25.9025 | 18.6166 | -4.4479 | 31.1936 | 25.4993 | 18.3268 | -4.1934
PENDLETON | FREDERICK RD | KEARSLEY | 381161 | 398842 | 31.6508 | 9.2873 | 6.7749 | 13.2393 | 31.7435 | 9.1194 | 6.6525 | 12.3765 | 31.7633 | 9.0259 | 6.5843 | 12.0756 | 31.8166 | 8.9738 | 6.5463 | 11.9099 | 31.8857 | 8.9046 | 6.4958 | 11.7637 | 31.9717 | 8.8055 | 6.4235 | 11.409 | 32.0617 | 8.7293 | 6.3679 | 11.0905 | 32.1546 | 8.671 | 6.3254 | 10.8289 | 32.2511 | 8.5858 | 6.2632 | 10.5129 | 32.3556 | 8.4915 | 6.1944 | 10.1883 | 32.874 | 8.0014 | 5.8369 | 8.6229 | 33.4704 | 7.5801 | 5.5295 | 7.2453 | 33.9771 | 7.2585 | 5.295 | 6.2288 | 34.4344 | 6.9664 | 5.0819 | 5.6754 | 31.5919 | 9.3446 | 6.8167 | 13.6488 | 31.6376 | 9.2115 | 6.7196 | 13.1884 | 31.7093 | 9.1291 | 6.6596 | 12.9398 | 31.8059 | 9.0391 | 6.5939 | 12.698 | 31.9103 | 8.952 | 6.5304 | 12.5025 | 32.0235 | 8.8452 | 6.4525 | 12.1149 | 32.1461 | 8.7697 | 6.3974 | 11.78 | 32.2759 | 8.6919 | 6.3406 | 11.4429 | 32.414 | 8.6085 | 6.2798 | 11.1143 | 32.5598 | 8.5169 | 6.213 | 10.6936 | 32.9513 | 8.2634 | 6.028 | 9.625 | 33.3578 | 8.0403 | 5.8653 | 8.5321 | 33.7519 | 7.9392 | 5.7915 | 7.5422 | 34.0874 | 7.7803 | 5.6756 | 6.6943 | 31.651 | 9.3454 | 6.8173 | 13.2476 | 31.744 | 9.2328 | 6.7352 | 12.402 | 31.7642 | 9.136 | 6.6646 | 12.1141 | 31.8182 | 9.012 | 6.5741 | 11.9603 | 31.8879 | 8.9304 | 6.5146 | 11.8278 | 31.9744 | 8.7951 | 6.4159 | 11.4889 | 32.0649 | 8.688 | 6.3378 | 11.1859 | 32.1583 | 8.5674 | 6.2498 | 10.9392 | 32.2547 | 8.4905 | 6.1937 | 10.6439 | 32.3569 | 8.3784 | 6.1119 | 10.3578 | 32.8146 | 8.0755 | 5.8909 | 8.9644 | 33.2297 | 7.7627 | 5.6628 | 7.8173 | 33.6577 | 7.5881 | 5.5354 | 6.9421 | 33.9606 | 7.3489 | 5.3609 | 6.5355 | 31.6438 | 9.2907 | 6.7774 | 13.2521 | 31.7311 | 9.1361 | 6.6647 | 12.4053 | 31.7471 | 9.0477 | 6.6002 | 12.1144 | 31.803 | 8.9786 | 6.5498 | 11.9472 | 31.8785 | 8.9016 | 6.4936 | 11.7979 | 31.984 | 8.7723 | 6.3993 | 11.418 | 32.109 | 8.7013 | 6.3475 | 11.0258 | 32.2485 | 8.6098 | 6.2807 | 10.6796 | 32.4007 | 8.5056 | 6.2047 | 10.2982 | 32.6019 | 8.3736 | 6.1084 | 9.9198 | 33.3996 | 7.6991 | 5.6164 | 7.6884 | 34.286 | 6.6546 | 4.8544 | 3.7644 | 34.8206 | 5.9141 | 4.3142 | 0.71062 | 32.5092 | 5.2733 | 3.8468 | -1.3215 | 31.6327 | 9.2959 | 6.7813 | 13.2724 | 31.7126 | 9.1988 | 6.7104 | 12.4231 | 31.7253 | 9.1364 | 6.6649 | 12.1375 | 31.7734 | 9.0909 | 6.6317 | 11.978 | 31.8438 | 8.9894 | 6.5576 | 11.8095 | 32.0039 | 8.898 | 6.4909 | 11.3688 | 32.1334 | 8.7653 | 6.3941 | 10.997 | 32.2703 | 8.6407 | 6.3032 | 10.6712 | 32.4246 | 8.5333 | 6.2249 | 10.2648 | 32.6144 | 8.3386 | 6.0829 | 9.4852 | 33.5401 | 7.1892 | 5.2444 | 5.1806 | 34.3252 | 6.1423 | 4.4807 | 1.4619 | 34.2033 | 5.5481 | 4.0473 | -0.63291 | 33.0636 | 5.3632 | 3.9124 | -0.41466
PETTERIL BANK | CARLISLE | HARKER / HUTTON | 341768 | 553686 | 31.3185 | 11.285 | 8.1107 | 12.6454 | 31.3816 | 11.6811 | 8.3954 | 12.4296 | 31.4055 | 11.5582 | 8.3071 | 12.161 | 31.4658 | 11.3519 | 8.1588 | 11.8071 | 31.5541 | 11.0741 | 7.9592 | 11.5248 | 31.668 | 10.4472 | 7.5086 | 11.0414 | 31.8006 | 10.3036 | 7.4054 | 10.5008 | 31.9472 | 10.0831 | 7.2469 | 10.045 | 32.1042 | 9.7907 | 7.0367 | 9.4576 | 32.28 | 9.4679 | 6.8048 | 8.813 | 33.0209 | 8.6109 | 6.1888 | 6.4339 | 33.6091 | 8.0951 | 5.8181 | 5.3109 | 33.9621 | 8.3566 | 6.0061 | 5.0771 | 34.2058 | 8.2129 | 5.9028 | 5.3326 | 31.2671 | 11.3397 | 8.1501 | 12.7027 | 31.294 | 11.1949 | 8.046 | 12.5442 | 31.3549 | 11.0069 | 7.9108 | 12.236 | 31.4338 | 10.7845 | 7.751 | 11.9265 | 31.527 | 10.5823 | 7.6057 | 11.7023 | 31.6331 | 10.249 | 7.3662 | 11.2766 | 31.7531 | 9.9856 | 7.1769 | 10.7972 | 31.8834 | 9.7785 | 7.028 | 10.4028 | 32.0229 | 9.5867 | 6.8902 | 9.9716 | 32.1695 | 9.3874 | 6.7469 | 9.463 | 32.5032 | 8.9096 | 6.4035 | 7.926 | 32.7664 | 8.7036 | 6.2554 | 6.8395 | 32.9354 | 8.8116 | 6.3331 | 6.2232 | 33.0353 | 8.896 | 6.3937 | 5.8728 | 31.319 | 11.3347 | 8.1464 | 12.658 | 31.3824 | 11.174 | 8.031 | 12.4628 | 31.4063 | 10.9347 | 7.859 | 12.2039 | 31.4668 | 10.6239 | 7.6356 | 11.8688 | 31.5549 | 10.3876 | 7.4658 | 11.6173 | 31.668 | 9.91 | 7.1225 | 11.1555 | 31.7998 | 9.6946 | 6.9677 | 10.6368 | 31.9455 | 9.4219 | 6.7717 | 10.2007 | 32.0998 | 9.1974 | 6.6103 | 9.6575 | 32.2662 | 8.9509 | 6.4332 | 9.0748 | 32.9499 | 8.3878 | 6.0285 | 6.9681 | 33.4449 | 8.1683 | 5.8707 | 5.9939 | 33.74 | 8.5099 | 6.1162 | 5.8255 | 33.9242 | 8.2484 | 5.9283 | 6.1148 | 31.3142 | 11.2527 | 8.0875 | 12.6445 | 31.3772 | 11.5881 | 8.3286 | 12.4148 | 31.4097 | 11.6674 | 8.3856 | 12.1187 | 31.4923 | 11.3961 | 8.1906 | 11.7294 | 31.6169 | 11.0597 | 7.9489 | 11.4335 | 31.7854 | 10.5886 | 7.6102 | 10.9187 | 31.9964 | 10.2101 | 7.3382 | 10.3197 | 32.2421 | 9.8311 | 7.0658 | 9.7991 | 32.5151 | 9.4877 | 6.819 | 9.3409 | 32.8219 | 9.1402 | 6.5692 | 8.7987 | 33.9358 | 7.9464 | 5.7113 | 5.9887 | 34.79 | 6.5967 | 4.7412 | 0.76768 | 35.1767 | 5.9801 | 4.298 | -3.2286 | 31.7446 | 5.2265 | 3.7564 | -6.1735 | 31.3016 | 11.2581 | 8.0914 | 12.6908 | 31.3637 | 11.3457 | 8.1544 | 12.4668 | 31.3983 | 11.7622 | 8.4537 | 12.1834 | 31.4752 | 11.5639 | 8.3112 | 11.8318 | 31.5929 | 11.2413 | 8.0793 | 11.5825 | 31.7495 | 10.8686 | 7.8115 | 11.1437 | 31.9539 | 10.5135 | 7.5562 | 10.625 | 32.1855 | 10.2372 | 7.3576 | 10.2005 | 32.4444 | 9.9463 | 7.1486 | 9.7052 | 32.7727 | 9.4706 | 6.8067 | 8.3931 | 33.9186 | 8.0021 | 5.7513 | 2.228 | 34.5804 | 6.6933 | 4.8106 | -2.426 | 34.7541 | 5.8966 | 4.238 | -5.1208 | 34.6077 | 5.8225 | 4.1848 | -4.4482
PHILLIPS LANE | NELSON | PADIHAM | 387571 | 439522 | 19.163 | 19.163 | 19.1303 | 12.3689 | 19.1827 | 19.1827 | 18.0112 | 12.2642 | 19.2003 | 19.2003 | 16.8853 | 12.2255 | 19.2261 | 19.2261 | 15.7811 | 12.1468 | 19.2594 | 19.2594 | 14.6706 | 12.0537 | 19.3 | 18.5773 | 13.5519 | 11.9275 | 19.347 | 18.5555 | 13.536 | 11.7987 | 19.3987 | 18.4566 | 13.4638 | 11.66 | 19.4544 | 18.4635 | 13.4689 | 11.5073 | 19.5162 | 18.4855 | 13.4849 | 11.3306 | 19.758 | 18.7146 | 13.652 | 10.7443 | 19.9809 | 19.9809 | 15.4002 | 10.4277 | 20.1365 | 20.1365 | 18.4173 | 10.3685 | 20.2797 | 20.2797 | 18.956 | 10.4106 | 19.1666 | 19.1666 | 19.1219 | 12.4534 | 19.1932 | 19.1932 | 17.9667 | 12.4118 | 19.2298 | 19.2298 | 16.8183 | 12.3206 | 19.2715 | 19.2715 | 15.6617 | 12.2113 | 19.3192 | 19.3192 | 14.4982 | 12.1 | 19.374 | 18.2735 | 13.3302 | 11.9646 | 19.4363 | 18.2583 | 13.3192 | 11.8159 | 19.4994 | 18.2208 | 13.2918 | 11.6535 | 19.5631 | 18.2089 | 13.2832 | 11.4844 | 19.632 | 18.1719 | 13.2561 | 11.3084 | 19.7442 | 18.388 | 13.4138 | 10.9281 | 19.8453 | 19.8453 | 14.5305 | 10.6552 | 19.9363 | 19.9363 | 16.5556 | 10.5271 | 20.0106 | 20.0106 | 17.147 | 10.4573 | 19.1631 | 19.1631 | 19.1221 | 12.3733 | 19.1828 | 19.1828 | 17.958 | 12.2731 | 19.2005 | 19.2005 | 16.8123 | 12.2392 | 19.2264 | 19.2264 | 15.6749 | 12.1656 | 19.2598 | 19.2598 | 14.5109 | 12.0782 | 19.3003 | 18.3292 | 13.3709 | 11.9584 | 19.3473 | 18.3224 | 13.3659 | 11.8361 | 19.399 | 18.2838 | 13.3378 | 11.7103 | 19.4542 | 18.2387 | 13.3049 | 11.5751 | 19.5132 | 18.1823 | 13.2637 | 11.4175 | 19.7309 | 18.3332 | 13.3738 | 10.8909 | 19.9017 | 19.9017 | 15.185 | 10.6346 | 20.0309 | 20.0309 | 18.2941 | 10.5987 | 20.1319 | 20.1319 | 18.8315 | 10.662 | 19.1625 | 19.1625 | 19.1317 | 12.3763 | 19.1829 | 19.1829 | 18.0247 | 12.278 | 19.2043 | 19.2043 | 16.9069 | 12.2443 | 19.2369 | 19.2369 | 15.7977 | 12.1694 | 19.2812 | 19.2812 | 14.6817 | 12.0787 | 19.339 | 18.5841 | 13.5568 | 11.9514 | 19.4108 | 18.5009 | 13.4961 | 11.813 | 19.4937 | 18.4761 | 13.4781 | 11.651 | 19.5865 | 18.4959 | 13.4925 | 11.503 | 19.6907 | 18.4961 | 13.4926 | 11.3517 | 20.0966 | 18.5363 | 13.522 | 10.4355 | 20.4834 | 20.4834 | 15.0044 | 8.4859 | 20.7118 | 20.7118 | 17.7996 | 7.0408 | 20.8201 | 20.8201 | 18.2499 | 6.1384 | 19.1559 | 19.1559 | 19.1327 | 12.379 | 19.1727 | 19.1727 | 19.1307 | 12.2751 | 19.1904 | 19.1904 | 19.0237 | 12.2449 | 19.2164 | 19.2164 | 19.1478 | 12.1841 | 19.2537 | 19.2537 | 19.1792 | 12.1081 | 19.3039 | 19.3039 | 19.1725 | 12.0017 | 19.3708 | 19.3708 | 19.1336 | 11.8844 | 19.4472 | 19.4472 | 19.0924 | 11.7661 | 19.5361 | 19.5361 | 19.077 | 11.598 | 19.6489 | 19.6489 | 19.0283 | 11.1084 | 20.0876 | 20.0876 | 19.0008 | 8.8916 | 20.3942 | 20.3942 | 18.547 | 7.1598 | 20.5158 | 20.5158 | 18.3137 | 6.2778 | 20.5032 | 20.5032 | 18.2522 | 6.696
PICCADILLY | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 30.1523 | 9.0223 | 6.5817 | 17.4169 | 30.2296 | 8.8422 | 6.4502 | 16.4931 | 30.2239 | 8.7702 | 6.3978 | 16.3047 | 30.2359 | 8.7078 | 6.3522 | 16.2534 | 30.2572 | 8.6125 | 6.2827 | 16.163 | 30.2898 | 8.5022 | 6.2022 | 15.9966 | 30.3209 | 8.4155 | 6.139 | 15.8699 | 30.3496 | 8.4192 | 6.1417 | 15.7664 | 30.3762 | 8.3634 | 6.101 | 15.6521 | 30.401 | 8.297 | 6.0526 | 15.5283 | 30.4689 | 8.0671 | 5.8848 | 15.2595 | 30.4938 | 7.9722 | 5.8156 | 15.1544 | 30.4861 | 9.2417 | 6.7417 | 15.2108 | 30.4559 | 9.4568 | 6.8986 | 15.3173 | 30.0693 | 9.1756 | 6.6934 | 18.0084 | 30.0778 | 9.0938 | 6.6338 | 17.6241 | 30.1085 | 8.991 | 6.5588 | 17.4012 | 30.1498 | 8.9135 | 6.5023 | 17.2209 | 30.1956 | 8.8421 | 6.4502 | 17.0201 | 30.2441 | 8.7664 | 6.395 | 16.765 | 30.296 | 8.7639 | 6.3931 | 16.5285 | 30.3493 | 8.7324 | 6.3702 | 16.301 | 30.404 | 8.6909 | 6.3399 | 16.0343 | 30.4594 | 8.638 | 6.3013 | 15.7411 | 30.5411 | 8.5451 | 6.2335 | 15.4228 | 30.5899 | 8.5031 | 6.2029 | 15.2257 | 30.5998 | 9.2346 | 6.7365 | 15.202 | 30.5734 | 10.0327 | 7.3187 | 15.2805 | 30.1523 | 9.1759 | 6.6937 | 17.4256 | 30.2296 | 9.1115 | 6.6467 | 16.5126 | 30.2239 | 9.0331 | 6.5895 | 16.3339 | 30.2359 | 8.9384 | 6.5205 | 16.2935 | 30.2572 | 8.8977 | 6.4908 | 16.2146 | 30.2897 | 8.8467 | 6.4536 | 16.0611 | 30.3208 | 8.7817 | 6.4061 | 15.9471 | 30.3495 | 8.7093 | 6.3533 | 15.8567 | 30.3759 | 8.6129 | 6.283 | 15.7569 | 30.4003 | 8.5429 | 6.2319 | 15.6502 | 30.4663 | 8.4194 | 6.1418 | 15.3894 | 30.4896 | 8.4332 | 6.1519 | 15.2895 | 30.4811 | 9.5951 | 6.9995 | 15.3466 | 30.4507 | 9.717 | 7.0884 | 15.4529 | 30.1455 | 9.026 | 6.5844 | 17.4398 | 30.2167 | 8.844 | 6.4516 | 16.5404 | 30.2059 | 8.7475 | 6.3812 | 16.3752 | 30.213 | 8.6922 | 6.3408 | 16.3478 | 30.2302 | 8.6058 | 6.2778 | 16.28 | 30.2603 | 8.4134 | 6.1374 | 16.138 | 30.2898 | 8.4737 | 6.1814 | 16.0357 | 30.3177 | 8.4466 | 6.1617 | 15.9566 | 30.3434 | 8.4009 | 6.1283 | 15.8676 | 30.3673 | 8.344 | 6.0868 | 15.7742 | 30.4073 | 8.1327 | 5.9327 | 15.6071 | 30.4099 | 7.9503 | 5.7996 | 15.3303 | 30.3657 | 9.1413 | 6.6684 | 15.1895 | 30.2958 | 9.2755 | 6.7664 | 15.0531 | 30.1436 | 9.0269 | 6.585 | 17.4519 | 30.2131 | 8.8409 | 6.4493 | 16.5635 | 30.1986 | 8.7317 | 6.3697 | 16.4145 | 30.2011 | 8.5771 | 6.2569 | 16.4067 | 30.2134 | 8.6135 | 6.2834 | 16.3606 | 30.2382 | 8.547 | 6.2349 | 16.2434 | 30.2623 | 8.4836 | 6.1887 | 16.1663 | 30.2842 | 8.4273 | 6.1476 | 16.1153 | 30.3024 | 8.3907 | 6.1209 | 16.0582 | 30.3233 | 8.3334 | 6.0791 | 15.9228 | 30.3771 | 8.9503 | 6.5291 | 15.4744 | 30.3689 | 8.6357 | 6.2996 | 15.1067 | 30.3124 | 8.942 | 6.523 | 14.9204 | 30.216 | 8.9608 | 6.5368 | 15.2367
PIMBO | SKELMERSDALE | WASHWAY FARM / KIRKBY | 349148 | 404549 | 40.0974 | 6.6017 | 4.7448 | 24.4483 | 35.022 | 5.7661 | 4.1442 | 24.0533 | 28.4234 | 4.6797 | 3.3634 | 24.0785 | 22.3033 | 3.6721 | 2.6392 | 22.3033 | 15.441 | 2.5422 | 1.8272 | 15.441 | 8.876 | 1.4614 | 1.0503 | 8.876 | 8.2533 | 1.3588 | 0.97663 | 8.2533 | 7.5458 | 1.2424 | 0.89291 | 7.5458 | 6.8252 | 1.1237 | 0.80764 | 6.8252 | 6.1071 | 1.0055 | 0.72267 | 6.1071 | 2.8816 | 0.47443 | 0.34098 | 2.8816 | 2.886 | 0.47516 | 0.34151 | 2.886 | 21.4102 | 3.525 | 2.5335 | 19.4955 | 35.9487 | 5.9187 | 4.2539 | 18.8573 | 41.1636 | 6.7773 | 4.871 | 24.9852 | 34.9434 | 5.7532 | 4.1349 | 25.0045 | 28.8281 | 4.7463 | 3.4113 | 24.8439 | 22.4956 | 3.7037 | 2.6619 | 22.4956 | 16.2065 | 2.6683 | 1.9177 | 16.2065 | 9.8543 | 1.6224 | 1.1661 | 9.8543 | 9.199 | 1.5145 | 1.0885 | 9.199 | 8.6549 | 1.425 | 1.0241 | 8.6549 | 8.0668 | 1.3281 | 0.95456 | 8.0668 | 7.461 | 1.2284 | 0.88287 | 7.461 | 5.6098 | 0.9236 | 0.66381 | 5.6098 | 5.9737 | 0.98352 | 0.70688 | 5.9737 | 19.9213 | 3.2799 | 2.3573 | 19.9213 | 31.4587 | 5.1794 | 3.7226 | 20.2614 | 41.1319 | 6.7721 | 4.8672 | 24.4528 | 34.9156 | 5.7486 | 4.1316 | 24.0619 | 28.5838 | 4.7061 | 3.3824 | 24.0914 | 22.086 | 3.6363 | 2.6135 | 22.086 | 15.4912 | 2.5505 | 1.8331 | 15.4912 | 8.8985 | 1.4651 | 1.053 | 8.8985 | 8.099 | 1.3334 | 0.95837 | 8.099 | 7.2773 | 1.1981 | 0.86113 | 7.2773 | 6.4986 | 1.0699 | 0.76898 | 6.4986 | 5.6274 | 0.92652 | 0.66591 | 5.6274 | 2.4077 | 0.39641 | 0.28491 | 2.4077 | 3.445 | 0.56719 | 0.40765 | 3.445 | 22.9112 | 3.7721 | 2.7111 | 20.2528 | 37.6363 | 6.1965 | 4.4536 | 19.991 | 40.1288 | 6.6069 | 4.7485 | 24.4842 | 35.0358 | 5.7684 | 4.1458 | 24.1256 | 27.5372 | 4.5338 | 3.2585 | 24.1825 | 22.2692 | 3.6665 | 2.6352 | 22.2692 | 15.361 | 2.5291 | 1.8177 | 15.361 | 8.4886 | 1.3976 | 1.0045 | 8.4886 | 7.5385 | 1.2412 | 0.89205 | 7.5385 | 6.5328 | 1.0756 | 0.77303 | 6.5328 | 5.5383 | 0.91184 | 0.65536 | 5.5383 | 4.5457 | 0.74841 | 0.5379 | 4.5457 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.2595 | 1.3599 | 0.97736 | 8.2595 | 20.4127 | 3.3608 | 2.4155 | 9.3755 | 40.1413 | 6.609 | 4.75 | 24.489 | 40.9061 | 6.7349 | 4.8405 | 24.1179 | 38.8222 | 6.3918 | 4.5939 | 24.1688 | 39.7299 | 6.5412 | 4.7013 | 24.1088 | 38.5364 | 6.3447 | 4.5601 | 23.9527 | 37.3365 | 6.1472 | 4.4181 | 23.473 | 36.3861 | 5.9907 | 4.3056 | 23.1893 | 35.5597 | 5.8546 | 4.2078 | 22.8789 | 34.7162 | 5.7158 | 4.108 | 22.5379 | 33.2395 | 5.4726 | 3.9333 | 21.6497 | 33.8882 | 5.5794 | 4.01 | 16.5774 | 26.4635 | 4.357 | 3.1315 | 11.9985 | 23.9208 | 3.9384 | 2.8306 | 9.4814 | 23.3355 | 3.842 | 2.7613 | 10.1035
MORTON PARK & PIRELLI | CARLISLE | HARKER / HUTTON | 339059 | 553548 | 3.4354 | 0.56561 | 0.40652 | 3.4354 | 1.1574 | 0.19056 | 0.13696 | 1.1574 | 0.41238 | 0.067896 | 0.048798 | 0.41238 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.368 | 2.6844 | 0.44197 | 0.31765 | -2.2486 | 2.6844 | 0.44197 | 0.31765 | -4.5282 | 2.6844 | 0.44197 | 0.31765 | -7.7381 | 0.16479 | 0.062548 | 0.051108 | -10.4421 | -5.6105 | -2.1295 | -1.74 | -15.6715 | -8.9352 | -3.3915 | -2.7712 | -18.1024 | -9.3027 | -3.5309 | -2.8851 | -18.7859 | -10.3781 | -3.9391 | -3.2187 | -18.4474 | 4.0818 | 0.67204 | 0.48301 | 4.0818 | 2.4482 | 0.40308 | 0.2897 | 2.4482 | 1.4399 | 0.23707 | 0.17039 | 1.4399 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.4103 | 2.6844 | 0.44197 | 0.31765 | 1.1877 | 2.6844 | 0.44197 | 0.31765 | 0.50276 | 2.6844 | 0.44197 | 0.31765 | 0.21552 | 4.0478 | 0.66644 | 0.47898 | 4.0478 | 2.3443 | 0.38596 | 0.2774 | 2.3443 | 1.1045 | 0.18185 | 0.1307 | 1.1045 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.5004 | 2.6844 | 0.44197 | 0.31765 | -2.089 | 2.6844 | 0.44197 | 0.31765 | -4.413 | 2.6844 | 0.44197 | 0.31765 | -7.5176 | 2.6844 | 0.44197 | 0.31765 | -10.1534 | 2.6844 | 0.44197 | 0.31765 | -15.2842 | 2.6844 | 0.44197 | 0.31765 | -17.526 | 2.6844 | 0.44197 | 0.31765 | -17.9589 | 2.6844 | 0.44197 | 0.31765 | -17.6098 | 3.4485 | 0.56777 | 0.40807 | 3.4485 | 0.7956 | 0.13099 | 0.094145 | 0.7956 | 0.56608 | 0.093201 | 0.066985 | 0.56608 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.435 | 2.6844 | 0.44197 | 0.31765 | -2.194 | 2.6844 | 0.44197 | 0.31765 | -4.4892 | 1.8592 | 0.44197 | 0.31765 | -7.6165 | -2.6184 | -0.99385 | -0.81207 | -11.9862 | -12.5579 | -4.7665 | -3.8947 | -20.3531 | -21.053 | -7.9909 | -6.5294 | -26.8542 | -26.0475 | -9.8867 | -8.0784 | -31.0885 | -30.3725 | -11.5283 | -9.4197 | -33.7823 | 3.5535 | 0.58505 | 0.42049 | 3.5535 | 1.9047 | 0.31359 | 0.22538 | 1.9047 | 0.82695 | 0.13615 | 0.097854 | 0.82695 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.107 | 2.6844 | 0.44197 | 0.31765 | -6.4433 | 1.4139 | 0.44197 | 0.31765 | -11.6248 | -2.4206 | -0.91875 | -0.75071 | -15.541 | -5.6672 | -2.1511 | -1.7576 | -18.6606 | -13.8033 | -5.2392 | -4.2809 | -25.5558 | -20.9859 | -7.9655 | -6.5086 | -30.415 | -25.5199 | -9.6864 | -7.9147 | -33.2914 | -26.0872 | -9.9017 | -8.0907 | -32.1413
PORTWOOD | VERNON PARK | BREDBURY | 389826 | 390619 | 29.054 | 9.6126 | 7.0123 | 8.5125 | 29.1572 | 8.8666 | 6.4681 | 4.6667 | 29.1891 | 8.2474 | 6.0164 | 2.1691 | 29.2487 | 7.7243 | 5.6348 | -0.085726 | 29.326 | 7.2184 | 5.2657 | -1.847 | 29.4221 | 6.3278 | 4.6161 | -4.8112 | 29.5271 | 5.9819 | 4.3637 | -7.2146 | 29.6379 | 5.9504 | 4.3407 | -7.2459 | 29.7544 | 5.9307 | 4.3263 | -6.8774 | 29.8783 | 5.7744 | 4.2123 | -7.1944 | 30.2393 | 5.2907 | 3.8595 | -7.9897 | 30.5162 | 4.9794 | 3.6324 | -8.2933 | 30.6695 | 5.4897 | 4.0046 | -8.7975 | 30.7338 | 6.1053 | 4.4538 | -8.7393 | 29.0112 | 9.7117 | 7.0846 | 9.2219 | 29.0917 | 9.0709 | 6.6171 | 5.9602 | 29.2078 | 8.5659 | 6.2487 | 3.4101 | 29.3485 | 8.0776 | 5.8925 | 0.99925 | 29.5069 | 7.7013 | 5.618 | -0.87651 | 29.6832 | 7.1561 | 5.2203 | -3.7572 | 29.84 | 6.6904 | 4.8805 | -6.1931 | 29.9973 | 6.6315 | 4.8376 | -6.2794 | 30.1689 | 6.576 | 4.7971 | -6.3458 | 30.3539 | 6.4553 | 4.709 | -6.7797 | 30.5725 | 6.2472 | 4.5572 | -7.164 | 30.7512 | 6.0719 | 4.4294 | -7.6552 | 30.841 | 6.3095 | 4.6027 | -8.2215 | 30.8604 | 6.9751 | 5.0883 | -8.1378 | 29.0547 | 9.7011 | 7.0768 | 8.5188 | 29.1581 | 9.0729 | 6.6185 | 4.7684 | 29.1902 | 8.5543 | 6.2403 | 2.1653 | 29.2498 | 8.0383 | 5.8638 | -0.089432 | 29.3269 | 7.624 | 5.5616 | -1.8522 | 29.4222 | 7.0588 | 5.1493 | -4.8112 | 29.5262 | 6.5751 | 4.7964 | -7.2123 | 29.6357 | 6.4926 | 4.7362 | -7.232 | 29.7499 | 6.3913 | 4.6624 | -6.6579 | 29.8682 | 6.2402 | 4.5522 | -6.939 | 30.204 | 5.7913 | 4.2246 | -7.838 | 30.4424 | 5.6052 | 4.0889 | -7.9412 | 30.5589 | 6.2064 | 4.5275 | -8.5499 | 30.6045 | 6.7901 | 4.9532 | -8.4985 | 29.0477 | 9.618 | 7.0162 | 8.5428 | 29.1456 | 8.8672 | 6.4685 | 4.7274 | 29.1765 | 8.2571 | 6.0234 | 2.256 | 29.2392 | 7.7057 | 5.6212 | 0.02735 | 29.325 | 7.2131 | 5.2618 | -1.7195 | 29.4372 | 6.4012 | 4.6696 | -4.6694 | 29.568 | 6.0224 | 4.3933 | -7.0802 | 29.7123 | 5.9444 | 4.3364 | -7.1221 | 29.8693 | 5.93 | 4.3258 | -6.722 | 30.0391 | 5.8298 | 4.2528 | -6.9932 | 30.4943 | 5.1858 | 3.7829 | -7.9611 | 27.5047 | 4.4615 | 3.2546 | -9.5827 | 27.8643 | 4.5199 | 3.2972 | -11.5512 | 29.8991 | 4.8499 | 3.538 | -12.5128 | 29.0299 | 9.617 | 7.0155 | 8.5283 | 29.114 | 8.8989 | 6.4917 | 4.7165 | 29.1277 | 8.3096 | 6.0617 | 2.2025 | 29.1681 | 7.7349 | 5.6425 | -0.015996 | 29.2306 | 7.2058 | 5.2565 | -1.7584 | 29.316 | 6.5256 | 4.7603 | -4.6851 | 29.4204 | 5.9642 | 4.3508 | -7.0615 | 29.5334 | 5.9432 | 4.3355 | -7.054 | 29.6554 | 5.9338 | 4.3286 | -6.5197 | 29.7929 | 5.6643 | 4.1321 | -7.0908 | 28.1118 | 4.56 | 3.3265 | -9.4882 | 23.4132 | 3.7979 | 2.7705 | -10.7394 | 28.2687 | 4.5855 | 3.345 | -12.1856 | 28.2078 | 4.5756 | 3.3378 | -11.5838
POULTON | BISPHAM | PENWORTHAM WEST / STANAH | 335679 | 439130 | 20.372 | 9.2306 | 6.7336 | 15.8526 | 20.525 | 8.7812 | 6.4058 | 15.41 | 20.7793 | 8.7599 | 6.3902 | 15.1547 | 20.8943 | 8.7852 | 6.4087 | 14.8809 | 20.9902 | 8.6948 | 6.3428 | 14.6533 | 21.108 | 8.6639 | 6.3202 | 14.4038 | 21.2443 | 8.5641 | 6.2474 | 14.065 | 21.3941 | 8.4283 | 6.1484 | 13.7207 | 21.5558 | 8.1998 | 5.9816 | 13.2592 | 21.7337 | 8.1166 | 5.921 | 12.7801 | 22.5668 | 7.907 | 5.7681 | 10.7157 | 23.4168 | 9.485 | 6.9191 | 9.4065 | 24.0327 | 12.952 | 9.4483 | 8.9348 | 24.5946 | 13.4414 | 9.8053 | 8.7713 | 20.3906 | 9.2548 | 6.7512 | 16.1241 | 20.553 | 9.285 | 6.7733 | 15.9072 | 20.7862 | 9.2884 | 6.7758 | 15.5983 | 20.904 | 8.9948 | 6.5616 | 15.1601 | 21.0166 | 8.8819 | 6.4792 | 14.7154 | 21.1437 | 8.755 | 6.3867 | 14.2159 | 21.2879 | 8.6262 | 6.2927 | 13.6093 | 21.4457 | 8.48 | 6.1861 | 13.0016 | 21.617 | 8.3006 | 6.0552 | 12.325 | 21.8012 | 8.2034 | 5.9843 | 11.5319 | 22.2354 | 8.2997 | 6.0545 | 10.8521 | 22.6573 | 9.5352 | 6.9558 | 10.4017 | 23.0242 | 11.8775 | 8.6645 | 10.1696 | 23.3186 | 12.4516 | 9.0833 | 9.9846 | 20.373 | 9.2562 | 6.7523 | 15.8224 | 20.5266 | 9.3544 | 6.8239 | 15.3708 | 20.7814 | 9.3037 | 6.7869 | 15.1235 | 20.897 | 9.0957 | 6.6352 | 14.9063 | 20.9932 | 8.8718 | 6.4719 | 14.6563 | 21.1104 | 8.6899 | 6.3391 | 14.4243 | 21.2459 | 8.5372 | 6.2278 | 14.114 | 21.3947 | 8.3564 | 6.0959 | 13.7022 | 21.5533 | 8.1169 | 5.9211 | 13.2596 | 21.7216 | 7.9452 | 5.7959 | 12.824 | 22.4644 | 7.8938 | 5.7584 | 11.1171 | 23.0926 | 10.0241 | 7.3124 | 10.0944 | 23.5762 | 13.5589 | 9.891 | 9.7665 | 23.9529 | 14.3699 | 10.4826 | 9.756 | 20.3725 | 9.2277 | 6.7315 | 15.8701 | 20.525 | 8.7899 | 6.4121 | 15.4427 | 20.774 | 8.9546 | 6.5322 | 15.1862 | 20.9284 | 8.9139 | 6.5025 | 14.9376 | 21.0596 | 8.7649 | 6.3939 | 14.6833 | 21.2344 | 8.6107 | 6.2814 | 14.4196 | 21.4528 | 8.4437 | 6.1596 | 14.0583 | 21.7075 | 8.2761 | 6.0373 | 13.682 | 21.9945 | 8.1377 | 5.9363 | 13.343 | 22.3169 | 8.1283 | 5.9295 | 12.9599 | 23.7291 | 7.3107 | 5.3331 | 10.3339 | 25.1103 | 8.5175 | 6.2134 | 5.9333 | 25.9281 | 11.0938 | 8.0927 | 2.58 | 26.2748 | 11.141 | 8.1272 | -0.070546 | 20.4307 | 9.2278 | 6.7316 | 15.8592 | 20.6748 | 8.8639 | 6.4661 | 15.3962 | 20.8526 | 8.9067 | 6.4973 | 15.1294 | 20.9483 | 9.0152 | 6.5764 | 14.9039 | 21.078 | 8.9392 | 6.521 | 14.6477 | 21.2537 | 8.8371 | 6.4466 | 14.4061 | 21.4847 | 8.777 | 6.4027 | 14.0627 | 21.7507 | 8.7855 | 6.4089 | 13.712 | 22.0553 | 8.7947 | 6.4156 | 13.3129 | 22.4224 | 8.7101 | 6.3539 | 12.4063 | 23.8972 | 13.9173 | 10.1525 | 7.4578 | 25.0143 | 12.4142 | 9.056 | 3.2635 | 25.5052 | 11.5955 | 8.4587 | 0.72471 | 25.5471 | 11.4018 | 8.3175 | 1.0159
POYNTON | HAZEL GROVE | BREDBURY | 392096 | 383493 | 23.6399 | 13.2745 | 9.5407 | 11.5585 | 23.685 | 13.1458 | 9.4481 | 11.0948 | 23.7105 | 13.0331 | 9.3672 | 10.9174 | 23.7663 | 12.8652 | 9.2465 | 10.6147 | 23.8236 | 12.7019 | 9.1291 | 10.5024 | 23.8945 | 12.7706 | 9.1785 | 10.2107 | 23.9728 | 12.7134 | 9.1374 | 9.8332 | 24.0561 | 12.6928 | 9.1226 | 9.7518 | 24.1451 | 12.6334 | 9.0799 | 9.4442 | 24.2432 | 12.5354 | 9.0095 | 9.0483 | 24.7515 | 12.1245 | 8.7141 | 7.8137 | 25.3341 | 11.7485 | 8.4438 | 6.9527 | 25.7758 | 11.5026 | 8.2672 | 6.5012 | 26.204 | 11.3025 | 8.1233 | 6.3739 | 23.6169 | 13.2995 | 9.5586 | 11.7118 | 23.6448 | 13.0955 | 9.412 | 11.3913 | 23.6877 | 13.0169 | 9.3555 | 11.1959 | 23.7387 | 12.9592 | 9.3141 | 10.8826 | 23.7992 | 12.9319 | 9.2944 | 10.7691 | 23.8668 | 12.8717 | 9.2511 | 10.4843 | 23.9413 | 12.8318 | 9.2225 | 10.1101 | 24.0201 | 12.8221 | 9.2155 | 10.0211 | 24.1022 | 12.778 | 9.1838 | 9.7052 | 24.1866 | 12.7186 | 9.1411 | 9.3367 | 24.4962 | 12.5717 | 9.0355 | 8.3914 | 24.8186 | 12.4019 | 8.9135 | 7.5875 | 25.1315 | 12.2913 | 8.834 | 6.9115 | 25.4025 | 12.153 | 8.7346 | 6.5094 | 23.6401 | 13.2914 | 9.5528 | 11.5627 | 23.6855 | 13.1745 | 9.4688 | 11.1188 | 23.7115 | 13.0528 | 9.3813 | 10.9592 | 23.7679 | 12.9579 | 9.3131 | 10.6687 | 23.8255 | 12.9624 | 9.3163 | 10.5703 | 23.8966 | 12.9175 | 9.2841 | 10.2953 | 23.9753 | 12.867 | 9.2478 | 9.9358 | 24.059 | 12.8457 | 9.2324 | 9.8667 | 24.1474 | 12.7817 | 9.1865 | 9.5805 | 24.2417 | 12.689 | 9.1198 | 9.2232 | 24.6876 | 12.3539 | 8.879 | 8.0858 | 25.0934 | 12.1374 | 8.7234 | 7.3964 | 25.4589 | 11.9385 | 8.5804 | 7.0186 | 25.7496 | 11.7705 | 8.4597 | 6.9781 | 23.6379 | 13.2741 | 9.5404 | 11.5696 | 23.6845 | 13.1374 | 9.4421 | 11.1216 | 23.7209 | 12.9987 | 9.3424 | 10.9627 | 23.7757 | 12.7966 | 9.1971 | 10.671 | 23.8472 | 12.7249 | 9.1457 | 10.5933 | 23.9459 | 12.7753 | 9.1819 | 10.3367 | 24.0668 | 12.709 | 9.1342 | 9.9849 | 24.2049 | 12.678 | 9.1119 | 9.9261 | 24.3585 | 12.6056 | 9.0599 | 9.675 | 24.5235 | 12.5194 | 8.998 | 9.3741 | 25.446 | 11.7828 | 8.4686 | 7.7459 | 26.6047 | 10.7729 | 7.7427 | 4.2795 | 27.3684 | 9.9313 | 7.1378 | 1.4892 | 27.6466 | 9.3258 | 6.7026 | -0.25762 | 23.6423 | 13.2729 | 9.5395 | 11.5572 | 23.7007 | 13.1017 | 9.4164 | 11.0939 | 23.7357 | 12.8944 | 9.2674 | 10.9476 | 23.7867 | 12.8601 | 9.2428 | 10.6817 | 23.8591 | 12.9135 | 9.2812 | 10.629 | 23.9632 | 12.9093 | 9.2782 | 10.4061 | 24.0981 | 12.7818 | 9.1866 | 10.0875 | 24.2534 | 12.7489 | 9.1629 | 10.0616 | 24.4379 | 12.6446 | 9.0879 | 9.7349 | 24.7001 | 12.3968 | 8.9099 | 8.8944 | 25.8956 | 11.2506 | 8.0861 | 5.2455 | 26.884 | 10.2766 | 7.386 | 2.0843 | 27.2027 | 9.688 | 6.963 | 0.18042 | 27.1888 | 9.5121 | 6.8365 | 0.57457
PREESALL | THORNTON | PENWORTHAM WEST / STANAH | 336965 | 446547 | 30.1337 | 14.9132 | 10.7184 | 16.4266 | 30.3152 | 14.6961 | 10.5624 | 16.0218 | 30.4586 | 14.385 | 10.3388 | 15.6955 | 30.5267 | 14.0298 | 10.0835 | 15.2675 | 30.6109 | 13.6858 | 9.8363 | 14.998 | 30.7113 | 13.2697 | 9.5372 | 14.5554 | 30.8269 | 13.1698 | 9.4654 | 14.1078 | 30.9519 | 13.2218 | 9.5028 | 13.6148 | 31.0859 | 13.2192 | 9.5009 | 13.1609 | 31.251 | 13.1364 | 9.4414 | 12.4798 | 31.9267 | 12.7451 | 9.1601 | 10.1763 | 32.3357 | 12.6583 | 9.0978 | 9.0362 | 32.5218 | 12.839 | 9.2276 | 8.8373 | 32.5899 | 12.6533 | 9.0942 | 9.3317 | 30.1523 | 14.9064 | 10.7136 | 16.595 | 30.3356 | 14.8245 | 10.6546 | 16.3401 | 30.4249 | 14.8587 | 10.6792 | 15.9972 | 30.5004 | 14.772 | 10.6169 | 15.6454 | 30.5874 | 14.6605 | 10.5368 | 15.4496 | 30.6848 | 14.6114 | 10.5015 | 15.0848 | 30.7952 | 14.5324 | 10.4447 | 14.7131 | 30.9144 | 14.4673 | 10.398 | 14.2916 | 31.0422 | 14.3683 | 10.3268 | 13.8854 | 31.1782 | 14.3358 | 10.3034 | 13.4242 | 31.4696 | 14.1625 | 10.1789 | 12.181 | 31.7463 | 13.8667 | 9.9663 | 11.0172 | 31.9076 | 13.9959 | 10.0591 | 10.2397 | 31.9581 | 14.0143 | 10.0723 | 9.7217 | 30.1343 | 14.8974 | 10.707 | 16.4329 | 30.3159 | 14.9076 | 10.7144 | 16.0431 | 30.4591 | 14.8986 | 10.7079 | 15.7349 | 30.5272 | 14.9497 | 10.7446 | 15.3313 | 30.6111 | 14.809 | 10.6435 | 15.0828 | 30.7108 | 14.7516 | 10.6023 | 14.6642 | 30.8255 | 14.6084 | 10.4994 | 14.2398 | 30.9495 | 14.5422 | 10.4518 | 13.7703 | 31.0812 | 14.4355 | 10.3751 | 13.3431 | 31.2387 | 14.2264 | 10.2248 | 12.7326 | 31.8784 | 13.7827 | 9.9059 | 10.6962 | 32.2578 | 13.3069 | 9.5639 | 9.6758 | 32.4201 | 13.3374 | 9.5858 | 9.5619 | 32.4814 | 13.0578 | 9.3849 | 9.9956 | 30.1343 | 14.9137 | 10.7188 | 16.442 | 30.339 | 14.6811 | 10.5516 | 16.0232 | 30.4703 | 14.1254 | 10.1522 | 15.6848 | 30.5631 | 13.6448 | 9.8068 | 15.2628 | 30.6913 | 13.5648 | 9.7493 | 14.9791 | 30.8567 | 13.5592 | 9.7452 | 14.4995 | 31.0593 | 13.5273 | 9.7223 | 13.979 | 31.2876 | 13.2783 | 9.5434 | 13.4109 | 31.4782 | 13.343 | 9.5899 | 12.9576 | 31.6745 | 13.3172 | 9.5713 | 12.4486 | 32.3112 | 12.778 | 9.1838 | 10.5436 | 32.8216 | 11.7224 | 8.4251 | 8.1829 | 33.0471 | 11.7561 | 8.4494 | 7.102 | 33.1364 | 11.3112 | 8.1296 | 6.1413 | 30.1981 | 14.9079 | 10.7146 | 16.4071 | 30.4232 | 14.7622 | 10.6099 | 15.9345 | 30.4885 | 14.4309 | 10.3717 | 15.5887 | 30.5791 | 14.0049 | 10.0656 | 15.1663 | 30.7032 | 13.9239 | 10.0074 | 14.8738 | 30.853 | 14.005 | 10.0656 | 14.4246 | 31.038 | 13.7999 | 9.9183 | 13.9731 | 31.2388 | 13.9306 | 10.0122 | 13.5073 | 31.4459 | 13.92 | 10.0046 | 13.1665 | 31.6477 | 13.8006 | 9.9188 | 12.457 | 32.2548 | 12.8817 | 9.2584 | 9.4228 | 32.5525 | 12.2171 | 8.7806 | 7.6445 | 32.5983 | 11.8024 | 8.4826 | 7.0744 | 32.5154 | 11.6325 | 8.3605 | 7.5739
PRESTON EAST | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 356777 | 432926 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 4.8315 | 0.78371 | 0.57171 | 4.8315 | 9.7725 | 1.5852 | 1.1564 | 9.7725 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 0.95992 | 0.15571 | 0.11359 | 0.95992 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.6657 | 0.91903 | 0.67042 | 5.6657 | 10.7542 | 1.7444 | 1.2725 | 10.7542 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 0.43712 | 0.070905 | 0.051725 | 0.43712 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 6.5332 | 1.0598 | 0.77308 | 6.5332 | 1.4137 | 0.22931 | 0.16728 | 1.4137 | 1.8032 | 0.2925 | 0.21337 | 1.8032 | 1.7966 | 0.29143 | 0.21259 | 1.7966
PRESTON OLD RD | BLACKPOOL | PENWORTHAM WEST / STANAH | 332562 | 434929 | 30.7217 | 12.1236 | 8.844 | 15.8088 | 30.7661 | 12.0461 | 8.7875 | 15.5596 | 30.7764 | 11.8633 | 8.6541 | 15.4038 | 30.818 | 11.9505 | 8.7177 | 15.1982 | 30.8818 | 11.9414 | 8.7111 | 14.999 | 30.9644 | 11.8709 | 8.6597 | 14.7589 | 31.0597 | 11.7422 | 8.5657 | 14.4546 | 31.164 | 11.5874 | 8.4528 | 14.1561 | 31.2776 | 11.4815 | 8.3756 | 13.8542 | 31.3807 | 11.3369 | 8.2701 | 13.4565 | 31.7036 | 10.678 | 7.7895 | 12.2608 | 31.9079 | 10.5592 | 7.7028 | 11.7344 | 32.0008 | 10.6233 | 7.7495 | 11.7567 | 32.024 | 10.7312 | 7.8283 | 12.1605 | 30.6774 | 12.2199 | 8.9142 | 16.0022 | 30.6884 | 12.1933 | 8.8948 | 15.9136 | 30.729 | 12.1923 | 8.8941 | 15.7039 | 30.7857 | 12.1629 | 8.8726 | 15.494 | 30.8528 | 12.1118 | 8.8354 | 15.3176 | 30.9293 | 12.0471 | 8.7882 | 15.1082 | 31.0158 | 11.9734 | 8.7344 | 14.8305 | 31.1095 | 11.8882 | 8.6723 | 14.5545 | 31.2113 | 11.7849 | 8.5969 | 14.2749 | 31.3195 | 11.6794 | 8.52 | 13.9643 | 31.5012 | 11.4438 | 8.3481 | 13.2105 | 31.6371 | 11.2638 | 8.2168 | 12.5995 | 31.7139 | 10.9582 | 7.9938 | 12.2861 | 31.7386 | 11.2409 | 8.2001 | 12.1855 | 30.7217 | 12.221 | 8.915 | 15.8146 | 30.7661 | 12.2804 | 8.9584 | 15.5795 | 30.7764 | 12.2726 | 8.9527 | 15.4386 | 30.818 | 12.1505 | 8.8636 | 15.2438 | 30.8815 | 11.9841 | 8.7422 | 15.0563 | 30.9635 | 11.7832 | 8.5957 | 14.8277 | 31.0582 | 11.5947 | 8.4581 | 14.5347 | 31.1622 | 11.4045 | 8.3194 | 14.2466 | 31.2739 | 11.2659 | 8.2183 | 13.9621 | 31.3728 | 11.2684 | 8.2201 | 13.6077 | 31.6721 | 11.0567 | 8.0657 | 12.5604 | 31.8574 | 10.8434 | 7.9101 | 12.1346 | 31.9408 | 10.9056 | 7.9555 | 12.1963 | 31.9615 | 10.8937 | 7.9468 | 12.5889 | 30.717 | 12.125 | 8.845 | 15.8255 | 30.7601 | 12.0463 | 8.7876 | 15.5946 | 30.7789 | 12.1776 | 8.8834 | 15.4657 | 30.8392 | 12.0686 | 8.8039 | 15.2933 | 30.9348 | 11.9271 | 8.7007 | 15.1344 | 31.0627 | 11.7423 | 8.5659 | 14.9303 | 31.1671 | 11.5127 | 8.3984 | 14.6343 | 31.2836 | 11.2197 | 8.1846 | 14.3494 | 31.4136 | 11.3018 | 8.2445 | 14.111 | 31.5601 | 11.2648 | 8.2175 | 13.8448 | 31.9941 | 10.6431 | 7.764 | 12.0832 | 32.3787 | 9.588 | 6.9943 | 7.8724 | 32.5667 | 8.989 | 6.5573 | 4.6631 | 32.6386 | 8.569 | 6.251 | 2.6249 | 30.7134 | 12.1253 | 8.8453 | 15.8212 | 30.7625 | 12.0162 | 8.7656 | 15.5643 | 30.7847 | 11.9669 | 8.7297 | 15.4348 | 30.8415 | 11.9955 | 8.7505 | 15.2812 | 30.9336 | 11.947 | 8.7152 | 15.1157 | 31.0195 | 11.7987 | 8.607 | 14.9323 | 31.1075 | 11.643 | 8.4934 | 14.682 | 31.2039 | 11.4793 | 8.374 | 14.4551 | 31.3173 | 11.2727 | 8.2233 | 14.1305 | 31.4737 | 10.8542 | 7.918 | 13.0839 | 31.9544 | 9.8458 | 7.1824 | 8.3638 | 32.2179 | 8.8669 | 6.4683 | 4.593 | 32.2585 | 8.4938 | 6.1961 | 2.5873 | 32.1148 | 8.5997 | 6.2734 | 3.5644
PRESTWICH | AGECROFT | KEARSLEY | 381392 | 404001 | 31.8352 | 8.033 | 5.8599 | 11.5867 | 31.9528 | 7.7152 | 5.6281 | 10.8903 | 32.0546 | 7.468 | 5.4478 | 10.8812 | 32.1782 | 7.1221 | 5.1955 | 10.3794 | 32.3366 | 6.7796 | 4.9456 | 10.1599 | 32.5154 | 6.5652 | 4.7892 | 9.4838 | 32.7092 | 6.5292 | 4.763 | 8.9654 | 32.9189 | 6.4419 | 4.6993 | 8.406 | 33.1452 | 6.332 | 4.6191 | 7.8407 | 33.4179 | 6.178 | 4.5067 | 7.1046 | 34.4558 | 5.5953 | 4.0817 | 5.0552 | 33.9878 | 5.5132 | 4.0218 | 4.1408 | 35.3619 | 5.736 | 4.1844 | 3.9279 | 34.8537 | 5.6536 | 4.1242 | 4.3047 | 31.7972 | 7.9175 | 5.7757 | 11.7462 | 31.881 | 7.682 | 5.6039 | 11.1949 | 32.0015 | 7.5792 | 5.529 | 11.0864 | 32.0972 | 7.37 | 5.3763 | 10.5514 | 32.2139 | 7.1559 | 5.2201 | 10.4007 | 32.3436 | 6.9666 | 5.0821 | 9.8082 | 32.4838 | 6.856 | 5.0013 | 9.3461 | 32.6326 | 6.7246 | 4.9055 | 8.8408 | 32.7896 | 6.6024 | 4.8163 | 8.3336 | 32.9515 | 6.4664 | 4.7172 | 7.6835 | 33.4759 | 6.2111 | 4.5309 | 6.2637 | 33.9408 | 6.1663 | 4.4982 | 5.2895 | 34.28 | 6.3081 | 4.6016 | 4.6451 | 34.3939 | 6.2619 | 4.568 | 4.3968 | 31.8352 | 7.9089 | 5.7695 | 11.598 | 31.9528 | 7.7268 | 5.6366 | 10.9378 | 32.0547 | 7.5996 | 5.5438 | 10.9686 | 32.1784 | 7.3189 | 5.339 | 10.4892 | 32.3363 | 7.073 | 5.1596 | 10.2282 | 32.5141 | 6.8809 | 5.0195 | 9.5569 | 32.7071 | 6.7723 | 4.9403 | 9.0411 | 32.9162 | 6.6587 | 4.8575 | 8.4977 | 33.1396 | 6.5377 | 4.7692 | 7.958 | 33.4003 | 6.3773 | 4.6522 | 7.2868 | 34.3882 | 5.9455 | 4.3371 | 5.4344 | 34.9013 | 5.8917 | 4.2979 | 4.7175 | 35.2318 | 6.1927 | 4.5175 | 4.563 | 35.4454 | 6.0953 | 4.4464 | 4.9365 | 31.8333 | 8.035 | 5.8614 | 11.6058 | 31.9652 | 7.7134 | 5.6268 | 10.9286 | 32.1059 | 7.4403 | 5.4276 | 10.95 | 32.2899 | 7.0904 | 5.1724 | 10.478 | 32.5362 | 6.7188 | 4.9012 | 10.3128 | 32.8437 | 6.6308 | 4.837 | 9.7028 | 33.2135 | 6.5756 | 4.7968 | 9.2402 | 33.5889 | 6.4698 | 4.7196 | 8.7498 | 33.9349 | 6.3852 | 4.6579 | 8.3425 | 34.2573 | 6.2504 | 4.5596 | 7.8037 | 33.7738 | 5.4784 | 3.9964 | 5.2819 | 27.8606 | 4.5193 | 3.2967 | 0.40683 | 24.0469 | 3.9006 | 2.8455 | -3.4899 | 20.1917 | 3.2753 | 2.3893 | -5.9902 | 31.8332 | 8.035 | 5.8614 | 11.593 | 31.9846 | 7.7548 | 5.657 | 10.8731 | 32.1405 | 7.4797 | 5.4564 | 10.8669 | 32.3334 | 7.0623 | 5.1518 | 10.4349 | 32.589 | 7.0665 | 5.1549 | 10.2841 | 32.8912 | 6.9668 | 5.0822 | 9.7349 | 33.2066 | 6.8525 | 4.9988 | 9.3405 | 33.4999 | 6.7596 | 4.931 | 8.9453 | 33.823 | 6.6306 | 4.8369 | 8.4951 | 34.2094 | 6.3306 | 4.6181 | 7.1288 | 33.9864 | 5.5129 | 4.0216 | 1.3068 | 25.6909 | 4.1673 | 3.04 | -3.0691 | 21.2922 | 3.4538 | 2.5195 | -5.6251 | 21.198 | 3.4385 | 2.5084 | -4.5615
PRINGLE ST | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 369088 | 427387 | 30.1028 | 13.7159 | 10.0056 | 15.875 | 30.1748 | 11.9029 | 8.683 | 15.5051 | 30.2167 | 9.8682 | 7.1987 | 15.4926 | 30.2895 | 7.7394 | 5.6458 | 15.0534 | 30.3892 | 5.6229 | 4.1018 | 15.1092 | 21.3624 | 3.4652 | 2.5278 | 14.6952 | 23.1925 | 3.7621 | 2.7444 | 14.4708 | 22.8574 | 3.7077 | 2.7047 | 14.2853 | 22.2136 | 3.6033 | 2.6285 | 13.9172 | 21.3936 | 3.4703 | 2.5315 | 13.5148 | 19.562 | 3.1731 | 2.3148 | 12.4351 | 32.6804 | 5.61 | 4.0924 | 11.8039 | 33.0708 | 10.3684 | 7.5636 | 10.9919 | 33.2674 | 10.5777 | 7.7163 | 10.3192 | 30.0733 | 13.7574 | 10.0358 | 16.0011 | 30.1218 | 11.8831 | 8.6685 | 15.7306 | 30.2035 | 10.0277 | 7.315 | 15.6334 | 30.3024 | 8.12 | 5.9234 | 15.1719 | 30.4187 | 6.3221 | 4.6119 | 15.2204 | 27.4888 | 4.459 | 3.2527 | 14.8133 | 27.017 | 4.3824 | 3.1969 | 14.5871 | 26.547 | 4.3062 | 3.1413 | 14.3936 | 25.8507 | 4.1932 | 3.0589 | 14.0092 | 25.0713 | 4.0668 | 2.9667 | 13.6225 | 24.0645 | 3.9035 | 2.8475 | 12.9062 | 31.5622 | 5.1197 | 3.7348 | 12.3771 | 32.3226 | 8.6765 | 6.3294 | 12.0109 | 32.4245 | 10.0383 | 7.3228 | 11.956 | 30.1115 | 13.7524 | 10.0322 | 15.889 | 30.1863 | 11.7659 | 8.5831 | 15.5344 | 30.23 | 9.7346 | 7.1013 | 15.5334 | 30.3034 | 7.599 | 5.5433 | 15.1116 | 30.4024 | 5.5937 | 4.0805 | 15.1772 | 22.8824 | 3.7118 | 2.7077 | 14.7817 | 23.2764 | 3.7757 | 2.7543 | 14.5717 | 23.3849 | 3.7933 | 2.7671 | 14.3997 | 22.9921 | 3.7295 | 2.7206 | 14.0536 | 22.4978 | 3.6494 | 2.6622 | 13.6885 | 22.882 | 3.7117 | 2.7076 | 12.7127 | 32.4488 | 5.9514 | 4.3414 | 12.176 | 32.7189 | 10.6969 | 7.8033 | 11.938 | 32.8414 | 11.4474 | 8.3507 | 12.0975 | 30.1116 | 13.7113 | 10.0022 | 15.8743 | 30.1872 | 11.8831 | 8.6685 | 15.5016 | 30.2392 | 9.7882 | 7.1404 | 15.4839 | 30.3285 | 7.5722 | 5.5238 | 15.0347 | 30.4533 | 5.2377 | 3.8209 | 15.0826 | 22.6243 | 3.6699 | 2.6771 | 14.6547 | 22.9147 | 3.717 | 2.7115 | 14.4066 | 22.1762 | 3.5972 | 2.6241 | 14.1891 | 21.1563 | 3.4318 | 2.5034 | 13.8218 | 19.9064 | 3.229 | 2.3555 | 13.4568 | 13.6818 | 2.2193 | 1.619 | 11.7013 | 26.6811 | 4.3279 | 3.1572 | 7.4609 | 34.6797 | 8.1984 | 5.9806 | 3.8002 | 34.9129 | 8.2122 | 5.9907 | 1.2992 | 30.1064 | 13.7137 | 10.004 | 15.888 | 30.1845 | 13.4727 | 9.8282 | 15.5208 | 30.2382 | 13.1088 | 9.5627 | 15.5234 | 30.3245 | 13.1742 | 9.6104 | 15.1183 | 30.4471 | 12.871 | 9.3892 | 15.2141 | 30.6378 | 12.2549 | 8.9398 | 14.8475 | 30.8739 | 12.5186 | 9.1321 | 14.647 | 31.0678 | 12.4656 | 9.0935 | 14.483 | 31.3046 | 12.2974 | 8.9708 | 14.0684 | 31.6684 | 12.06 | 8.7976 | 12.9556 | 33.0959 | 10.8927 | 7.9461 | 8.2951 | 33.94 | 9.9103 | 7.2294 | 4.4624 | 34.1394 | 8.9562 | 6.5334 | 1.9603 | 33.9603 | 8.5372 | 6.2278 | 2.5201
GRANE RD & PRINNY HILL | ROSSENDALE | PADIHAM | 378328 | 423395 | 25.5536 | 12.3002 | 8.9728 | 14.3062 | 25.6309 | 12.211 | 8.9078 | 14.0753 | 25.6473 | 12.1136 | 8.8367 | 13.9769 | 25.6866 | 11.9062 | 8.6854 | 13.8203 | 25.7423 | 11.7422 | 8.5657 | 13.6234 | 25.8136 | 11.3969 | 8.3139 | 13.3916 | 25.8922 | 11.5263 | 8.4083 | 13.1387 | 25.976 | 11.5572 | 8.4308 | 12.8814 | 26.0613 | 11.5884 | 8.4536 | 12.6122 | 26.1398 | 11.5751 | 8.4439 | 12.3222 | 26.44 | 11.3624 | 8.2887 | 11.4347 | 26.6367 | 11.1257 | 8.116 | 11.1553 | 26.7342 | 11.4135 | 8.326 | 11.276 | 26.7751 | 11.2825 | 8.2305 | 11.5312 | 25.4811 | 12.3563 | 9.0138 | 14.5005 | 25.4979 | 12.2335 | 8.9242 | 14.4322 | 25.5417 | 12.0205 | 8.7688 | 14.2722 | 25.5972 | 11.9125 | 8.69 | 14.088 | 25.6585 | 11.8353 | 8.6337 | 13.8968 | 25.7239 | 11.7623 | 8.5804 | 13.6849 | 25.7953 | 11.7339 | 8.5597 | 13.4496 | 25.8702 | 11.6794 | 8.52 | 13.2072 | 25.9484 | 11.6304 | 8.4842 | 12.9583 | 26.0292 | 11.5769 | 8.4452 | 12.7124 | 26.189 | 11.4019 | 8.3175 | 12.0346 | 26.2963 | 11.3519 | 8.2811 | 11.6062 | 26.3484 | 11.6041 | 8.4651 | 11.4482 | 26.3531 | 11.8307 | 8.6303 | 11.4511 | 25.5536 | 12.3617 | 9.0177 | 14.3091 | 25.6309 | 12.266 | 8.9479 | 14.082 | 25.6473 | 12.0848 | 8.8157 | 13.9876 | 25.6866 | 11.9595 | 8.7243 | 13.8346 | 25.7421 | 11.9196 | 8.6952 | 13.6476 | 25.8129 | 11.7373 | 8.5622 | 13.4217 | 25.8912 | 11.7354 | 8.5608 | 13.1745 | 25.9747 | 11.6574 | 8.5039 | 12.9202 | 26.0592 | 11.5457 | 8.4224 | 12.6544 | 26.1335 | 11.4243 | 8.3339 | 12.3892 | 26.4138 | 11.1376 | 8.1247 | 11.58 | 26.5935 | 11.0012 | 8.0252 | 11.3418 | 26.682 | 11.3765 | 8.299 | 11.4787 | 26.72 | 11.1541 | 8.1368 | 11.7465 | 25.547 | 12.2981 | 8.9713 | 14.3233 | 25.6199 | 12.1996 | 8.8994 | 14.1159 | 25.6382 | 12.0735 | 8.8074 | 14.0487 | 25.6855 | 11.8921 | 8.6751 | 13.9288 | 25.7565 | 11.6212 | 8.4775 | 13.7862 | 25.8512 | 11.5952 | 8.4585 | 13.6198 | 25.9544 | 11.6683 | 8.5119 | 13.4408 | 26.0572 | 11.7365 | 8.5616 | 13.2699 | 26.1694 | 11.6996 | 8.5347 | 13.1198 | 26.293 | 11.7031 | 8.5373 | 12.9791 | 26.6657 | 11.2945 | 8.2392 | 12.2856 | 26.8866 | 10.5319 | 7.6828 | 11.1655 | 26.9496 | 10.6243 | 7.7503 | 10.472 | 26.9345 | 10.2936 | 7.5091 | 10.0798 | 25.5489 | 12.2967 | 8.9703 | 14.306 | 25.6311 | 12.1829 | 8.8873 | 14.0643 | 25.6544 | 12.0252 | 8.7722 | 13.9888 | 25.7017 | 12.0945 | 8.8228 | 13.8765 | 25.7718 | 12.2108 | 8.9076 | 13.7365 | 25.8607 | 12.1835 | 8.8877 | 13.5941 | 25.9539 | 12.1482 | 8.862 | 13.4383 | 26.047 | 12.1247 | 8.8448 | 13.3007 | 26.1468 | 12.1211 | 8.8422 | 13.1627 | 26.2593 | 12.0463 | 8.7876 | 12.8422 | 26.5706 | 11.757 | 8.5766 | 11.4485 | 26.6901 | 10.9472 | 7.9858 | 10.58 | 26.6563 | 10.5276 | 7.6797 | 10.2451 | 26.5456 | 10.3973 | 7.5847 | 10.6275
QUEENS PARK | STUART ST | STALYBRIDGE | 385893 | 400645 | 26.0785 | 12.4277 | 9.0658 | 5.8555 | 26.227 | 10.0098 | 7.302 | 4.9503 | 26.2678 | 7.1129 | 5.1888 | 1.7029 | 23.145 | 3.7543 | 2.7387 | -4.1619 | 3.2537 | 0.52778 | 0.38501 | -9.8923 | 2.6914 | 0.43658 | 0.31848 | -15.7393 | 2.6914 | 0.43658 | 0.31848 | -21.7671 | 2.6914 | 0.43658 | 0.31848 | -22.0918 | 2.6914 | 0.43658 | 0.31848 | -22.4357 | 2.6914 | 0.43658 | 0.31848 | -23.0837 | 2.6914 | 0.43658 | 0.31848 | -25.0257 | 2.6914 | 0.43658 | 0.31848 | -26.6911 | 18.2862 | 2.9662 | 2.1638 | -27.7425 | 29.6662 | 4.8122 | 3.5104 | -28.4003 | 25.9561 | 12.543 | 9.1499 | 6.3895 | 26.0022 | 10.2185 | 7.4542 | 5.9763 | 26.0947 | 7.2568 | 5.2937 | 2.7658 | 25.2808 | 4.1008 | 2.9915 | -3.1186 | 4.9939 | 0.81006 | 0.59093 | -8.8474 | 2.6914 | 0.43658 | 0.31848 | -14.6675 | 2.6914 | 0.43658 | 0.31848 | -20.6709 | 2.6914 | 0.43658 | 0.31848 | -20.9789 | 2.6914 | 0.43658 | 0.31848 | -21.3053 | 2.6914 | 0.43658 | 0.31848 | -21.8665 | 2.6914 | 0.43658 | 0.31848 | -23.1318 | 2.6914 | 0.43658 | 0.31848 | -24.3401 | 7.4313 | 1.2054 | 0.87934 | -25.308 | 14.9321 | 2.4221 | 1.7669 | -25.9499 | 26.0789 | 12.5419 | 9.1491 | 5.867 | 26.228 | 10.0862 | 7.3577 | 4.9759 | 26.2697 | 7.3313 | 5.3481 | 1.7435 | 23.9527 | 3.8854 | 2.8343 | -4.1083 | 4.6525 | 0.75468 | 0.55053 | -9.8234 | 2.6914 | 0.43658 | 0.31848 | -15.6546 | 2.6914 | 0.43658 | 0.31848 | -21.6657 | 2.6914 | 0.43658 | 0.31848 | -21.9747 | 2.6914 | 0.43658 | 0.31848 | -22.2963 | 2.6914 | 0.43658 | 0.31848 | -22.8946 | 2.6914 | 0.43658 | 0.31848 | -24.5703 | 2.6914 | 0.43658 | 0.31848 | -25.8079 | 23.4988 | 3.8117 | 2.7806 | -26.6432 | 29.9991 | 5.4709 | 3.991 | -27.0182 | 26.0713 | 12.428 | 9.0661 | 5.8628 | 26.2225 | 10.0088 | 7.3013 | 4.9588 | 26.2829 | 7.0712 | 5.1584 | 1.7045 | 22.9049 | 3.7154 | 2.7103 | -4.1797 | 2.8366 | 0.46012 | 0.33565 | -9.9307 | 2.6914 | 0.43658 | 0.31848 | -15.8287 | 2.6914 | 0.43658 | 0.31848 | -21.9585 | 2.6914 | 0.43658 | 0.31848 | -22.4127 | 2.6914 | 0.43658 | 0.31848 | -22.8596 | 2.6914 | 0.43658 | 0.31848 | -23.5624 | 2.6914 | 0.43658 | 0.31848 | -26.5607 | 2.6914 | 0.43658 | 0.31848 | -31.6109 | 6.5873 | 1.0685 | 0.77947 | -35.3971 | 14.7852 | 2.3983 | 1.7495 | -38.01 | 26.0618 | 12.4311 | 9.0683 | 5.8716 | 26.2147 | 12.2268 | 8.9193 | 4.9526 | 26.2847 | 11.5239 | 8.4066 | 1.6931 | 26.4169 | 10.3696 | 7.5645 | -4.1843 | 26.6082 | 9.1041 | 6.6413 | -9.9414 | 26.8069 | 8.0919 | 5.9029 | -15.8373 | 27.0464 | 6.8376 | 4.988 | -21.962 | 27.3265 | 6.6742 | 4.8687 | -22.4127 | 27.6511 | 6.518 | 4.7548 | -22.9261 | 28.0818 | 6.1899 | 4.5155 | -24.2911 | 29.1878 | 4.7345 | 3.4538 | -29.8142 | 21.4665 | 3.4821 | 2.5401 | -34.4238 | 17.7554 | 2.8801 | 2.101 | -37.2495 | 17.4073 | 2.8236 | 2.0598 | -36.7523
RADCLIFFE | - | KEARSLEY | 377524 | 406160 | 51.4613 | 13.562 | 9.7472 | 17.2551 | 51.6075 | 13.2187 | 9.5005 | 15.5023 | 51.7009 | 13.1122 | 9.424 | 15.391 | 51.8551 | 12.7741 | 9.181 | 14.0166 | 52.0582 | 12.6042 | 9.0589 | 13.651 | 52.3041 | 12.2296 | 8.7896 | 12.2972 | 52.581 | 11.9933 | 8.6198 | 11.0409 | 52.8812 | 11.777 | 8.4644 | 10.0408 | 53.2017 | 11.4423 | 8.2238 | 8.4401 | 53.5547 | 11.1179 | 7.9907 | 7.0356 | 55.2977 | 9.6694 | 6.9496 | 1.9643 | 54.8797 | 9.0355 | 6.494 | -0.0025578 | 51.2818 | 8.4432 | 6.0683 | -0.34781 | 50.2713 | 8.2768 | 5.9487 | 0.29583 | 51.3762 | 13.6916 | 9.8404 | 17.9642 | 51.4565 | 13.5459 | 9.7357 | 16.8366 | 51.6042 | 13.4585 | 9.6729 | 16.559 | 51.7795 | 13.2054 | 9.491 | 15.3126 | 51.9779 | 13.1339 | 9.4396 | 15.1337 | 52.2013 | 12.9039 | 9.2743 | 14.0074 | 52.4504 | 12.7143 | 9.138 | 12.963 | 52.7192 | 12.5587 | 9.0262 | 12.1495 | 53.0076 | 12.3038 | 8.843 | 10.7444 | 53.3117 | 12.094 | 8.6922 | 9.6294 | 54.006 | 11.4703 | 8.244 | 6.4079 | 54.5677 | 10.9509 | 7.8706 | 4.4182 | 55.0072 | 10.7451 | 7.7227 | 3.1626 | 55.3247 | 10.5762 | 7.6013 | 2.8043 | 51.4614 | 13.6977 | 9.8448 | 17.2718 | 51.6079 | 13.5528 | 9.7407 | 15.5634 | 51.7017 | 13.4437 | 9.6623 | 15.4856 | 51.8564 | 13.1592 | 9.4577 | 14.0795 | 52.0591 | 13.0526 | 9.3812 | 13.7318 | 52.304 | 12.7852 | 9.189 | 12.4125 | 52.58 | 12.544 | 9.0156 | 11.1868 | 52.8798 | 12.3505 | 8.8765 | 10.2114 | 53.1961 | 12.0309 | 8.6468 | 8.6637 | 53.5303 | 11.7453 | 8.4416 | 7.3839 | 55.1499 | 11.0498 | 7.9417 | 2.7652 | 56.0473 | 10.4905 | 7.5398 | 1.1541 | 56.6105 | 10.0812 | 7.2455 | 0.98009 | 57.0023 | 9.6588 | 6.942 | 1.7572 | 51.4545 | 13.5677 | 9.7514 | 17.309 | 51.5997 | 13.2284 | 9.5075 | 15.6185 | 51.7071 | 13.092 | 9.4095 | 15.5901 | 51.8912 | 12.7587 | 9.1699 | 14.3708 | 52.1438 | 12.6059 | 9.0601 | 14.1619 | 52.4657 | 12.3811 | 8.8985 | 13.002 | 52.8502 | 12.1345 | 8.7213 | 11.9275 | 53.2875 | 11.9106 | 8.5604 | 11.1267 | 53.7713 | 11.5925 | 8.3317 | 9.877 | 54.3103 | 11.3219 | 8.1373 | 8.9623 | 56.9644 | 9.688 | 6.963 | 2.7793 | 45.231 | 7.4469 | 5.3523 | -7.4186 | 34.3545 | 5.6562 | 4.0652 | -14.8718 | 27.5672 | 4.5387 | 3.2621 | -19.6398 | 51.4554 | 13.5605 | 9.7462 | 17.2413 | 51.6259 | 13.2142 | 9.4973 | 15.3943 | 51.7466 | 13.0331 | 9.3672 | 15.3048 | 51.9258 | 12.7642 | 9.1739 | 13.9981 | 52.1704 | 12.6404 | 9.0849 | 13.7853 | 52.8824 | 12.2533 | 8.8067 | 12.3239 | 53.645 | 11.8208 | 8.4958 | 10.9719 | 54.0113 | 11.6403 | 8.3661 | 10.3931 | 54.4359 | 11.3581 | 8.1633 | 9.0599 | 55.017 | 10.8605 | 7.8056 | 6.5703 | 50.1614 | 8.2587 | 5.9357 | -5.1979 | 36.7389 | 6.0488 | 4.3474 | -14.0069 | 28.671 | 4.7205 | 3.3927 | -19.0949 | 29.2957 | 4.8233 | 3.4666 | -16.6307
RANDAL ST | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 368092 | 428515 | 35.6818 | 14.0709 | 10.2646 | 17.8312 | 35.763 | 13.73 | 10.0158 | 17.5529 | 35.7979 | 13.0599 | 9.527 | 17.3555 | 35.8504 | 12.568 | 9.1682 | 16.9871 | 35.9279 | 12.2583 | 8.9423 | 16.925 | 36.0263 | 12.1219 | 8.8427 | 16.7359 | 36.1351 | 12.0408 | 8.7836 | 16.3606 | 36.2513 | 11.9157 | 8.6923 | 16.0651 | 36.3754 | 11.8359 | 8.6341 | 15.7353 | 36.514 | 11.6928 | 8.5298 | 15.2266 | 36.9801 | 11.1045 | 8.1005 | 13.8564 | 37.2805 | 10.6865 | 7.7957 | 13.3527 | 37.4298 | 11.4477 | 8.3509 | 13.298 | 37.4888 | 11.3541 | 8.2826 | 13.7094 | 35.634 | 14.1397 | 10.3147 | 18.1576 | 35.6724 | 13.6944 | 9.9898 | 18.093 | 35.745 | 13.2051 | 9.6329 | 17.8128 | 35.8312 | 12.7818 | 9.3242 | 17.3127 | 35.9328 | 12.478 | 9.1025 | 17.2484 | 36.0463 | 12.113 | 8.8363 | 16.9117 | 36.1732 | 12.0039 | 8.7567 | 16.5649 | 36.3098 | 11.8884 | 8.6724 | 16.2238 | 36.4577 | 11.8054 | 8.6119 | 15.7815 | 36.6153 | 11.6719 | 8.5145 | 15.2374 | 36.841 | 11.3923 | 8.3105 | 14.2197 | 36.998 | 11.1758 | 8.1526 | 13.6288 | 37.0778 | 11.5471 | 8.4235 | 13.2513 | 37.1008 | 12.0137 | 8.7638 | 13.248 | 35.6818 | 14.1312 | 10.3085 | 17.8423 | 35.763 | 13.648 | 9.956 | 17.5768 | 35.7979 | 13.1541 | 9.5957 | 17.3957 | 35.8504 | 12.6087 | 9.1978 | 17.0387 | 35.9276 | 12.2182 | 8.913 | 16.9977 | 36.0254 | 11.7325 | 8.5587 | 16.8208 | 36.1337 | 11.6008 | 8.4626 | 16.4694 | 36.2496 | 11.4342 | 8.3411 | 16.1921 | 36.372 | 11.2034 | 8.1727 | 15.9176 | 36.5039 | 10.9797 | 8.0095 | 15.4588 | 36.9405 | 10.5806 | 7.7184 | 14.2276 | 37.2172 | 10.3248 | 7.5318 | 13.7998 | 37.3548 | 11.4169 | 8.3285 | 13.7651 | 37.4107 | 10.9463 | 7.9852 | 14.0937 | 35.6773 | 14.072 | 10.2654 | 17.8505 | 35.7605 | 13.7033 | 9.9963 | 17.59 | 35.7919 | 13.1076 | 9.5618 | 17.4088 | 35.8545 | 12.4649 | 9.0929 | 17.0447 | 35.9492 | 12.4022 | 9.0472 | 17.004 | 36.074 | 12.1486 | 8.8623 | 16.8177 | 36.2206 | 11.9649 | 8.7283 | 16.4553 | 36.3848 | 11.8954 | 8.6775 | 16.1605 | 36.5633 | 11.7814 | 8.5943 | 15.9426 | 36.7626 | 11.6267 | 8.4815 | 15.5649 | 37.4529 | 10.7238 | 7.8229 | 13.9552 | 38.3102 | 9.6046 | 7.0064 | 10.1507 | 38.7103 | 9.6365 | 7.0297 | 6.969 | 38.7502 | 9.0752 | 6.6202 | 5.2323 | 35.6682 | 14.0752 | 10.2676 | 17.8558 | 35.7516 | 13.8427 | 10.098 | 17.5832 | 35.7708 | 14.1119 | 10.2944 | 17.4124 | 35.8194 | 13.9989 | 10.212 | 17.106 | 35.8988 | 13.8032 | 10.0692 | 17.079 | 36.0019 | 13.4816 | 9.8347 | 16.9543 | 36.1279 | 13.0876 | 9.5472 | 16.6358 | 36.2644 | 13.0143 | 9.4937 | 16.4056 | 36.4364 | 12.8462 | 9.3711 | 16.1583 | 36.7204 | 12.5018 | 9.1199 | 15.2292 | 37.7297 | 11.1161 | 8.109 | 10.8656 | 38.0761 | 9.9126 | 7.2311 | 7.3632 | 38.1347 | 9.331 | 6.8069 | 5.3396 | 37.9823 | 9.2539 | 6.7506 | 6.4287
RAWTENSTALL RD | ROSSENDALE | PADIHAM | 379395 | 422143 | 31.0316 | 16.9902 | 12.3941 | 14.445 | 31.0973 | 16.8567 | 12.2967 | 14.0751 | 31.1261 | 16.7025 | 12.1842 | 13.8441 | 31.1781 | 16.5158 | 12.048 | 13.6119 | 31.2481 | 16.2878 | 11.8817 | 13.3111 | 31.3344 | 16.0016 | 11.6729 | 12.9644 | 31.4302 | 15.7344 | 11.478 | 12.5962 | 31.5334 | 15.7318 | 11.4762 | 12.2131 | 31.6435 | 15.6481 | 11.4151 | 11.8116 | 31.766 | 15.504 | 11.31 | 11.3421 | 32.2422 | 14.7848 | 10.7853 | 9.6297 | 32.6631 | 14.254 | 10.3981 | 8.567 | 32.9539 | 14.157 | 10.3274 | 8.1271 | 33.197 | 13.9442 | 10.1721 | 8.0433 | 31.0032 | 17.0196 | 12.4155 | 14.5829 | 31.0513 | 16.9036 | 12.331 | 14.3441 | 31.1256 | 16.7566 | 12.2237 | 14.0418 | 31.2137 | 16.6167 | 12.1216 | 13.7645 | 31.3141 | 16.4793 | 12.0214 | 13.4423 | 31.4259 | 16.3314 | 11.9135 | 13.0722 | 31.5505 | 16.2255 | 11.8363 | 12.6692 | 31.686 | 16.116 | 11.7564 | 12.2407 | 31.8329 | 15.9976 | 11.67 | 11.77 | 31.9914 | 15.8635 | 11.5722 | 11.2241 | 32.2373 | 15.5299 | 11.3288 | 10.1488 | 32.4595 | 15.1798 | 11.0734 | 9.1687 | 32.6451 | 15.1182 | 11.0285 | 8.5451 | 32.7871 | 14.983 | 10.9299 | 8.0887 | 31.0317 | 17.0145 | 12.4119 | 14.4565 | 31.0974 | 16.8872 | 12.319 | 14.1167 | 31.1264 | 16.7211 | 12.1978 | 13.902 | 31.1786 | 16.5545 | 12.0763 | 13.6791 | 31.2486 | 16.3821 | 11.9505 | 13.3999 | 31.3348 | 16.2016 | 11.8188 | 13.0764 | 31.4304 | 16.0618 | 11.7169 | 12.7315 | 31.5336 | 15.9146 | 11.6095 | 12.3718 | 31.6426 | 15.7569 | 11.4944 | 12.0005 | 31.7603 | 15.5799 | 11.3653 | 11.5846 | 32.1973 | 15.0863 | 11.0053 | 10.0545 | 32.5394 | 14.8011 | 10.7972 | 9.1497 | 32.7899 | 14.6258 | 10.6693 | 8.7813 | 32.9714 | 14.3298 | 10.4534 | 8.7372 | 31.0272 | 16.9876 | 12.3922 | 14.451 | 31.0911 | 16.8427 | 12.2865 | 14.09 | 31.1247 | 16.6656 | 12.1573 | 13.8658 | 31.1881 | 16.4622 | 12.0089 | 13.6354 | 31.2766 | 16.2087 | 11.824 | 13.3527 | 31.3927 | 15.9026 | 11.6007 | 13.0181 | 31.5323 | 15.7548 | 11.4929 | 12.6311 | 31.6914 | 15.6874 | 11.4438 | 12.2253 | 31.8667 | 15.5404 | 11.3365 | 11.8556 | 32.0618 | 15.3758 | 11.2165 | 11.4862 | 32.8134 | 14.2542 | 10.3982 | 8.7043 | 33.6046 | 12.7111 | 9.2726 | 2.2017 | 34.106 | 11.5547 | 8.429 | -2.9864 | 34.3578 | 10.6664 | 7.781 | -6.4437 | 31.0141 | 16.9965 | 12.3987 | 14.4907 | 31.0722 | 16.8807 | 12.3143 | 14.1337 | 31.0984 | 16.7228 | 12.199 | 13.9368 | 31.1482 | 16.4759 | 12.019 | 13.7441 | 31.2231 | 16.2256 | 11.8364 | 13.491 | 31.3235 | 16.2266 | 11.8371 | 13.2074 | 31.4506 | 16.1002 | 11.7449 | 12.8868 | 31.5942 | 15.9489 | 11.6345 | 12.555 | 31.7642 | 15.7491 | 11.4887 | 12.0396 | 31.9984 | 15.3657 | 11.2091 | 10.5256 | 32.8979 | 13.5019 | 9.8495 | 3.3953 | 33.535 | 11.9418 | 8.7113 | -2.5055 | 33.7991 | 11.0273 | 8.0442 | -5.9297 | 33.7333 | 10.9264 | 7.9707 | -5.0624
REDDISH VALE | VERNON PARK | BREDBURY | 390147 | 393309 | 30.051 | 10.0801 | 7.3533 | 16.6243 | 30.0837 | 10.3119 | 7.5224 | 16.5328 | 30.1117 | 10.3746 | 7.5681 | 16.2372 | 30.1642 | 10.2941 | 7.5094 | 15.891 | 30.2354 | 10.1858 | 7.4304 | 15.6177 | 30.3214 | 9.9279 | 7.2423 | 15.2607 | 30.4204 | 9.7545 | 7.1158 | 14.7107 | 30.5291 | 9.5756 | 6.9853 | 14.2861 | 30.6474 | 9.3819 | 6.844 | 13.8439 | 30.7795 | 9.129 | 6.6595 | 13.2717 | 31.2624 | 8.4826 | 6.188 | 11.4111 | 31.5923 | 8.0857 | 5.8984 | 10.6119 | 31.7835 | 7.6431 | 5.5755 | 10.48 | 31.8962 | 7.8427 | 5.7211 | 10.8238 | 30.0434 | 10.2829 | 7.5012 | 16.6714 | 30.0733 | 10.3793 | 7.5715 | 16.6153 | 30.1237 | 10.3052 | 7.5175 | 16.2593 | 30.1876 | 10.2419 | 7.4714 | 15.9687 | 30.262 | 10.1496 | 7.404 | 15.7509 | 30.3464 | 10.0913 | 7.3614 | 15.4493 | 30.4416 | 10.003 | 7.297 | 14.9265 | 30.5451 | 9.9459 | 7.2554 | 14.6208 | 30.6575 | 9.884 | 7.2103 | 14.259 | 30.7773 | 9.8012 | 7.1498 | 13.8298 | 30.9967 | 9.5029 | 6.9323 | 12.5413 | 31.1552 | 9.238 | 6.739 | 11.6794 | 31.2581 | 9.0412 | 6.5954 | 11.1496 | 31.3244 | 8.8397 | 6.4484 | 10.9047 | 30.051 | 10.2908 | 7.507 | 16.631 | 30.0837 | 10.3218 | 7.5296 | 16.565 | 30.1117 | 10.2634 | 7.487 | 16.274 | 30.1642 | 10.2197 | 7.4551 | 15.9413 | 30.2351 | 10.1634 | 7.4141 | 15.6826 | 30.3205 | 10.0717 | 7.3472 | 15.3411 | 30.419 | 9.93 | 7.2438 | 14.7882 | 30.5273 | 9.8419 | 7.1795 | 14.3762 | 30.644 | 9.7606 | 7.1202 | 13.9552 | 30.7694 | 9.6368 | 7.0299 | 13.4365 | 31.2215 | 9.1346 | 6.6636 | 11.7608 | 31.5262 | 8.6592 | 6.3168 | 11.076 | 31.7046 | 8.3234 | 6.0718 | 10.9797 | 31.8136 | 8.15 | 5.9453 | 11.3055 | 30.0487 | 10.0721 | 7.3475 | 16.6296 | 30.0809 | 10.3275 | 7.5337 | 16.5432 | 30.1144 | 10.3761 | 7.5693 | 16.2606 | 30.1801 | 10.2901 | 7.5065 | 15.9342 | 30.2726 | 10.1381 | 7.3956 | 15.6969 | 30.3895 | 9.8907 | 7.2151 | 15.3767 | 30.5313 | 9.681 | 7.0621 | 14.8518 | 30.6935 | 9.4582 | 6.8997 | 14.4865 | 30.8743 | 9.2366 | 6.738 | 14.165 | 31.0776 | 8.9627 | 6.5382 | 13.7813 | 31.7409 | 8.1845 | 5.9705 | 11.3553 | 32.3258 | 6.5934 | 4.8098 | 6.2022 | 32.6676 | 5.7614 | 4.2029 | 2.0606 | 31.4163 | 5.096 | 3.7175 | -0.57219 | 30.0382 | 10.0772 | 7.3512 | 16.6479 | 30.0691 | 10.3845 | 7.5753 | 16.5406 | 30.1022 | 10.4297 | 7.6083 | 16.2375 | 30.1598 | 10.3023 | 7.5154 | 15.9345 | 30.2439 | 10.1641 | 7.4146 | 15.7127 | 30.3457 | 9.8557 | 7.1896 | 15.4384 | 30.4731 | 9.614 | 7.0132 | 14.9741 | 30.6138 | 9.3759 | 6.8396 | 14.6792 | 30.7768 | 9.0929 | 6.6331 | 14.2646 | 30.9957 | 8.8032 | 6.4218 | 12.9739 | 31.7081 | 7.5658 | 5.5191 | 7.0542 | 32.1312 | 6.2264 | 4.5421 | 2.4132 | 32.2791 | 5.5182 | 4.0254 | -0.31145 | 32.2007 | 5.5824 | 4.0723 | 0.67949
RIBBLESDALE T14 | PADIHAM | PADIHAM | 374759 | 443587 | 22.1804 | 18.4384 | 13.2521 | 4.6933 | 22.3038 | 18.3331 | 13.1764 | 4.3665 | 22.3584 | 18.2284 | 13.1011 | 4.072 | 22.4452 | 18.1013 | 13.0097 | 3.7688 | 22.5583 | 17.9642 | 12.9112 | 3.4366 | 22.6985 | 17.8011 | 12.794 | 3.0587 | 22.8572 | 17.6641 | 12.6956 | 2.6383 | 23.028 | 17.5019 | 12.579 | 2.1352 | 24.8285 | 17.0664 | 12.2659 | -0.0018923 | 25.0118 | 16.8911 | 12.14 | -0.56978 | 26.9028 | 16.0085 | 11.5056 | -3.6433 | 32.2446 | 14.571 | 10.4725 | -9.3766 | 32.8545 | 13.5627 | 9.7478 | -9.8883 | 33.3001 | 13.2757 | 9.5415 | -10.0898 | 22.1038 | 18.466 | 13.2719 | 4.7666 | 22.1622 | 18.4003 | 13.2246 | 4.5075 | 22.2581 | 18.3203 | 13.1672 | 4.1826 | 22.3684 | 18.2415 | 13.1106 | 3.8875 | 22.4906 | 18.1546 | 13.0481 | 3.5728 | 22.6247 | 18.0547 | 12.9763 | 3.2098 | 22.774 | 17.9472 | 12.899 | 2.7762 | 22.9323 | 17.8238 | 12.8103 | 2.2683 | 23.1007 | 17.6821 | 12.7085 | 1.7339 | 23.2774 | 17.567 | 12.6257 | 1.1804 | 23.7992 | 17.1993 | 12.3615 | -0.28846 | 24.3013 | 16.8652 | 12.1214 | -1.3724 | 24.7344 | 16.4959 | 11.856 | -2.0814 | 25.0733 | 16.157 | 11.6124 | -2.6773 | 22.1812 | 18.4628 | 13.2696 | 4.7014 | 22.3052 | 18.386 | 13.2144 | 4.387 | 22.3604 | 18.2918 | 13.1467 | 4.1054 | 22.4479 | 18.1842 | 13.0693 | 3.8153 | 22.5613 | 18.0631 | 12.9823 | 3.4977 | 22.701 | 17.9181 | 12.8781 | 3.1354 | 22.859 | 17.7804 | 12.7791 | 2.7306 | 23.0289 | 17.6321 | 12.6725 | 2.2577 | 24.8264 | 17.4929 | 12.5725 | 0.15471 | 24.9995 | 17.3388 | 12.4618 | -0.35467 | 26.7965 | 16.747 | 12.0364 | -3.2042 | 31.9239 | 16.1587 | 11.6136 | -8.8053 | 32.4137 | 15.3078 | 11.002 | -9.258 | 32.7557 | 15.0166 | 10.7927 | -9.3517 | 22.1752 | 18.437 | 13.2511 | 4.6953 | 22.2986 | 18.3217 | 13.1681 | 4.3657 | 22.3658 | 18.203 | 13.0828 | 4.0721 | 22.4771 | 18.0678 | 12.9857 | 3.7654 | 22.6289 | 17.9151 | 12.8759 | 3.4436 | 22.8317 | 17.7487 | 12.7563 | 3.0739 | 23.082 | 17.5838 | 12.6379 | 2.651 | 23.387 | 17.424 | 12.523 | 2.2015 | 25.2886 | 16.9258 | 12.1649 | 0.21374 | 25.7429 | 16.8184 | 12.0877 | -0.32362 | 31.4212 | 15.114 | 10.8628 | -7.1442 | 33.6049 | 13.6793 | 9.8315 | -11.9893 | 34.3649 | 12.3671 | 8.8885 | -14.9344 | 34.6739 | 11.9424 | 8.5832 | -16.9507 | 22.1771 | 18.4385 | 13.2521 | 4.6941 | 22.3171 | 18.3279 | 13.1726 | 4.34 | 22.3935 | 18.2098 | 13.0877 | 4.0573 | 22.5055 | 18.0693 | 12.9868 | 3.7851 | 22.6576 | 17.9182 | 12.8782 | 3.4951 | 22.8821 | 17.7189 | 12.7349 | 3.1544 | 23.1471 | 17.5862 | 12.6396 | 2.7817 | 23.6206 | 17.3816 | 12.4925 | 2.2163 | 24.8189 | 17.0705 | 12.2689 | 0.8982 | 25.1686 | 16.8016 | 12.0756 | -0.047364 | 32.6604 | 14.2778 | 10.2617 | -10.6253 | 33.6177 | 13.0032 | 9.3456 | -14.4292 | 34.0605 | 12.0311 | 8.647 | -16.3291 | 34.0443 | 12.0907 | 8.6898 | -15.9942
RIBBLETON | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 356730 | 431506 | 29.7954 | 8.2053 | 5.9856 | 18.1201 | 29.8361 | 7.9464 | 5.7968 | 17.8016 | 29.8475 | 7.766 | 5.6652 | 17.8579 | 29.8798 | 7.4942 | 5.4669 | 17.5524 | 29.9275 | 7.2265 | 5.2716 | 17.5435 | 29.9914 | 7.0988 | 5.1785 | 17.2317 | 30.0646 | 7.0893 | 5.1715 | 17.0745 | 30.1446 | 7.0473 | 5.1409 | 16.8846 | 30.2313 | 6.9908 | 5.0997 | 16.6558 | 30.328 | 6.8891 | 5.0255 | 16.2537 | 30.9964 | 6.4879 | 4.7328 | 14.9914 | 31.9574 | 6.2874 | 4.5866 | 14.0376 | 32.6916 | 8.2843 | 6.0432 | 13.3692 | 33.5152 | 9.6353 | 7.0288 | 12.758 | 29.761 | 8.2334 | 6.0061 | 18.2184 | 29.7772 | 7.9857 | 5.8254 | 18.0411 | 29.8147 | 7.7064 | 5.6217 | 17.9693 | 29.8619 | 7.3082 | 5.3312 | 17.6953 | 29.9177 | 7.0335 | 5.1309 | 17.6733 | 29.9832 | 6.6898 | 4.8801 | 17.3687 | 30.0577 | 6.671 | 4.8664 | 17.1596 | 30.1383 | 6.6296 | 4.8362 | 16.9143 | 30.2255 | 6.6024 | 4.8164 | 16.6953 | 30.3177 | 6.5422 | 4.7725 | 16.321 | 30.724 | 6.3925 | 4.6633 | 15.4103 | 31.2183 | 6.2594 | 4.5662 | 14.7363 | 31.7845 | 7.5635 | 5.5175 | 14.1074 | 32.3055 | 9.4251 | 6.8755 | 13.737 | 29.7957 | 8.2315 | 6.0048 | 18.1302 | 29.8371 | 7.9742 | 5.8171 | 17.8238 | 29.8495 | 7.6491 | 5.5799 | 17.8884 | 29.8829 | 7.2812 | 5.3116 | 17.5937 | 29.932 | 6.8655 | 5.0083 | 17.5931 | 29.997 | 6.7753 | 4.9425 | 17.2939 | 30.0713 | 6.7259 | 4.9064 | 17.1506 | 30.1524 | 6.6603 | 4.8586 | 16.9545 | 30.2393 | 6.5907 | 4.8078 | 16.7462 | 30.333 | 6.5191 | 4.7556 | 16.3657 | 30.8865 | 6.2575 | 4.5648 | 15.264 | 31.4733 | 6.1726 | 4.5028 | 14.6215 | 32.0663 | 8.1931 | 5.9768 | 14.1735 | 32.5605 | 9.7584 | 7.1186 | 13.8632 | 29.7926 | 8.2049 | 5.9853 | 18.1278 | 29.8335 | 7.9478 | 5.7978 | 17.8142 | 29.8521 | 7.7452 | 5.65 | 17.8683 | 29.898 | 7.4453 | 5.4312 | 17.5517 | 29.9655 | 7.1578 | 5.2215 | 17.5326 | 30.0725 | 7.1034 | 5.1818 | 17.1887 | 30.2136 | 7.0647 | 5.1536 | 16.9802 | 30.3838 | 6.9949 | 5.1027 | 16.7208 | 30.5769 | 6.9031 | 5.0357 | 16.4067 | 30.7956 | 6.7946 | 4.9566 | 16.0447 | 32.1698 | 6.1806 | 4.5087 | 14.018 | 33.3158 | 5.4042 | 3.9423 | 10.1567 | 34.7129 | 6.8419 | 4.991 | 6.8247 | 35.181 | 7.89 | 5.7557 | 4.626 | 29.7904 | 8.2073 | 5.9871 | 18.1345 | 29.8376 | 8.1192 | 5.9229 | 17.8125 | 29.8618 | 8.089 | 5.9008 | 17.8656 | 29.9118 | 7.9789 | 5.8205 | 17.5598 | 29.9861 | 7.889 | 5.7549 | 17.5526 | 30.1152 | 7.6255 | 5.5627 | 17.2161 | 30.2979 | 7.6904 | 5.6101 | 17.0011 | 30.5225 | 7.649 | 5.5798 | 16.7839 | 30.7902 | 7.574 | 5.5252 | 16.3306 | 31.0891 | 7.3999 | 5.3981 | 15.5116 | 32.6633 | 6.5166 | 4.7538 | 11.2503 | 34.041 | 5.9054 | 4.3079 | 7.6774 | 34.6625 | 8.1617 | 5.9539 | 5.2775 | 34.7474 | 8.0712 | 5.8878 | 5.4873
RINGLEY | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 23.3475 | 12.7001 | 9.1278 | 19.2761 | 23.3592 | 12.411 | 8.92 | 19.2126 | 23.3614 | 12.0764 | 8.6795 | 19.1263 | 23.3801 | 11.8117 | 8.4893 | 19.0011 | 23.4076 | 11.4983 | 8.2641 | 18.8893 | 23.4428 | 11.2088 | 8.056 | 18.7304 | 23.4836 | 11.1421 | 8.008 | 18.5376 | 23.5286 | 11.0882 | 7.9693 | 18.3709 | 23.5776 | 11.0125 | 7.9149 | 18.1934 | 23.6334 | 10.9402 | 7.863 | 17.9808 | 23.9184 | 10.6564 | 7.659 | 17.2039 | 24.2493 | 10.4067 | 7.4795 | 16.7348 | 24.506 | 10.256 | 7.3712 | 16.5493 | 24.7672 | 10.0906 | 7.2523 | 16.518 | 23.338 | 12.737 | 9.1544 | 19.3487 | 23.344 | 12.7086 | 9.1339 | 19.3431 | 23.3602 | 12.651 | 9.0926 | 19.2277 | 23.3862 | 12.5829 | 9.0435 | 19.1005 | 23.4176 | 12.5269 | 9.0034 | 19.0019 | 23.454 | 12.4477 | 8.9464 | 18.8613 | 23.4956 | 12.4126 | 8.9212 | 18.6862 | 23.5409 | 12.3819 | 8.8991 | 18.5364 | 23.5898 | 12.3432 | 8.8713 | 18.3716 | 23.6419 | 12.301 | 8.8409 | 18.1946 | 23.801 | 12.1322 | 8.7196 | 17.6484 | 23.9746 | 12.0043 | 8.6277 | 17.2525 | 24.1531 | 11.8908 | 8.5461 | 16.9836 | 24.3107 | 11.8956 | 8.5496 | 16.8301 | 23.3476 | 12.7383 | 9.1553 | 19.2806 | 23.3594 | 12.4609 | 8.9559 | 19.2235 | 23.3619 | 12.1472 | 8.7305 | 19.1441 | 23.3809 | 11.8512 | 8.5177 | 19.0232 | 23.4087 | 11.5209 | 8.2803 | 18.9165 | 23.4441 | 11.216 | 8.0612 | 18.7632 | 23.4851 | 11.1708 | 8.0287 | 18.576 | 23.5303 | 11.1194 | 7.9917 | 18.4143 | 23.579 | 11.0583 | 7.9478 | 18.245 | 23.6325 | 10.9849 | 7.8951 | 18.052 | 23.8805 | 10.7644 | 7.7366 | 17.362 | 24.107 | 10.5937 | 7.6139 | 17.0058 | 24.3113 | 10.5333 | 7.5705 | 16.8686 | 24.4776 | 10.3698 | 7.453 | 16.9028 | 23.3457 | 12.6997 | 9.1275 | 19.2828 | 23.3565 | 12.4016 | 8.9133 | 19.2277 | 23.3606 | 12.1017 | 8.6977 | 19.1528 | 23.3855 | 11.8102 | 8.4882 | 19.0385 | 23.4231 | 11.5015 | 8.2663 | 18.9437 | 23.4773 | 11.1939 | 8.0453 | 18.8006 | 23.5473 | 11.134 | 8.0022 | 18.6169 | 23.6304 | 11.0481 | 7.9405 | 18.4581 | 23.7225 | 10.9891 | 7.8981 | 18.3119 | 23.8271 | 10.9061 | 7.8384 | 18.1522 | 24.4112 | 10.3816 | 7.4614 | 17.0365 | 24.989 | 9.8458 | 7.0764 | 14.7769 | 25.3246 | 9.2643 | 6.6585 | 13.0312 | 25.4755 | 8.9443 | 6.4285 | 11.5583 | 23.3403 | 12.6694 | 9.1058 | 19.2968 | 23.3495 | 12.3392 | 8.8684 | 19.2349 | 23.3546 | 12.0685 | 8.6739 | 19.1535 | 23.3781 | 11.7394 | 8.4374 | 19.0501 | 23.4151 | 11.3789 | 8.1782 | 18.9672 | 23.4713 | 11.0641 | 7.952 | 18.8439 | 23.5482 | 10.9219 | 7.8498 | 18.6769 | 23.6401 | 10.9279 | 7.8541 | 18.538 | 23.7543 | 10.8717 | 7.8137 | 18.352 | 23.933 | 10.7149 | 7.701 | 17.834 | 24.5605 | 10.0148 | 7.1978 | 15.3467 | 25.0358 | 9.3687 | 6.7335 | 13.3167 | 25.2208 | 8.9261 | 6.4153 | 11.8601 | 25.2015 | 8.881 | 6.383 | 12.0821
RISLEY | - | BOLD | 365181 | 392989 | 7.3719 | 1.2137 | 0.87233 | 7.3719 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.3413 | 1.3733 | 0.98704 | 8.3413 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.319 | 1.3697 | 0.9844 | 8.319 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 7.368 | 1.2131 | 0.87186 | 7.368 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.1616 | 2.6844 | 0.44197 | 0.31765 | -2.8723 | 2.6844 | 0.44197 | 0.31765 | -5.6654 | 7.3339 | 1.2075 | 0.86783 | 7.3339 | 5.7627 | 0.94879 | 0.68191 | 5.7627 | 4.4832 | 0.73813 | 0.53051 | 4.4832 | 3.1129 | 0.51252 | 0.36836 | 3.1129 | 1.7766 | 0.29251 | 0.21023 | 1.7766 | 0.30677 | 0.050507 | 0.0363 | 0.30677 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5718 | 2.6844 | 0.44197 | 0.31765 | -2.0398 | 2.6844 | 0.44197 | 0.31765 | -4.7756 | 2.6844 | 0.44197 | 0.31765 | -4.454
ROBERT HALL ST | FREDERICK RD | KEARSLEY | 381359 | 397718 | 31.3138 | 8.9236 | 6.5097 | 14.1816 | 31.4029 | 8.7333 | 6.3708 | 13.2153 | 31.4211 | 8.6498 | 6.3099 | 13.0453 | 31.4752 | 8.5643 | 6.2475 | 12.7932 | 31.542 | 8.4943 | 6.1964 | 12.6712 | 31.6243 | 8.3652 | 6.1023 | 12.2268 | 31.7071 | 8.3076 | 6.0603 | 12.0332 | 31.789 | 8.2048 | 5.9853 | 11.6863 | 31.8746 | 8.1032 | 5.9112 | 11.4246 | 31.9724 | 7.9461 | 5.7966 | 10.9403 | 32.3045 | 7.4974 | 5.4692 | 9.5327 | 32.5517 | 7.4197 | 5.4126 | 8.4791 | 32.707 | 7.4781 | 5.4552 | 7.7614 | 32.7898 | 7.4005 | 5.3986 | 7.5366 | 31.2566 | 8.9754 | 6.5474 | 14.6195 | 31.3002 | 8.8585 | 6.4621 | 14.1463 | 31.3684 | 8.7937 | 6.4149 | 13.9715 | 31.4645 | 8.6984 | 6.3454 | 13.6165 | 31.5669 | 8.6337 | 6.2982 | 13.4861 | 31.6769 | 8.526 | 6.2196 | 13.0543 | 31.7947 | 8.4525 | 6.166 | 12.7685 | 31.9182 | 8.3631 | 6.1007 | 12.3829 | 32.0485 | 8.2902 | 6.0476 | 12.0784 | 32.1853 | 8.1918 | 5.9758 | 11.6121 | 32.4465 | 7.9518 | 5.8007 | 10.6508 | 32.6833 | 7.6913 | 5.6107 | 9.6024 | 32.8258 | 7.7929 | 5.6848 | 8.6206 | 32.9152 | 7.817 | 5.7024 | 7.9347 | 31.3138 | 8.9746 | 6.5468 | 14.2303 | 31.4029 | 8.8591 | 6.4626 | 13.1816 | 31.4211 | 8.7801 | 6.405 | 13.0242 | 31.4752 | 8.6595 | 6.317 | 12.8051 | 31.5419 | 8.5756 | 6.2558 | 12.6707 | 31.6239 | 8.4468 | 6.1618 | 12.2384 | 31.7066 | 8.3425 | 6.0857 | 12.0506 | 31.7884 | 8.2206 | 5.9968 | 11.713 | 31.8734 | 8.1129 | 5.9182 | 11.4702 | 31.9689 | 7.9656 | 5.8108 | 11.0312 | 32.2886 | 7.6094 | 5.551 | 9.7443 | 32.5258 | 7.6377 | 5.5716 | 8.8053 | 32.6757 | 7.7619 | 5.6622 | 8.156 | 32.7566 | 7.6682 | 5.5939 | 7.9307 | 31.3072 | 8.9268 | 6.512 | 14.1928 | 31.3902 | 8.7473 | 6.381 | 13.2412 | 31.4019 | 8.6592 | 6.3168 | 13.0775 | 31.4558 | 8.5681 | 6.2503 | 12.8281 | 31.5264 | 8.483 | 6.1883 | 12.6897 | 31.6174 | 8.3401 | 6.084 | 12.2128 | 31.7179 | 8.259 | 6.0249 | 11.9289 | 31.8239 | 8.1253 | 5.9273 | 11.4805 | 31.9346 | 7.9958 | 5.8328 | 11.14 | 32.0516 | 7.8225 | 5.7064 | 10.6858 | 32.3923 | 7.3058 | 5.3295 | 8.8733 | 32.6797 | 6.7332 | 4.9118 | 5.7124 | 32.798 | 6.3024 | 4.5975 | 3.2003 | 32.8414 | 5.8842 | 4.2924 | 1.278 | 31.2961 | 8.9313 | 6.5153 | 14.2109 | 31.371 | 8.7906 | 6.4126 | 13.24 | 31.3755 | 8.7188 | 6.3603 | 13.0656 | 31.414 | 8.604 | 6.2765 | 12.8289 | 31.4708 | 8.4723 | 6.1804 | 12.6434 | 31.5447 | 8.2533 | 6.0206 | 12.1511 | 31.6263 | 8.0692 | 5.8864 | 11.8753 | 31.7103 | 7.8894 | 5.7552 | 11.4565 | 31.7987 | 7.9087 | 5.7693 | 11.1231 | 31.9059 | 7.7756 | 5.6722 | 10.2379 | 32.2592 | 7.3398 | 5.3543 | 6.6661 | 32.4754 | 6.421 | 4.6841 | 3.7787 | 32.513 | 5.9976 | 4.3752 | 1.9157 | 32.4385 | 5.8769 | 4.2871 | 2.0252
ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 1.8058 | 0.29291 | 0.21368 | 1.8058 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.4486 | 0.39718 | 0.28974 | 2.4486 | 0.76831 | 0.12463 | 0.090914 | 0.76831 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.4319 | 0.39447 | 0.28776 | 2.4319 | 0.51645 | 0.083774 | 0.061112 | 0.51645 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 1.8212 | 0.29541 | 0.2155 | 1.8212 | 0.16903 | 0.027418 | 0.020001 | 0.16903 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 1.8694 | 0.30324 | 0.22121 | 1.8694 | 1.3482 | 0.21868 | 0.15953 | 1.3482 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
ROMAN RD | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 32.8033 | 16.5779 | 12.0934 | 13.0379 | 32.9176 | 15.7469 | 11.4872 | 12.2204 | 32.9056 | 14.9043 | 10.8725 | 12.2407 | 32.9296 | 14.5716 | 10.6298 | 11.9866 | 32.9786 | 14.0649 | 10.2601 | 11.9239 | 33.051 | 13.5271 | 9.8678 | 11.7738 | 33.1295 | 13.3717 | 9.7545 | 11.601 | 33.2101 | 13.3163 | 9.7141 | 11.616 | 33.2943 | 13.2695 | 9.6799 | 11.3915 | 33.3912 | 13.1862 | 9.6192 | 11.1462 | 33.9763 | 13.0214 | 9.499 | 10.5953 | 34.6685 | 13.8982 | 10.1386 | 10.1416 | 35.0823 | 15.7273 | 11.4728 | 9.7469 | 35.4905 | 15.8646 | 11.573 | 9.6527 | 32.6588 | 16.6936 | 12.1778 | 13.6032 | 32.6547 | 16.0134 | 11.6815 | 13.3042 | 32.6923 | 15.4811 | 11.2933 | 13.2585 | 32.7411 | 14.845 | 10.8292 | 12.9244 | 32.8016 | 14.2449 | 10.3915 | 12.8233 | 32.8673 | 13.6344 | 9.9461 | 12.6705 | 32.9403 | 13.5964 | 9.9184 | 12.4844 | 33.0151 | 13.5866 | 9.9113 | 12.4597 | 33.0927 | 13.5464 | 9.8819 | 12.22 | 33.171 | 13.4904 | 9.841 | 11.9615 | 33.5431 | 13.4485 | 9.8105 | 11.566 | 33.9381 | 14.0453 | 10.2458 | 11.2368 | 34.2757 | 15.4563 | 11.2752 | 10.8794 | 34.5221 | 15.9869 | 11.6622 | 10.9003 | 32.8045 | 16.6915 | 12.1762 | 13.0541 | 32.9194 | 16.0549 | 11.7119 | 12.2254 | 32.9081 | 15.459 | 11.2771 | 12.2475 | 32.9328 | 14.8377 | 10.8239 | 12.0237 | 32.9824 | 14.263 | 10.4046 | 11.9368 | 33.0547 | 13.6663 | 9.9694 | 11.7901 | 33.1326 | 13.5948 | 9.9172 | 11.6209 | 33.2122 | 13.563 | 9.894 | 11.6509 | 33.2941 | 13.4803 | 9.8337 | 11.4198 | 33.3858 | 13.3869 | 9.7655 | 11.1876 | 33.8949 | 13.299 | 9.7014 | 10.7484 | 34.3745 | 14.1408 | 10.3155 | 10.4582 | 34.6592 | 16.3892 | 11.9557 | 10.1794 | 34.8654 | 16.5961 | 12.1066 | 10.232 | 32.7957 | 16.5803 | 12.0951 | 13.0627 | 32.9052 | 15.7621 | 11.4982 | 12.2732 | 32.896 | 14.8237 | 10.8137 | 12.3165 | 32.9297 | 14.5263 | 10.5967 | 12.0721 | 32.9952 | 14.07 | 10.2638 | 12.0442 | 33.1038 | 13.4788 | 9.8326 | 11.9082 | 33.2405 | 13.3489 | 9.7378 | 11.7405 | 33.3978 | 13.2909 | 9.6955 | 11.7021 | 33.564 | 13.1996 | 9.6289 | 11.526 | 33.7486 | 13.0722 | 9.536 | 11.2863 | 34.6541 | 12.7988 | 9.3365 | 10.1331 | 35.5754 | 12.9349 | 9.4359 | 7.6074 | 36.1334 | 14.3892 | 10.4967 | 5.4157 | 36.3011 | 14.3545 | 10.4714 | 4.2282 | 32.7988 | 16.582 | 12.0963 | 13.0525 | 32.9128 | 16.3663 | 11.939 | 12.2494 | 32.9075 | 16.3901 | 11.9563 | 12.2939 | 32.9446 | 16.317 | 11.903 | 12.0613 | 33.0136 | 16.3282 | 11.9112 | 12.0415 | 33.1352 | 16.246 | 11.8512 | 11.9151 | 33.2987 | 16.1504 | 11.7815 | 11.7453 | 33.4894 | 16.1361 | 11.7711 | 11.7155 | 33.7239 | 16.0582 | 11.7142 | 11.4973 | 34.0374 | 15.8607 | 11.5702 | 10.8995 | 34.9608 | 16.1115 | 11.7531 | 8.1332 | 35.7547 | 15.1989 | 11.0874 | 5.7683 | 36.0718 | 14.7291 | 10.7447 | 4.3281 | 36.004 | 14.6762 | 10.7061 | 4.9169
ROMILEY | VERNON PARK | BREDBURY | 393626 | 390716 | 22.2037 | 11.1311 | 8.0002 | 6.2808 | 22.2469 | 11.0711 | 7.957 | 6.0641 | 22.2774 | 10.924 | 7.8513 | 5.791 | 22.3388 | 10.7518 | 7.7275 | 5.3914 | 22.4215 | 10.5492 | 7.5819 | 5.1631 | 22.5221 | 10.3442 | 7.4346 | 4.7704 | 22.6376 | 10.1531 | 7.2973 | 4.0278 | 22.7639 | 9.9833 | 7.1752 | 3.7113 | 22.9006 | 9.7611 | 7.0155 | 3.3449 | 23.0528 | 9.6619 | 6.9442 | 2.6918 | 27.0499 | 8.4272 | 6.0568 | -2.5478 | 27.5052 | 7.9406 | 5.7071 | -3.3929 | 29.0569 | 8.3843 | 6.0259 | -4.977 | 29.1821 | 9.2049 | 6.6157 | -4.453 | 22.1871 | 11.1494 | 8.0133 | 6.4168 | 22.2201 | 11.1005 | 7.9782 | 6.3122 | 22.2773 | 10.9452 | 7.8665 | 5.948 | 22.3524 | 10.804 | 7.7651 | 5.5833 | 22.4392 | 10.6943 | 7.6862 | 5.3609 | 22.5373 | 10.564 | 7.5926 | 5.0399 | 22.6478 | 10.3971 | 7.4726 | 4.3171 | 22.7674 | 10.313 | 7.4122 | 4.0216 | 22.8971 | 10.2231 | 7.3476 | 3.7336 | 23.0352 | 10.0579 | 7.2288 | 3.1452 | 23.3225 | 9.7424 | 7.0021 | 1.8449 | 23.57 | 9.47 | 6.8063 | 0.85966 | 23.7743 | 10.0414 | 7.217 | 0.12282 | 23.9322 | 10.662 | 7.663 | -0.15481 | 22.2037 | 11.1456 | 8.0106 | 6.2907 | 22.2471 | 11.0799 | 7.9633 | 6.1026 | 22.2777 | 10.9132 | 7.8435 | 5.8364 | 22.3393 | 10.7644 | 7.7366 | 5.4726 | 22.4219 | 10.6323 | 7.6417 | 5.2371 | 22.5221 | 10.4424 | 7.5052 | 4.887 | 22.6373 | 10.2949 | 7.3991 | 4.147 | 22.7633 | 10.1813 | 7.3175 | 3.834 | 22.8983 | 10.0655 | 7.2343 | 3.522 | 23.0429 | 9.8971 | 7.1132 | 2.9074 | 26.9876 | 9.3791 | 6.741 | -2.1499 | 27.3526 | 8.9986 | 6.4674 | -2.8473 | 28.8579 | 9.6849 | 6.9608 | -4.3443 | 28.9191 | 10.3121 | 7.4115 | -3.8285 | 22.2007 | 11.1333 | 8.0017 | 6.2958 | 22.2443 | 11.0702 | 7.9564 | 6.0944 | 22.2842 | 10.8845 | 7.8229 | 5.8432 | 22.3657 | 10.73 | 7.7119 | 5.475 | 22.4804 | 10.5063 | 7.5511 | 5.2803 | 22.629 | 10.3066 | 7.4075 | 4.9411 | 22.812 | 10.0669 | 7.2353 | 4.1943 | 24.895 | 9.4958 | 6.8248 | 1.9723 | 25.0136 | 9.4617 | 6.8003 | 1.8556 | 25.16 | 9.3128 | 6.6933 | 1.4507 | 29.2216 | 7.7395 | 5.5626 | -4.3135 | 30.0567 | 5.9763 | 4.2953 | -10.2871 | 30.1005 | 5.8068 | 4.1734 | -14.791 | 30.269 | 5.8924 | 4.235 | -17.8212 | 22.1942 | 11.1358 | 8.0036 | 6.2996 | 22.2423 | 11.1058 | 7.982 | 6.0416 | 22.2851 | 10.9593 | 7.8767 | 5.8107 | 22.3617 | 10.8057 | 7.7662 | 5.4369 | 22.4712 | 10.6151 | 7.6293 | 5.2913 | 27.0662 | 9.5128 | 6.8371 | 0.38334 | 26.9495 | 9.4791 | 6.8128 | -0.035417 | 26.8819 | 9.4318 | 6.7788 | 0.11375 | 26.8677 | 9.3222 | 6.7001 | -0.02073 | 26.9232 | 8.9791 | 6.4535 | -1.3383 | 28.1202 | 7.1709 | 5.1539 | -8.2617 | 28.6688 | 5.7683 | 4.1458 | -13.5555 | 28.5677 | 6.6871 | 4.8062 | -16.5601 | 28.3249 | 6.6649 | 4.7902 | -15.249
ROSSALL | THORNTON | PENWORTHAM WEST / STANAH | 331916 | 445505 | -4.6367 | -4.6367 | -4.6367 | -4.6367 | -4.6167 | -4.6167 | -4.6167 | -4.6167 | -4.5888 | -4.5888 | -4.5888 | -4.5888 | -4.5571 | -4.5571 | -4.5571 | -4.5571 | -4.5211 | -4.5211 | -4.5211 | -4.5211 | -4.4804 | -4.4804 | -4.4804 | -4.4804 | -4.4352 | -4.4352 | -4.4352 | -4.4352 | -4.388 | -4.388 | -4.388 | -4.388 | -4.34 | -4.34 | -4.34 | -4.34 | -4.2888 | -4.2888 | -4.2888 | -4.2888 | -4.0822 | -4.0822 | -4.0822 | -4.0822 | -3.9243 | -3.9243 | -3.9243 | -3.9243 | -3.8291 | -3.8291 | -3.8291 | -3.8291 | -3.7454 | -3.7454 | -3.7454 | -3.7454 | -4.6326 | -4.6326 | -4.6326 | -4.6326 | -4.6105 | -4.6105 | -4.6105 | -4.6105 | -4.5801 | -4.5801 | -4.5801 | -4.5801 | -4.5502 | -4.5502 | -4.5502 | -4.5502 | -4.5183 | -4.5183 | -4.5183 | -4.5183 | -4.4815 | -4.4815 | -4.4815 | -4.4815 | -4.4405 | -4.4405 | -4.4405 | -4.4405 | -4.397 | -4.397 | -4.397 | -4.397 | -4.3515 | -4.3515 | -4.3515 | -4.3515 | -4.3042 | -4.3042 | -4.3042 | -4.3042 | -4.1752 | -4.1752 | -4.1752 | -4.1752 | -4.0765 | -4.0765 | -4.0765 | -4.0765 | -3.9957 | -3.9957 | -3.9957 | -3.9957 | -3.9294 | -3.9294 | -3.9294 | -3.9294 | -4.6367 | -4.6367 | -4.6367 | -4.6367 | -4.6166 | -4.6166 | -4.6166 | -4.6166 | -4.5886 | -4.5886 | -4.5886 | -4.5886 | -4.5568 | -4.5568 | -4.5568 | -4.5568 | -4.5209 | -4.5209 | -4.5209 | -4.5209 | -4.4803 | -4.4803 | -4.4803 | -4.4803 | -4.4353 | -4.4353 | -4.4353 | -4.4353 | -4.3881 | -4.3881 | -4.3881 | -4.3881 | -4.3407 | -4.3407 | -4.3407 | -4.3407 | -4.2924 | -4.2924 | -4.2924 | -4.2924 | -4.1059 | -4.1059 | -4.1059 | -4.1059 | -3.9864 | -3.9864 | -3.9864 | -3.9864 | -3.9087 | -3.9087 | -3.9087 | -3.9087 | -3.8546 | -3.8546 | -3.8546 | -3.8546 | -4.6346 | -4.6346 | -4.6346 | -4.6346 | -4.6125 | -4.6125 | -4.6125 | -4.6125 | -4.5827 | -4.5827 | -4.5827 | -4.5827 | -4.5495 | -4.5495 | -4.5495 | -4.5495 | -4.5117 | -4.5117 | -4.5117 | -4.5117 | -4.4687 | -4.4687 | -4.4687 | -4.4687 | -4.4204 | -4.4204 | -4.4204 | -4.4204 | -4.3695 | -4.3695 | -4.3695 | -4.3695 | -4.3176 | -4.3176 | -4.3176 | -4.3176 | -4.2651 | -4.2651 | -4.2651 | -4.2651 | -3.9719 | -3.9719 | -3.9719 | -3.9719 | -3.6233 | -3.6233 | -3.6233 | -3.6233 | -3.4363 | -3.4363 | -3.4363 | -3.4363 | -3.3321 | -3.3321 | -3.3321 | -3.3321 | -4.6329 | -4.6329 | -4.6329 | -4.6329 | -4.6054 | -4.6054 | -4.6054 | -4.6054 | -4.5745 | -4.5745 | -4.5745 | -4.5745 | -4.544 | -4.544 | -4.544 | -4.544 | -4.5096 | -4.5096 | -4.5096 | -4.5096 | -4.4706 | -4.4706 | -4.4706 | -4.4706 | -4.4238 | -4.4238 | -4.4238 | -4.4238 | -4.375 | -4.375 | -4.375 | -4.375 | -4.3239 | -4.3239 | -4.3239 | -4.3239 | -4.2296 | -4.2296 | -4.2296 | -4.2296 | -3.8463 | -3.8463 | -3.8463 | -3.8463 | -3.6057 | -3.6057 | -3.6057 | -3.6057 | -3.4915 | -3.4915 | -3.4915 | -3.4915 | -3.5004 | -3.5004 | -3.5004 | -3.5004
ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 30.1297 | 12.7491 | 9.3003 | 15.8101 | 30.1832 | 12.4112 | 9.0538 | 15.4439 | 30.2096 | 12.1414 | 8.857 | 15.2033 | 30.2617 | 11.9053 | 8.6847 | 14.9149 | 30.3332 | 11.6194 | 8.4762 | 14.6622 | 30.4206 | 11.379 | 8.3008 | 14.3138 | 30.5177 | 11.3111 | 8.2513 | 13.9879 | 30.6229 | 11.2176 | 8.1831 | 13.6031 | 30.735 | 11.0964 | 8.0947 | 13.1907 | 30.8594 | 10.9672 | 8.0005 | 12.7442 | 31.4055 | 10.558 | 7.7019 | 11.197 | 31.877 | 10.4845 | 7.6483 | 10.3394 | 32.1945 | 11.5076 | 8.3946 | 10.0841 | 32.4318 | 11.3556 | 8.2838 | 10.1344 | 30.0975 | 12.8015 | 9.3385 | 15.9377 | 30.1255 | 12.5352 | 9.1442 | 15.6889 | 30.1792 | 12.1666 | 8.8754 | 15.423 | 30.2435 | 11.9115 | 8.6893 | 15.143 | 30.3184 | 11.7253 | 8.5534 | 14.918 | 30.4016 | 11.4795 | 8.3741 | 14.5985 | 30.4937 | 11.4105 | 8.3238 | 14.2957 | 30.5924 | 11.3278 | 8.2635 | 13.9338 | 30.6973 | 11.2366 | 8.1969 | 13.5346 | 30.8073 | 11.1519 | 8.1351 | 13.1486 | 31.1067 | 10.9177 | 7.9643 | 12.0327 | 31.3672 | 10.8901 | 7.9441 | 11.246 | 31.5563 | 11.507 | 8.3942 | 10.7713 | 31.693 | 12.1037 | 8.8295 | 10.4453 | 30.1305 | 12.8028 | 9.3395 | 15.8194 | 30.1843 | 12.4856 | 9.1081 | 15.4663 | 30.2106 | 12.1535 | 8.8658 | 15.239 | 30.2629 | 11.9055 | 8.6849 | 14.962 | 30.3343 | 11.6198 | 8.4765 | 14.7214 | 30.421 | 11.3199 | 8.2577 | 14.3865 | 30.5173 | 11.2383 | 8.1982 | 14.073 | 30.6215 | 11.1466 | 8.1313 | 13.7012 | 30.7314 | 11.0453 | 8.0574 | 13.3078 | 30.8491 | 10.9474 | 7.986 | 12.9034 | 31.3542 | 10.6309 | 7.7551 | 11.5145 | 31.7484 | 10.7372 | 7.8326 | 10.7927 | 32.0131 | 12.1076 | 8.8323 | 10.5635 | 32.1961 | 12.0478 | 8.7887 | 10.5935 | 30.1267 | 12.7481 | 9.2996 | 15.8143 | 30.179 | 12.4118 | 9.0542 | 15.451 | 30.2115 | 12.1349 | 8.8522 | 15.217 | 30.278 | 11.8826 | 8.6682 | 14.9346 | 30.3728 | 11.5647 | 8.4363 | 14.7002 | 30.4963 | 11.3642 | 8.29 | 14.3673 | 30.6445 | 11.2847 | 8.232 | 14.0446 | 30.814 | 11.166 | 8.1454 | 13.6611 | 30.9983 | 11.034 | 8.0492 | 13.3019 | 31.2027 | 10.911 | 7.9594 | 12.9578 | 32.0882 | 10.2456 | 7.474 | 10.6729 | 32.8832 | 9.2912 | 6.7778 | 5.4783 | 33.3171 | 9.5089 | 6.9366 | 1.2862 | 33.5472 | 8.8722 | 6.4722 | -1.6273 | 30.1173 | 12.7553 | 9.3048 | 15.8467 | 30.1694 | 12.6211 | 9.2069 | 15.4835 | 30.2018 | 12.531 | 9.1412 | 15.2541 | 30.2635 | 12.3954 | 9.0423 | 15.0079 | 30.3529 | 12.3662 | 9.021 | 14.8147 | 30.4684 | 12.2555 | 8.9402 | 14.5416 | 30.6124 | 12.137 | 8.8538 | 14.2751 | 30.7744 | 12.0395 | 8.7826 | 13.9587 | 30.9687 | 11.9237 | 8.6982 | 13.5125 | 31.2679 | 11.6729 | 8.5152 | 12.2779 | 32.1703 | 11.1824 | 8.1574 | 6.5397 | 32.7432 | 10.0036 | 7.2975 | 1.8195 | 32.9778 | 9.2814 | 6.7707 | -0.99069 | 32.9346 | 9.1981 | 6.7099 | -0.33969
SALE | SALE | CARRINGTON | 378952 | 392177 | 30.9771 | 8.6274 | 6.2936 | 16.081 | 31.0615 | 8.4555 | 6.1682 | 15.4247 | 31.1232 | 8.3247 | 6.0728 | 15.1291 | 31.2202 | 8.195 | 5.9781 | 15.0939 | 31.3416 | 8.0227 | 5.8525 | 14.9134 | 31.4846 | 7.7513 | 5.6545 | 14.2967 | 31.6438 | 7.6475 | 5.5787 | 13.9266 | 31.8047 | 7.6609 | 5.5885 | 13.7985 | 31.9696 | 7.5318 | 5.4944 | 13.0141 | 32.1486 | 7.4355 | 5.4241 | 12.5924 | 32.7291 | 6.9701 | 5.0846 | 11.2471 | 33.1364 | 6.6224 | 4.831 | 10.4889 | 33.3895 | 6.7214 | 4.9031 | 10.3181 | 33.5536 | 6.8302 | 4.9825 | 10.4224 | 30.9647 | 8.7461 | 6.3801 | 16.2156 | 31.0465 | 8.6378 | 6.3012 | 15.6445 | 31.1321 | 8.5321 | 6.2241 | 15.2929 | 31.2285 | 8.4645 | 6.1747 | 15.2374 | 31.3361 | 8.3727 | 6.1077 | 15.0571 | 31.4555 | 8.2058 | 5.986 | 14.4422 | 31.5869 | 8.0978 | 5.9072 | 14.0315 | 31.7275 | 8.0669 | 5.8847 | 13.8848 | 31.8779 | 7.921 | 5.7783 | 13.0522 | 32.0363 | 7.8355 | 5.7159 | 12.633 | 32.3445 | 7.6515 | 5.5817 | 11.8066 | 32.5887 | 7.4775 | 5.4548 | 11.0024 | 32.7637 | 7.513 | 5.4806 | 10.3833 | 32.8763 | 7.5681 | 5.5208 | 10.0496 | 30.9771 | 8.7471 | 6.3809 | 16.0903 | 31.0615 | 8.643 | 6.3049 | 15.4681 | 31.1233 | 8.5019 | 6.202 | 15.2022 | 31.2204 | 8.4303 | 6.1498 | 15.1818 | 31.3413 | 8.3424 | 6.0856 | 15.02 | 31.4836 | 8.1734 | 5.9624 | 14.4315 | 31.6421 | 8.0728 | 5.889 | 14.0761 | 31.8025 | 8.0095 | 5.8428 | 13.9667 | 31.9651 | 7.827 | 5.7097 | 13.2187 | 32.1342 | 7.7166 | 5.6291 | 12.8499 | 32.6814 | 7.3474 | 5.3598 | 11.6461 | 33.0422 | 7.1221 | 5.1955 | 10.9792 | 33.2709 | 7.1663 | 5.2277 | 10.8587 | 33.411 | 7.1762 | 5.2349 | 10.9669 | 30.9742 | 8.6266 | 6.2929 | 16.0892 | 31.0615 | 8.447 | 6.162 | 15.4396 | 31.1397 | 8.2993 | 6.0542 | 15.1571 | 31.2672 | 8.1661 | 5.9571 | 15.1325 | 31.4353 | 8.0047 | 5.8393 | 14.9618 | 31.6392 | 7.7362 | 5.6435 | 14.3467 | 31.85 | 7.6677 | 5.5935 | 13.9746 | 32.0868 | 7.6644 | 5.5911 | 13.8169 | 32.3411 | 7.5349 | 5.4966 | 13.0559 | 32.5681 | 7.4538 | 5.4374 | 12.7134 | 33.3561 | 6.8669 | 5.0093 | 11.0556 | 34.0308 | 5.9276 | 4.3241 | 7.2455 | 33.3543 | 5.4104 | 3.9468 | 4.2291 | 31.2802 | 5.074 | 3.7014 | 2.2983 | 30.9711 | 8.6239 | 6.291 | 16.0674 | 31.0675 | 8.4334 | 6.152 | 15.3799 | 31.1406 | 8.26 | 6.0255 | 15.1135 | 31.2513 | 8.0484 | 5.8712 | 15.1324 | 31.4001 | 8.0341 | 5.8608 | 14.9979 | 31.5572 | 7.9703 | 5.8142 | 14.4424 | 31.7406 | 7.887 | 5.7535 | 14.1356 | 31.9397 | 7.8337 | 5.7146 | 14.0536 | 32.159 | 7.6524 | 5.5823 | 13.3098 | 32.4212 | 7.3869 | 5.3886 | 12.3148 | 33.2225 | 6.0824 | 4.437 | 8.0523 | 31.1572 | 5.054 | 3.6868 | 4.6265 | 29.5667 | 4.796 | 3.4986 | 2.5682 | 29.7181 | 4.8206 | 3.5165 | 3.3271
SALE MOOR | SALE | CARRINGTON | 379671 | 391133 | 11.8202 | 11.8202 | 11.8202 | 1.7748 | 11.8527 | 11.8527 | 11.8527 | 1.6535 | 11.8886 | 11.8886 | 11.8886 | 1.4396 | 11.9469 | 11.9469 | 11.9469 | 1.1506 | 12.0224 | 12.0224 | 12.0224 | 1.0819 | 12.1121 | 12.1121 | 12.1121 | 0.80283 | 12.2067 | 12.2067 | 12.2067 | 0.45718 | 12.3018 | 12.3018 | 12.3018 | 0.2674 | 12.3949 | 12.3949 | 12.3949 | -0.053109 | 12.4973 | 12.4973 | 12.4973 | -0.3451 | 12.8552 | 12.8552 | 12.8552 | -1.3633 | 13.118 | 13.118 | 13.118 | -1.9054 | 13.285 | 13.285 | 13.285 | -1.9702 | 13.388 | 13.388 | 13.388 | -1.8844 | 11.8139 | 11.8139 | 11.8139 | 1.8217 | 11.8408 | 11.8408 | 11.8408 | 1.7386 | 11.8857 | 11.8857 | 11.8857 | 1.4867 | 11.9413 | 11.9413 | 11.9413 | 1.2178 | 12.0046 | 12.0046 | 12.0046 | 1.1809 | 12.0763 | 12.0763 | 12.0763 | 0.9326 | 12.1558 | 12.1558 | 12.1558 | 0.61315 | 12.2421 | 12.2421 | 12.2421 | 0.44505 | 12.335 | 12.335 | 12.335 | 0.14087 | 12.4182 | 12.4182 | 12.4182 | -0.10511 | 12.6149 | 12.6149 | 12.6149 | -0.84682 | 12.7695 | 12.7695 | 12.7695 | -1.4019 | 12.8598 | 12.8598 | 12.8598 | -1.6743 | 12.9105 | 12.9105 | 12.9105 | -1.8587 | 11.8208 | 11.8208 | 11.8208 | 1.7815 | 11.8534 | 11.8534 | 11.8534 | 1.671 | 11.8895 | 11.8895 | 11.8895 | 1.4695 | 11.9478 | 11.9478 | 11.9478 | 1.19 | 12.0229 | 12.0229 | 12.0229 | 1.1289 | 12.1117 | 12.1117 | 12.1117 | 0.86009 | 12.2053 | 12.2053 | 12.2053 | 0.52505 | 12.2997 | 12.2997 | 12.2997 | 0.34292 | 12.3908 | 12.3908 | 12.3908 | 0.036595 | 12.4871 | 12.4871 | 12.4871 | -0.22483 | 12.8241 | 12.8241 | 12.8241 | -1.1223 | 13.0603 | 13.0603 | 13.0603 | -1.5956 | 13.2058 | 13.2058 | 13.2058 | -1.648 | 13.2985 | 13.2985 | 13.2985 | -1.5611 | 11.8203 | 11.8203 | 11.8203 | 1.781 | 11.8563 | 11.8563 | 11.8563 | 1.6647 | 11.906 | 11.906 | 11.906 | 1.4581 | 11.9887 | 11.9887 | 11.9887 | 1.1738 | 12.0986 | 12.0986 | 12.0986 | 1.1175 | 12.2208 | 12.2208 | 12.2208 | 0.84634 | 12.3448 | 12.3448 | 12.3448 | 0.49883 | 12.481 | 12.481 | 12.481 | 0.30401 | 12.6078 | 12.6078 | 12.6078 | 0.018685 | 12.748 | 12.748 | 12.748 | -0.20783 | 13.2342 | 13.2342 | 13.2342 | -1.7198 | 13.6972 | 13.6972 | 13.6972 | -5.2646 | 13.983 | 13.983 | 13.983 | -8.0365 | 14.152 | 14.152 | 14.152 | -10.0206 | 11.821 | 11.821 | 11.821 | 1.7784 | 11.8693 | 11.8693 | 11.8693 | 1.6397 | 11.9262 | 11.9262 | 11.9262 | 1.4358 | 12.0028 | 12.0028 | 12.0028 | 1.178 | 12.0987 | 12.0987 | 12.0987 | 1.1542 | 12.2092 | 12.2092 | 12.2092 | 0.92851 | 12.326 | 12.326 | 12.326 | 0.62358 | 12.4436 | 12.4436 | 12.4436 | 0.47752 | 12.5605 | 12.5605 | 12.5605 | 0.14528 | 12.7162 | 12.7162 | 12.7162 | -0.69437 | 13.2409 | 13.2409 | 13.2409 | -4.6165 | 13.5851 | 13.5851 | 13.5851 | -7.8389 | 13.7319 | 13.7319 | 13.7319 | -9.6834 | 13.698 | 13.698 | 13.698 | -9.1828
SALFORD QUAYS | FREDERICK RD | KEARSLEY | 380334 | 397555 | 31.5149 | 13.9629 | 10.1857 | 16.7696 | 31.642 | 13.7336 | 10.0185 | 15.5296 | 31.7006 | 13.6255 | 9.9396 | 15.1202 | 31.785 | 13.5605 | 9.8922 | 14.9569 | 31.8758 | 13.503 | 9.8503 | 14.895 | 31.9768 | 13.4109 | 9.783 | 14.5587 | 32.0803 | 13.37 | 9.7532 | 14.4589 | 32.1849 | 13.3021 | 9.7037 | 14.2419 | 32.2904 | 13.2306 | 9.6515 | 14.0907 | 32.4014 | 13.128 | 9.5767 | 13.8689 | 32.805 | 12.8945 | 9.4063 | 13.1787 | 33.0409 | 12.8338 | 9.3621 | 12.7305 | 33.1933 | 12.7521 | 9.3025 | 12.4275 | 33.3137 | 12.6334 | 9.2159 | 12.2692 | 31.4608 | 14.0586 | 10.2556 | 17.4757 | 31.5117 | 13.9349 | 10.1653 | 16.9155 | 31.5882 | 13.8515 | 10.1044 | 16.5915 | 31.6792 | 13.7771 | 10.0502 | 16.3316 | 31.7764 | 13.7218 | 10.0099 | 16.2239 | 31.8801 | 13.6482 | 9.9562 | 15.9309 | 31.9897 | 13.6004 | 9.9213 | 15.7706 | 32.1024 | 13.5485 | 9.8834 | 15.5627 | 32.2189 | 13.4906 | 9.8412 | 15.3174 | 32.3375 | 13.435 | 9.8007 | 15.0585 | 32.6492 | 13.2614 | 9.674 | 14.4841 | 32.8908 | 13.0177 | 9.4962 | 14.085 | 33.0544 | 13.1514 | 9.5937 | 13.7568 | 33.1523 | 13.1923 | 9.6236 | 13.6227 | 31.515 | 14.0578 | 10.255 | 16.7369 | 31.6421 | 13.9328 | 10.1638 | 15.5007 | 31.7007 | 13.8384 | 10.0949 | 15.0949 | 31.7853 | 13.7412 | 10.024 | 14.9456 | 31.876 | 13.6695 | 9.9717 | 14.8775 | 31.9767 | 13.577 | 9.9043 | 14.5466 | 32.08 | 13.5033 | 9.8505 | 14.4511 | 32.1845 | 13.4243 | 9.7929 | 14.2391 | 32.2889 | 13.3361 | 9.7285 | 14.0942 | 32.3955 | 13.2347 | 9.6545 | 13.8855 | 32.7788 | 13.0602 | 9.5272 | 13.2408 | 32.9751 | 13.0569 | 9.5248 | 12.8496 | 33.1042 | 13.0852 | 9.5455 | 12.5745 | 33.1847 | 13.0204 | 9.4982 | 12.4446 | 31.5091 | 13.9667 | 10.1885 | 16.7855 | 31.6296 | 13.7492 | 10.0299 | 15.5614 | 31.6804 | 13.6361 | 9.9474 | 15.1667 | 31.7574 | 13.569 | 9.8984 | 15.0188 | 31.8441 | 13.5021 | 9.8496 | 14.9643 | 31.9411 | 13.4126 | 9.7843 | 14.6391 | 32.043 | 13.3663 | 9.7505 | 14.5459 | 32.1485 | 13.2854 | 9.6915 | 14.3336 | 32.2572 | 13.2069 | 9.6343 | 14.1922 | 32.3709 | 13.0859 | 9.546 | 13.9955 | 32.8204 | 12.8747 | 9.3919 | 13.1322 | 33.1427 | 12.5101 | 9.1259 | 11.4931 | 33.2724 | 12.1086 | 8.833 | 10.0617 | 33.2806 | 11.8268 | 8.6275 | 9.0897 | 31.5007 | 13.9683 | 10.1897 | 16.7865 | 31.6179 | 13.7816 | 10.0535 | 15.5562 | 31.6567 | 13.6804 | 9.9797 | 15.1627 | 31.7129 | 13.5901 | 9.9138 | 15.031 | 31.7823 | 13.4942 | 9.8438 | 14.9809 | 31.8657 | 13.3157 | 9.7136 | 14.6708 | 31.9553 | 13.1697 | 9.6071 | 14.5886 | 32.0434 | 13.1477 | 9.5911 | 14.3903 | 32.1319 | 13.1773 | 9.6126 | 14.239 | 32.2546 | 13.1013 | 9.5572 | 13.7809 | 32.7774 | 12.6708 | 9.2432 | 11.8854 | 33.0936 | 12.1161 | 8.8385 | 10.3349 | 33.1408 | 11.817 | 8.6203 | 9.2961 | 33.0547 | 11.7625 | 8.5806 | 9.4897
SANDGATE | BARROW & SANDGATE | HARKER / HUTTON | 321492 | 468870 | 29.9806 | 10.5939 | 7.614 | 13.8916 | 30.0583 | 10.5383 | 7.5741 | 13.6067 | 30.0871 | 10.4961 | 7.5438 | 13.4499 | 30.1495 | 10.4865 | 7.5368 | 13.1596 | 30.2381 | 10.4708 | 7.5256 | 13.0662 | 30.3513 | 10.1884 | 7.3226 | 12.7376 | 30.4797 | 9.9083 | 7.1213 | 12.3459 | 30.6195 | 9.6717 | 6.9513 | 12.1259 | 30.7713 | 9.3886 | 6.7478 | 11.7958 | 30.9094 | 9.1054 | 6.5442 | 11.4014 | 31.3995 | 8.4802 | 6.0949 | 10.1595 | 31.8187 | 8.2321 | 5.9166 | 9.558 | 32.0823 | 9.3167 | 6.6961 | 9.4554 | 32.2893 | 9.2269 | 6.6315 | 9.7683 | 29.9316 | 10.6214 | 7.6338 | 14.0877 | 29.9771 | 10.5793 | 7.6035 | 13.9676 | 30.0634 | 10.4792 | 7.5316 | 13.7138 | 30.1673 | 10.405 | 7.4783 | 13.3806 | 30.286 | 10.3488 | 7.4379 | 13.2607 | 30.421 | 10.2243 | 7.3484 | 12.9144 | 30.5728 | 10.0877 | 7.2502 | 12.4931 | 30.7385 | 9.9938 | 7.1827 | 12.2331 | 30.8926 | 9.8718 | 7.0951 | 11.8456 | 31.0299 | 9.73 | 6.9931 | 11.4435 | 31.2605 | 9.4347 | 6.7809 | 10.685 | 31.4376 | 9.1152 | 6.5513 | 10.1696 | 31.5688 | 9.6874 | 6.9625 | 9.8873 | 31.6375 | 10.3619 | 7.4473 | 9.8726 | 29.9807 | 10.6235 | 7.6354 | 13.9043 | 30.0585 | 10.5835 | 7.6066 | 13.6644 | 30.0875 | 10.5074 | 7.5519 | 13.4914 | 30.1501 | 10.3205 | 7.4175 | 13.2186 | 30.2385 | 10.1789 | 7.3158 | 13.1392 | 30.3513 | 9.7622 | 7.0163 | 12.8288 | 30.4793 | 9.4502 | 6.792 | 12.4563 | 30.619 | 9.1641 | 6.5864 | 12.2517 | 30.7688 | 8.9108 | 6.4043 | 11.9973 | 30.902 | 8.6373 | 6.2078 | 11.6429 | 31.3439 | 8.2252 | 5.9116 | 10.5255 | 31.6697 | 8.064 | 5.7958 | 10.0314 | 31.8853 | 9.1321 | 6.5635 | 9.9941 | 32.0206 | 8.9654 | 6.4436 | 10.3252 | 29.9757 | 10.5967 | 7.616 | 13.8957 | 30.0527 | 10.584 | 7.6069 | 13.6112 | 30.0921 | 10.5664 | 7.5942 | 13.4547 | 30.1765 | 10.5316 | 7.5693 | 13.1676 | 30.3022 | 10.4545 | 7.5139 | 13.0756 | 30.4706 | 10.1291 | 7.28 | 12.7445 | 30.6759 | 9.8471 | 7.0773 | 12.3291 | 30.8591 | 9.5687 | 6.8772 | 12.079 | 31.0569 | 9.2969 | 6.6818 | 11.8169 | 31.2767 | 8.964 | 6.4426 | 11.5067 | 32.0954 | 8.1019 | 5.823 | 9.1506 | 32.9093 | 6.8022 | 4.8889 | 2.9793 | 33.383 | 6.9958 | 5.028 | -1.9747 | 33.5484 | 6.3125 | 4.5369 | -4.9855 | 29.958 | 10.6113 | 7.6265 | 13.9442 | 30.0305 | 10.5936 | 7.6138 | 13.669 | 30.0676 | 10.5581 | 7.5883 | 13.5439 | 30.1405 | 10.5716 | 7.598 | 13.308 | 30.2534 | 10.4766 | 7.5297 | 13.2602 | 30.4032 | 10.1384 | 7.2866 | 12.9933 | 30.5942 | 9.7632 | 7.017 | 12.6452 | 30.7728 | 9.5123 | 6.8367 | 12.4674 | 30.9646 | 9.2052 | 6.616 | 12.0688 | 31.2226 | 8.7546 | 6.2921 | 10.5861 | 32.1747 | 8.3325 | 5.9887 | 3.74 | 32.8044 | 6.8598 | 4.9303 | -1.8238 | 33.0124 | 6.1634 | 4.4298 | -5.0438 | 32.8613 | 6.245 | 4.4884 | -3.6341
SCARISBRICK | SKELMERSDALE | WASHWAY FARM / KIRKBY | 338069 | 412086 | 6.2936 | 6.2936 | 6.2936 | 2.2547 | 6.3444 | 6.3444 | 6.3444 | 2.1525 | 6.4145 | 6.4145 | 6.4145 | 2.0927 | 6.5001 | 6.5001 | 6.5001 | 2.0137 | 6.5951 | 6.5951 | 6.5951 | 1.9135 | 6.695 | 6.695 | 6.695 | 1.8066 | 6.7509 | 6.7509 | 6.7509 | 1.6686 | 6.8082 | 6.8082 | 6.8082 | 1.5369 | 6.8622 | 6.8622 | 6.8622 | 1.3552 | 6.9261 | 6.9261 | 6.9261 | 1.0932 | 7.2293 | 7.2293 | 7.2293 | 0.1214 | 7.5109 | 7.5109 | 7.5109 | -0.38419 | 7.7034 | 7.7034 | 7.7034 | -0.56809 | 7.8681 | 7.8681 | 7.8681 | -0.41315 | 6.2854 | 6.2854 | 6.2854 | 2.3322 | 6.3249 | 6.3249 | 6.3249 | 2.2929 | 6.3846 | 6.3846 | 6.3846 | 2.2093 | 6.4314 | 6.4314 | 6.4314 | 2.1439 | 6.4851 | 6.4851 | 6.4851 | 2.0587 | 6.5459 | 6.5459 | 6.5459 | 1.9704 | 6.6172 | 6.6172 | 6.6172 | 1.8527 | 6.6923 | 6.6923 | 6.6923 | 1.7488 | 6.7502 | 6.7502 | 6.7502 | 1.6271 | 6.7931 | 6.7931 | 6.7931 | 1.4835 | 6.9543 | 6.9543 | 6.9543 | 0.97967 | 7.0835 | 7.0835 | 7.0835 | 0.47622 | 7.2031 | 7.2031 | 7.2031 | 0.078377 | 7.2951 | 7.2951 | 7.2951 | -0.16263 | 6.2937 | 6.2937 | 6.2937 | 2.2567 | 6.3445 | 6.3445 | 6.3445 | 2.1594 | 6.4147 | 6.4147 | 6.4147 | 2.1058 | 6.5005 | 6.5005 | 6.5005 | 2.0351 | 6.5952 | 6.5952 | 6.5952 | 1.9428 | 6.6955 | 6.6955 | 6.6955 | 1.8437 | 6.7514 | 6.7514 | 6.7514 | 1.7183 | 6.8087 | 6.8087 | 6.8087 | 1.6116 | 6.8622 | 6.8622 | 6.8622 | 1.4327 | 6.9231 | 6.9231 | 6.9231 | 1.1853 | 7.1964 | 7.1964 | 7.1964 | 0.28865 | 7.41 | 7.41 | 7.41 | -0.11959 | 7.5681 | 7.5681 | 7.5681 | -0.21094 | 7.6766 | 7.6766 | 7.6766 | -0.025311 | 6.2939 | 6.2939 | 6.2939 | 2.2596 | 6.3564 | 6.3564 | 6.3564 | 2.1493 | 6.446 | 6.446 | 6.446 | 2.077 | 6.5539 | 6.5539 | 6.5539 | 1.9857 | 6.6832 | 6.6832 | 6.6832 | 1.8587 | 6.7572 | 6.7572 | 6.7572 | 1.693 | 6.837 | 6.837 | 6.837 | 1.4835 | 6.9293 | 6.9293 | 6.9293 | 1.2883 | 7.0326 | 7.0326 | 7.0326 | 1.0982 | 7.1495 | 7.1495 | 7.1495 | 0.89856 | 7.6363 | 7.6363 | 7.6363 | -0.04594 | 8.0519 | 8.0519 | 7.8669 | -1.3647 | 8.2722 | 8.2722 | 8.2722 | -2.1638 | 8.3587 | 8.3587 | 8.3587 | -2.7779 | 6.3065 | 6.3065 | 6.3065 | 2.2555 | 6.3927 | 6.3927 | 6.3927 | 2.1341 | 6.4957 | 6.4957 | 6.4957 | 2.0586 | 6.6152 | 6.6152 | 6.6152 | 1.9651 | 6.6957 | 6.6957 | 6.6957 | 1.8295 | 6.7702 | 6.7702 | 6.7702 | 1.6619 | 6.8657 | 6.8657 | 6.8657 | 1.4663 | 6.9628 | 6.9628 | 6.9628 | 1.2928 | 7.0694 | 7.0694 | 7.0694 | 1.1264 | 7.1958 | 7.1958 | 7.1958 | 0.81584 | 7.6839 | 7.6839 | 7.6839 | -0.73217 | 8.0048 | 8.0048 | 7.9604 | -1.8492 | 8.1051 | 8.1051 | 8.1051 | -2.3352 | 8.0821 | 8.0821 | 8.0821 | -2.1905
SEBERGHAM | CARLISLE | HARKER / HUTTON | 335344 | 542653 | 1.1742 | 1.1742 | 1.1742 | 1.1742 | 1.186 | 1.186 | 1.186 | 1.1344 | 1.2011 | 1.2011 | 1.2011 | 1.096 | 1.2205 | 1.2205 | 1.2205 | 1.0067 | 1.2425 | 1.2425 | 1.2425 | 0.93351 | 1.2677 | 1.2677 | 1.2677 | 0.87504 | 1.2984 | 1.2984 | 1.2984 | 0.7583 | 1.3325 | 1.3325 | 1.3325 | 0.66674 | 1.3719 | 1.3719 | 1.3719 | 0.56759 | 1.4221 | 1.4221 | 1.4221 | 0.4568 | 1.6644 | 1.6644 | 1.6644 | -0.015604 | 1.8978 | 1.8978 | 1.8978 | -0.39946 | 2.0718 | 2.0718 | 2.0718 | -0.60878 | 2.2107 | 2.2107 | 2.2107 | -0.47001 | 1.175 | 1.175 | 1.175 | 1.175 | 1.1874 | 1.1874 | 1.1874 | 1.1874 | 1.2052 | 1.2052 | 1.2052 | 1.2052 | 1.2231 | 1.2231 | 1.2231 | 1.1283 | 1.2431 | 1.2431 | 1.2431 | 1.0323 | 1.266 | 1.266 | 1.266 | 0.95741 | 1.2927 | 1.2927 | 1.2927 | 0.81918 | 1.3221 | 1.3221 | 1.3221 | 0.69988 | 1.3538 | 1.3538 | 1.3538 | 0.57365 | 1.3879 | 1.3879 | 1.3879 | 0.45946 | 1.4899 | 1.4899 | 1.4899 | 0.19821 | 1.6215 | 1.6215 | 1.6215 | -0.091945 | 1.7537 | 1.7537 | 1.7537 | -0.35229 | 1.8628 | 1.8628 | 1.8628 | -0.63714 | 1.1743 | 1.1743 | 1.1743 | 1.1743 | 1.1861 | 1.1861 | 1.1861 | 1.1412 | 1.2013 | 1.2013 | 1.2013 | 1.1069 | 1.2209 | 1.2209 | 1.2209 | 1.0224 | 1.2429 | 1.2429 | 1.2429 | 0.95385 | 1.2682 | 1.2682 | 1.2682 | 0.89983 | 1.2989 | 1.2989 | 1.2989 | 0.78886 | 1.3331 | 1.3331 | 1.3331 | 0.70263 | 1.372 | 1.372 | 1.372 | 0.61015 | 1.4202 | 1.4202 | 1.4202 | 0.50979 | 1.6404 | 1.6404 | 1.6404 | 0.067177 | 1.8211 | 1.8211 | 1.8211 | -0.17757 | 1.9686 | 1.9686 | 1.9686 | -0.32503 | 2.0631 | 2.0631 | 2.0631 | -0.25488 | 1.1743 | 1.1743 | 1.1743 | 1.1743 | 1.1886 | 1.1886 | 1.1886 | 1.1437 | 1.2089 | 1.2089 | 1.2089 | 1.1069 | 1.2367 | 1.2367 | 1.2367 | 1.0178 | 1.2726 | 1.2726 | 1.2726 | 0.93627 | 1.3188 | 1.3188 | 1.3188 | 0.86371 | 1.3793 | 1.3793 | 1.3793 | 0.7239 | 1.4492 | 1.4492 | 1.4492 | 0.6091 | 1.5274 | 1.5274 | 1.5274 | 0.49568 | 1.6149 | 1.6149 | 1.6149 | 0.40066 | 1.9999 | 1.9999 | 1.9999 | -0.096349 | 2.3202 | 2.3202 | 2.3202 | -0.57972 | 2.4905 | 2.4905 | 2.4905 | -0.82822 | 2.5701 | 2.5701 | 2.5701 | -0.87146 | 1.175 | 1.175 | 1.175 | 1.175 | 1.193 | 1.193 | 1.193 | 1.1363 | 1.2161 | 1.2161 | 1.2161 | 1.0998 | 1.2458 | 1.2458 | 1.2458 | 1.014 | 1.2858 | 1.2858 | 1.2858 | 0.92885 | 1.3354 | 1.3354 | 1.3354 | 0.85893 | 1.4 | 1.4 | 1.4 | 0.72692 | 1.4734 | 1.4734 | 1.4734 | 0.62281 | 1.5549 | 1.5549 | 1.5549 | 0.52079 | 1.6465 | 1.6465 | 1.6465 | 0.38255 | 2.0219 | 2.0219 | 2.0219 | -0.29875 | 2.2755 | 2.2755 | 2.2755 | -0.69964 | 2.36 | 2.36 | 2.36 | -0.81673 | 2.3677 | 2.3677 | 2.3677 | -0.6163
SEDBERGH | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 365151 | 491747 | 18.655 | 18.655 | 18.655 | 12.8334 | 18.7026 | 18.7026 | 18.7026 | 12.7019 | 18.7635 | 18.7635 | 18.7635 | 12.5387 | 18.8007 | 18.8007 | 18.8007 | 12.3362 | 18.8457 | 18.8457 | 18.8457 | 12.2094 | 18.8996 | 18.8996 | 18.8996 | 11.9891 | 18.9638 | 18.9638 | 18.9638 | 11.7359 | 19.0344 | 19.0344 | 19.0344 | 11.4895 | 19.1111 | 19.1111 | 19.0316 | 11.2212 | 19.1984 | 19.1984 | 18.9408 | 10.8359 | 19.5409 | 19.5409 | 18.5836 | 9.5525 | 19.827 | 19.827 | 18.3568 | 8.8909 | 20.0036 | 20.0036 | 18.2106 | 8.6503 | 20.1133 | 20.1133 | 18.1381 | 8.8394 | 18.6553 | 18.6553 | 18.6553 | 12.8621 | 18.7032 | 18.7032 | 18.7032 | 12.7665 | 18.7719 | 18.7719 | 18.7719 | 12.5793 | 18.8303 | 18.8303 | 18.8303 | 12.4024 | 18.8739 | 18.8739 | 18.8739 | 12.303 | 18.9232 | 18.9232 | 18.9232 | 12.103 | 18.9803 | 18.9803 | 18.9803 | 11.87 | 19.0424 | 19.0424 | 19.0424 | 11.6424 | 19.1094 | 19.1094 | 19.1094 | 11.3832 | 19.1806 | 19.1806 | 19.1074 | 11.0259 | 19.3674 | 19.3674 | 18.9559 | 10.3952 | 19.5543 | 19.5543 | 18.7954 | 9.7217 | 19.688 | 19.688 | 18.6587 | 9.1817 | 19.7739 | 19.7739 | 18.5558 | 8.8523 | 18.6566 | 18.6566 | 18.6566 | 12.842 | 18.7047 | 18.7047 | 18.7047 | 12.7139 | 18.7645 | 18.7645 | 18.7645 | 12.5601 | 18.8018 | 18.8018 | 18.8018 | 12.3683 | 18.8467 | 18.8467 | 18.8467 | 12.2495 | 18.9 | 18.9 | 18.9 | 12.0395 | 18.9634 | 18.9634 | 18.9634 | 11.7932 | 19.033 | 19.033 | 19.033 | 11.5474 | 19.1078 | 19.1078 | 19.0627 | 11.2907 | 19.1903 | 19.1903 | 18.9768 | 10.9395 | 19.506 | 19.506 | 18.7238 | 9.7689 | 19.7414 | 19.7414 | 18.4962 | 9.1951 | 19.8782 | 19.8782 | 18.2831 | 8.9996 | 19.9548 | 19.9548 | 18.1015 | 9.1908 | 18.6572 | 18.6572 | 18.6572 | 12.8349 | 18.7102 | 18.7102 | 18.7102 | 12.6921 | 18.7686 | 18.7686 | 18.7686 | 12.5194 | 18.8129 | 18.8129 | 18.8129 | 12.3097 | 18.8701 | 18.8701 | 18.8701 | 12.1625 | 18.9427 | 18.9427 | 18.9427 | 11.9124 | 19.0349 | 19.0349 | 19.0349 | 11.616 | 19.1409 | 19.1409 | 19.0225 | 11.3331 | 19.259 | 19.259 | 18.9394 | 11.0799 | 19.3912 | 19.3912 | 18.8529 | 10.7883 | 19.8739 | 19.8739 | 18.4596 | 9.6182 | 20.2445 | 20.2445 | 18.0611 | 8.1651 | 20.4285 | 20.4285 | 17.7802 | 7.3326 | 20.5087 | 20.5087 | 17.5788 | 6.8271 | 18.6652 | 18.6652 | 18.6652 | 12.8296 | 18.7317 | 18.7317 | 18.7317 | 12.6589 | 18.76 | 18.76 | 18.76 | 12.486 | 18.7978 | 18.7978 | 18.7978 | 12.2877 | 18.8487 | 18.8487 | 18.8487 | 12.1373 | 18.9139 | 18.9139 | 18.9139 | 11.9025 | 19.0009 | 19.0009 | 19.0009 | 11.636 | 19.0993 | 19.0993 | 19.001 | 11.3946 | 19.2086 | 19.2086 | 18.9189 | 11.1719 | 19.3353 | 19.3353 | 18.8056 | 10.7498 | 19.7813 | 19.7813 | 18.2989 | 8.9718 | 20.0465 | 20.0465 | 17.8884 | 7.817 | 20.1389 | 20.1389 | 17.696 | 7.3581 | 20.1349 | 20.1349 | 17.6221 | 7.6108
SELSMIRE | PENRITH & SHAP | HARKER / HUTTON | 361018 | 507505 | 4.5029 | 4.5029 | 4.5029 | 1.8621 | 4.5158 | 4.5158 | 4.5158 | 1.7425 | 4.5293 | 4.5293 | 4.5293 | 1.727 | 4.5473 | 4.5473 | 4.5473 | 1.6447 | 4.5695 | 4.5695 | 4.5695 | 1.6442 | 4.5955 | 4.5955 | 4.5955 | 1.5512 | 4.6278 | 4.6278 | 4.6278 | 1.4729 | 4.6622 | 4.6622 | 4.6622 | 1.4635 | 4.6856 | 4.6856 | 4.6856 | 1.3626 | 4.7129 | 4.7129 | 4.7129 | 1.2437 | 4.8178 | 4.8178 | 4.8178 | 0.72081 | 4.9047 | 4.9047 | 4.9047 | 0.35913 | 4.959 | 4.959 | 4.959 | 0.15648 | 4.9983 | 4.9983 | 4.9983 | 0.15543 | 4.4983 | 4.4983 | 4.4983 | 1.8928 | 4.5074 | 4.5074 | 4.5074 | 1.8013 | 4.522 | 4.522 | 4.522 | 1.7755 | 4.5379 | 4.5379 | 4.5379 | 1.7002 | 4.5556 | 4.5556 | 4.5556 | 1.7033 | 4.5755 | 4.5755 | 4.5755 | 1.6156 | 4.5991 | 4.5991 | 4.5991 | 1.5414 | 4.6239 | 4.6239 | 4.6239 | 1.5334 | 4.6496 | 4.6496 | 4.6496 | 1.4453 | 4.6763 | 4.6763 | 4.6763 | 1.3756 | 4.7593 | 4.7593 | 4.7593 | 1.1539 | 4.8258 | 4.8258 | 4.8258 | 0.84441 | 4.8722 | 4.8722 | 4.8722 | 0.55203 | 4.8985 | 4.8985 | 4.8985 | 0.35745 | 4.503 | 4.503 | 4.503 | 1.8631 | 4.5159 | 4.5159 | 4.5159 | 1.7481 | 4.5293 | 4.5293 | 4.5293 | 1.7366 | 4.5474 | 4.5474 | 4.5474 | 1.6587 | 4.5695 | 4.5695 | 4.5695 | 1.6602 | 4.5954 | 4.5954 | 4.5954 | 1.5703 | 4.6275 | 4.6275 | 4.6275 | 1.4944 | 4.6621 | 4.6621 | 4.6621 | 1.4859 | 4.6854 | 4.6854 | 4.6854 | 1.3906 | 4.7115 | 4.7115 | 4.7115 | 1.2867 | 4.8072 | 4.8072 | 4.8072 | 0.81095 | 4.8765 | 4.8765 | 4.8765 | 0.50705 | 4.9221 | 4.9221 | 4.9221 | 0.34073 | 4.948 | 4.948 | 4.948 | 0.34874 | 4.5025 | 4.5025 | 4.5025 | 1.8656 | 4.5157 | 4.5157 | 4.5157 | 1.7437 | 4.5311 | 4.5311 | 4.5311 | 1.7257 | 4.5541 | 4.5541 | 4.5541 | 1.638 | 4.5845 | 4.5845 | 4.5845 | 1.6228 | 4.6226 | 4.6226 | 4.6226 | 1.5086 | 4.6619 | 4.6619 | 4.6619 | 1.3997 | 4.6954 | 4.6954 | 4.6954 | 1.3644 | 4.7327 | 4.7327 | 4.7327 | 1.2502 | 4.7748 | 4.7748 | 4.7748 | 1.1571 | 4.926 | 4.926 | 4.926 | 0.56622 | 5.0277 | 5.0277 | 5.0277 | 0.20639 | 5.0649 | 5.0649 | 5.0649 | 0.10123 | 5.0707 | 5.0707 | 5.0707 | 0.089139 | 4.5069 | 4.5069 | 4.5069 | 1.8588 | 4.5263 | 4.5263 | 4.5263 | 1.7265 | 4.5445 | 4.5445 | 4.5445 | 1.7068 | 4.5681 | 4.5681 | 4.5681 | 1.6196 | 4.5994 | 4.5994 | 4.5994 | 1.5939 | 4.6281 | 4.6281 | 4.6281 | 1.4766 | 4.6566 | 4.6566 | 4.6566 | 1.3738 | 4.6882 | 4.6882 | 4.6882 | 1.3483 | 4.723 | 4.723 | 4.723 | 1.2446 | 4.7616 | 4.7616 | 4.7616 | 1.1274 | 4.8977 | 4.8977 | 4.8977 | 0.56362 | 4.9761 | 4.9761 | 4.9761 | 0.31993 | 4.9882 | 4.9882 | 4.9882 | 0.32072 | 4.9746 | 4.9746 | 4.9746 | 0.41779
SETTLE | PADIHAM | PADIHAM | 381588 | 463721 | 13.6325 | 13.6325 | 13.6325 | 8.103 | 13.6581 | 13.6581 | 13.6581 | 7.9703 | 13.6688 | 13.6688 | 13.6688 | 7.9474 | 13.687 | 13.687 | 13.687 | 7.8932 | 13.7046 | 13.7046 | 13.7046 | 7.8232 | 13.7271 | 13.7271 | 13.7271 | 7.7389 | 13.7512 | 13.7512 | 13.7512 | 7.6436 | 13.7767 | 13.7767 | 13.7767 | 7.5679 | 13.803 | 13.803 | 13.803 | 7.4832 | 13.8354 | 13.8354 | 13.8354 | 7.375 | 13.9816 | 13.9816 | 13.9816 | 7.0062 | 14.1416 | 14.1416 | 14.1416 | 6.4516 | 14.2629 | 14.2629 | 14.2629 | 6.0642 | 14.3721 | 14.3721 | 14.3721 | 5.9961 | 13.6248 | 13.6248 | 13.6248 | 8.2012 | 13.6407 | 13.6407 | 13.6407 | 8.1449 | 13.6628 | 13.6628 | 13.6628 | 8.0542 | 13.6891 | 13.6891 | 13.6891 | 7.9496 | 13.718 | 13.718 | 13.718 | 7.8313 | 13.7505 | 13.7505 | 13.7505 | 7.705 | 13.7863 | 13.7863 | 13.7863 | 7.5565 | 13.8253 | 13.8253 | 13.8253 | 7.4184 | 13.8669 | 13.8669 | 13.8669 | 7.2614 | 13.9118 | 13.9118 | 13.9118 | 7.093 | 13.9956 | 13.9956 | 13.9956 | 6.8551 | 14.0962 | 14.0962 | 14.0962 | 6.5981 | 14.1955 | 14.1955 | 14.1955 | 6.3562 | 14.2758 | 14.2758 | 14.2758 | 5.9652 | 13.6326 | 13.6326 | 13.6326 | 8.1087 | 13.6582 | 13.6582 | 13.6582 | 7.9822 | 13.669 | 13.669 | 13.669 | 7.9657 | 13.6874 | 13.6874 | 13.6874 | 7.9182 | 13.7051 | 13.7051 | 13.7051 | 7.8554 | 13.7278 | 13.7278 | 13.7278 | 7.7786 | 13.752 | 13.752 | 13.752 | 7.6915 | 13.7776 | 13.7776 | 13.7776 | 7.6238 | 13.8038 | 13.8038 | 13.8038 | 7.5482 | 13.8356 | 13.8356 | 13.8356 | 7.4512 | 13.9669 | 13.9669 | 13.9669 | 7.099 | 14.0819 | 14.0819 | 14.0819 | 6.7062 | 14.1806 | 14.1806 | 14.1806 | 6.3811 | 14.2479 | 14.2479 | 14.2479 | 6.3389 | 13.6312 | 13.6312 | 13.6312 | 8.1096 | 13.6571 | 13.6571 | 13.6571 | 7.9796 | 13.6692 | 13.6692 | 13.6692 | 7.9584 | 13.6875 | 13.6875 | 13.6875 | 7.906 | 13.7089 | 13.7089 | 13.7089 | 7.8318 | 13.7394 | 13.7394 | 13.7394 | 7.7385 | 13.7763 | 13.7763 | 13.7763 | 7.6264 | 13.8179 | 13.8179 | 13.8179 | 7.532 | 13.8623 | 13.8623 | 13.8623 | 7.4332 | 13.9111 | 13.9111 | 13.9111 | 7.3333 | 14.1487 | 14.1487 | 14.1487 | 6.4332 | 14.3978 | 14.3978 | 14.3978 | 4.9362 | 14.5423 | 14.5423 | 14.5423 | 3.963 | 14.6085 | 14.6085 | 14.6085 | 3.2353 | 13.6248 | 13.6248 | 13.6248 | 8.1229 | 13.6454 | 13.6454 | 13.6454 | 8.0044 | 13.653 | 13.653 | 13.653 | 7.9952 | 13.6686 | 13.6686 | 13.6686 | 7.9556 | 13.6908 | 13.6908 | 13.6908 | 7.891 | 13.7218 | 13.7218 | 13.7218 | 7.8102 | 13.7589 | 13.7589 | 13.7589 | 7.7141 | 13.8017 | 13.8017 | 13.8017 | 7.6364 | 13.849 | 13.849 | 13.849 | 7.5515 | 13.9086 | 13.9086 | 13.9086 | 7.2916 | 14.1816 | 14.1816 | 14.1816 | 5.4991 | 14.3876 | 14.3876 | 14.3876 | 4.1645 | 14.4684 | 14.4684 | 14.4684 | 3.5047 | 14.4653 | 14.4653 | 14.4653 | 3.6254
MOSS SIDE (Leyland) & SEVEN STARS | LEYLAND | PENWORTHAM WEST / STANAH | 352653 | 421636 | 31.4089 | 14.3827 | 10.3371 | 10.3957 | 31.5257 | 14.1246 | 10.1516 | 9.7511 | 31.6195 | 13.9504 | 10.0264 | 9.6207 | 31.7454 | 13.651 | 9.8112 | 9.1797 | 31.9107 | 13.3381 | 9.5863 | 8.9377 | 32.107 | 12.6899 | 9.1205 | 8.3621 | 32.3283 | 12.5689 | 9.0335 | 7.8841 | 32.5671 | 12.4587 | 8.9543 | 7.1967 | 32.8241 | 12.298 | 8.8388 | 6.5211 | 33.1301 | 12.0741 | 8.6779 | 5.7565 | 34.6372 | 11.004 | 7.9088 | 3.0375 | 36.1295 | 10.067 | 7.2353 | 1.4147 | 37.2506 | 9.424 | 6.7732 | 0.87104 | 38.2951 | 9.1559 | 6.5805 | 0.41982 | 31.3735 | 14.4406 | 10.3787 | 10.7539 | 31.4542 | 14.3144 | 10.2881 | 10.3615 | 31.5715 | 14.1989 | 10.205 | 10.1523 | 31.6804 | 14.0522 | 10.0996 | 9.7046 | 31.8168 | 13.9324 | 10.0135 | 9.489 | 31.9766 | 13.7605 | 9.89 | 8.9766 | 32.1561 | 13.6234 | 9.7914 | 8.5743 | 32.3465 | 13.4576 | 9.6723 | 8.0909 | 32.5487 | 13.2724 | 9.5391 | 7.5099 | 32.7581 | 13.0786 | 9.3998 | 6.9042 | 33.7124 | 12.3232 | 8.8569 | 4.8339 | 34.6632 | 11.5327 | 8.2888 | 3.3529 | 35.4762 | 11.362 | 8.1661 | 2.4466 | 36.1083 | 11.1417 | 8.0077 | 1.8736 | 31.4099 | 14.4317 | 10.3723 | 10.4021 | 31.5276 | 14.1636 | 10.1796 | 9.8191 | 31.6226 | 13.781 | 9.9047 | 9.7025 | 31.7499 | 13.5118 | 9.7112 | 9.2743 | 31.9162 | 13.5944 | 9.7706 | 9.0467 | 32.1126 | 13.437 | 9.6575 | 8.4891 | 32.3337 | 13.2789 | 9.5438 | 8.0021 | 32.5724 | 13.1108 | 9.423 | 7.3321 | 32.8265 | 12.9146 | 9.282 | 6.6841 | 33.1206 | 12.6399 | 9.0846 | 5.9866 | 34.4616 | 11.7727 | 8.4613 | 3.584 | 35.4588 | 10.9909 | 7.8994 | 2.4101 | 36.3261 | 10.3865 | 7.465 | 2.1084 | 37.0173 | 9.7914 | 7.0373 | 1.9774 | 31.4162 | 14.3832 | 10.3375 | 10.4138 | 31.5477 | 14.1181 | 10.147 | 9.7832 | 31.6685 | 13.7513 | 9.8833 | 9.674 | 31.8362 | 13.3088 | 9.5653 | 9.2526 | 32.0495 | 13.0044 | 9.3465 | 9.0469 | 32.3282 | 12.9939 | 9.339 | 8.5012 | 32.6764 | 12.8281 | 9.2198 | 8.0605 | 33.0787 | 12.6321 | 9.0789 | 7.6049 | 33.5051 | 12.392 | 8.9064 | 7.0875 | 33.9824 | 12.1293 | 8.7176 | 6.5845 | 36.3812 | 10.4702 | 7.5251 | 3.279 | 38.7751 | 8.5172 | 6.1214 | -2.1704 | 40.1553 | 6.7917 | 4.8814 | -6.2738 | 33.2175 | 5.469 | 3.9307 | -9.2434 | 31.4158 | 14.3808 | 10.3358 | 10.4013 | 31.5621 | 14.1044 | 10.1371 | 9.7174 | 31.6958 | 13.8707 | 9.9692 | 9.6023 | 31.8734 | 13.3602 | 9.6023 | 9.2067 | 32.0963 | 13.279 | 9.5438 | 9.0336 | 32.3962 | 13.1723 | 9.4672 | 8.5275 | 32.7848 | 12.9748 | 9.3252 | 8.1087 | 33.2373 | 12.7442 | 9.1595 | 7.6146 | 33.7935 | 12.482 | 8.9711 | 7.0094 | 34.5914 | 11.9962 | 8.6219 | 5.6873 | 37.2651 | 9.8226 | 7.0597 | -0.31499 | 39.1797 | 7.9749 | 5.7317 | -5.1998 | 40.023 | 6.7588 | 4.8577 | -8.1955 | 38.4265 | 6.3266 | 4.5471 | -7.8881
SHANNON ST SOUTH | BLACKPOOL | PENWORTHAM WEST / STANAH | 330806 | 435291 | 32.0185 | 11.067 | 8.0732 | 12.4048 | 32.0459 | 10.936 | 7.9776 | 12.1016 | 32.0828 | 11.034 | 8.0492 | 12.0346 | 32.1587 | 11.0042 | 8.0274 | 11.69 | 32.2516 | 10.9039 | 7.9542 | 11.5159 | 32.3703 | 10.7367 | 7.8323 | 11.1166 | 32.512 | 10.5692 | 7.7101 | 10.758 | 32.6718 | 10.3897 | 7.5791 | 10.3778 | 32.8501 | 10.1965 | 7.4382 | 9.9208 | 33.0723 | 9.9738 | 7.2757 | 9.3818 | 34.0648 | 9.2079 | 6.717 | 7.5544 | 35.0058 | 8.8098 | 6.4267 | 6.3308 | 35.626 | 8.7698 | 6.3975 | 5.8491 | 35.9008 | 8.772 | 6.399 | 5.9735 | 32.0468 | 11.2224 | 8.1866 | 12.4586 | 32.1206 | 11.123 | 8.1141 | 12.1819 | 32.2078 | 11.0288 | 8.0454 | 11.9728 | 32.3136 | 10.8976 | 7.9496 | 11.5729 | 32.4396 | 10.7951 | 7.8749 | 11.3488 | 32.5936 | 10.6374 | 7.7599 | 10.8814 | 32.7751 | 10.5042 | 7.6627 | 10.4329 | 32.9801 | 10.3592 | 7.5569 | 9.9448 | 33.2062 | 10.194 | 7.4364 | 9.3544 | 33.4552 | 9.9397 | 7.2509 | 8.2986 | 34.0672 | 9.7443 | 7.1083 | 7.6001 | 34.6839 | 9.5051 | 6.9338 | 6.5567 | 35.039 | 9.4978 | 6.9285 | 5.9403 | 35.2465 | 9.4912 | 6.9237 | 5.5969 | 32.0259 | 11.2212 | 8.1857 | 12.4178 | 32.0543 | 11.1559 | 8.138 | 12.1489 | 32.0925 | 11.0144 | 8.0348 | 12.1145 | 32.1688 | 10.8173 | 7.8911 | 11.8007 | 32.261 | 10.6367 | 7.7593 | 11.6532 | 32.3753 | 10.4735 | 7.6403 | 11.2859 | 32.5096 | 10.3029 | 7.5158 | 10.9581 | 32.6618 | 10.1267 | 7.3873 | 10.6098 | 32.829 | 9.9234 | 7.239 | 10.1963 | 33.0338 | 9.6694 | 7.0537 | 9.7288 | 33.9538 | 9.2029 | 6.7134 | 8.0428 | 34.7177 | 8.9403 | 6.5218 | 7.0453 | 35.129 | 8.911 | 6.5004 | 6.7643 | 35.2888 | 8.8087 | 6.4258 | 6.9726 | 32.0273 | 11.0598 | 8.068 | 12.3986 | 32.0632 | 10.9658 | 7.9994 | 12.0927 | 32.1169 | 11.256 | 8.2111 | 12.0357 | 32.2184 | 11.0422 | 8.0552 | 11.6988 | 32.3502 | 10.8687 | 7.9286 | 11.5171 | 32.5345 | 10.7026 | 7.8074 | 11.0992 | 32.771 | 10.5395 | 7.6884 | 10.6786 | 33.0432 | 10.3636 | 7.5601 | 10.2338 | 33.3365 | 10.1828 | 7.4282 | 9.772 | 33.6642 | 9.9937 | 7.2903 | 9.3104 | 35.3482 | 8.9644 | 6.5394 | 6.4372 | 37.3697 | 7.4249 | 5.4164 | -0.51572 | 38.198 | 6.4244 | 4.6865 | -5.8222 | 35.5742 | 5.7705 | 4.2095 | -9.2767 | 32.0068 | 11.0603 | 8.0683 | 12.3989 | 32.0315 | 11.1158 | 8.1088 | 12.0797 | 32.0678 | 11.1511 | 8.1346 | 12.0865 | 32.146 | 11.0184 | 8.0378 | 11.8437 | 32.2663 | 10.8346 | 7.9037 | 11.7199 | 32.4382 | 10.6027 | 7.7345 | 11.3786 | 32.6634 | 10.3585 | 7.5564 | 11.0479 | 32.9304 | 10.1785 | 7.4251 | 10.6977 | 33.2705 | 9.9699 | 7.2729 | 10.2053 | 33.9176 | 9.5329 | 6.9541 | 8.5806 | 35.7857 | 7.6337 | 5.5687 | 1.193 | 35.6103 | 5.7763 | 4.2138 | -5.1155 | 31.2878 | 5.0752 | 3.7023 | -8.791 | 31.4813 | 5.1066 | 3.7252 | -7.8126
SHAP | PENRITH & SHAP | HARKER / HUTTON | 356910 | 513357 | 12.5032 | 12.5032 | 12.5032 | 7.1105 | 12.5392 | 12.5392 | 12.5392 | 6.9808 | 12.5829 | 12.5829 | 12.5829 | 6.9988 | 12.6363 | 12.6363 | 12.6363 | 7.001 | 12.6688 | 12.6688 | 12.6688 | 6.9079 | 12.7058 | 12.7058 | 12.7058 | 6.8529 | 12.7504 | 12.7504 | 12.7504 | 6.7664 | 12.7988 | 12.7988 | 12.7988 | 6.7673 | 12.8499 | 12.8499 | 12.8499 | 6.6797 | 12.8892 | 12.8892 | 12.8892 | 6.6085 | 15.0827 | 15.0827 | 14.9842 | 4.3721 | 17.3888 | 17.3888 | 14.7002 | 2.0489 | 17.5497 | 17.5497 | 14.6148 | 1.8359 | 17.7537 | 17.7537 | 14.5683 | 1.6445 | 12.4962 | 12.4962 | 12.4962 | 7.1893 | 12.5265 | 12.5265 | 12.5265 | 7.1228 | 12.5747 | 12.5747 | 12.5747 | 7.102 | 12.5988 | 12.5988 | 12.5988 | 7.0776 | 12.6253 | 12.6253 | 12.6253 | 6.9659 | 12.6547 | 12.6547 | 12.6547 | 6.8986 | 12.6886 | 12.6886 | 12.6886 | 6.7962 | 12.7243 | 12.7243 | 12.7243 | 6.777 | 12.7613 | 12.7613 | 12.7613 | 6.6644 | 12.7994 | 12.7994 | 12.7994 | 6.5718 | 12.9395 | 12.9395 | 12.9395 | 6.4411 | 13.0727 | 13.0727 | 13.0727 | 6.2862 | 13.191 | 13.191 | 13.191 | 6.1824 | 13.2861 | 13.2861 | 13.2861 | 6.1052 | 12.5033 | 12.5033 | 12.5033 | 7.1128 | 12.5394 | 12.5394 | 12.5394 | 6.9862 | 12.5832 | 12.5832 | 12.5832 | 7.0062 | 12.6368 | 12.6368 | 12.6368 | 7.0104 | 12.6696 | 12.6696 | 12.6696 | 6.9209 | 12.7066 | 12.7066 | 12.7066 | 6.869 | 12.7513 | 12.7513 | 12.7513 | 6.7861 | 12.7997 | 12.7997 | 12.7997 | 6.7891 | 12.8504 | 12.8504 | 12.8504 | 6.7061 | 12.8895 | 12.8895 | 12.8895 | 6.6415 | 15.0584 | 15.0584 | 15.0584 | 4.4223 | 17.2891 | 17.2891 | 15.1343 | 2.1642 | 17.4124 | 17.4124 | 15.0062 | 2.0504 | 17.5676 | 17.5676 | 15.0004 | 1.9161 | 12.5021 | 12.5021 | 12.5021 | 7.1159 | 12.5357 | 12.5357 | 12.5357 | 6.9915 | 12.5737 | 12.5737 | 12.5737 | 7.0149 | 12.6195 | 12.6195 | 12.6195 | 7.0219 | 12.6729 | 12.6729 | 12.6729 | 6.933 | 12.733 | 12.733 | 12.733 | 6.8791 | 12.8044 | 12.8044 | 12.8044 | 6.7905 | 12.8692 | 12.8692 | 12.8692 | 6.7572 | 12.9177 | 12.9177 | 12.9177 | 6.6942 | 12.9718 | 12.9718 | 12.9718 | 6.6137 | 13.2826 | 13.2826 | 13.2826 | 6.0608 | 16.262 | 16.262 | 14.6133 | 2.5264 | 16.454 | 16.454 | 14.4556 | 1.8818 | 16.474 | 16.474 | 14.3499 | 1.4972 | 12.5117 | 12.5117 | 12.5117 | 7.1166 | 12.5589 | 12.5589 | 12.5589 | 6.9904 | 12.6009 | 12.6009 | 12.6009 | 7.0149 | 12.6449 | 12.6449 | 12.6449 | 7.0252 | 12.6956 | 12.6956 | 12.6956 | 6.9395 | 12.752 | 12.752 | 12.752 | 6.8881 | 14.0985 | 14.0985 | 14.0985 | 5.4797 | 14.1006 | 14.1006 | 14.1006 | 5.4947 | 14.0953 | 14.0953 | 14.0953 | 5.4891 | 14.1271 | 14.1271 | 14.1271 | 5.3527 | 15.6741 | 15.6741 | 14.8071 | 3.214 | 16.075 | 16.075 | 14.5807 | 2.2653 | 16.1341 | 16.1341 | 14.4658 | 1.8384 | 16.0734 | 16.0734 | 14.4405 | 1.9529
SHAW | ROYTON | WHITEGATE | 394298 | 409450 | 31.2918 | 10.9711 | 8.0032 | 14.422 | 31.3705 | 10.8391 | 7.9069 | 14.1256 | 31.4156 | 10.6969 | 7.8033 | 13.9424 | 31.4973 | 10.5195 | 7.6738 | 13.6042 | 31.6083 | 10.3331 | 7.5379 | 13.3045 | 31.7438 | 10.1213 | 7.3834 | 12.9183 | 31.8973 | 10.027 | 7.3146 | 12.5914 | 32.0658 | 9.9162 | 7.2337 | 12.1616 | 32.2472 | 9.7945 | 7.145 | 11.6935 | 32.4464 | 9.6502 | 7.0397 | 11.124 | 33.3044 | 9.0549 | 6.6055 | 9.0464 | 34.1523 | 8.8794 | 6.4774 | 7.9327 | 34.7895 | 9.701 | 7.0767 | 7.5981 | 35.3989 | 9.7212 | 7.0915 | 7.6073 | 31.2504 | 10.9111 | 7.9595 | 14.5416 | 31.2906 | 10.7146 | 7.8162 | 14.3445 | 31.3654 | 10.3972 | 7.5846 | 14.0981 | 31.4581 | 10.2432 | 7.4723 | 13.7572 | 31.5635 | 10.0845 | 7.3565 | 13.4833 | 31.6806 | 9.8562 | 7.19 | 13.1318 | 31.8103 | 9.7882 | 7.1404 | 12.8349 | 31.95 | 9.6991 | 7.0754 | 12.4363 | 32.099 | 9.6007 | 7.0036 | 11.9939 | 32.2556 | 9.504 | 6.9331 | 11.5634 | 32.709 | 9.1916 | 6.7051 | 10.2546 | 33.1259 | 9.0901 | 6.6311 | 9.1725 | 33.5242 | 9.5703 | 6.9814 | 8.4862 | 33.8566 | 9.9491 | 7.2577 | 8.0316 | 31.292 | 10.9105 | 7.9591 | 14.4294 | 31.371 | 10.6592 | 7.7758 | 14.1437 | 31.4166 | 10.4353 | 7.6124 | 13.971 | 31.4989 | 10.2241 | 7.4584 | 13.6424 | 31.6101 | 9.9014 | 7.2229 | 13.3534 | 31.7456 | 9.8493 | 7.1849 | 12.9791 | 31.899 | 9.7896 | 7.1414 | 12.6626 | 32.0676 | 9.7058 | 7.0803 | 12.244 | 32.2471 | 9.6089 | 7.0095 | 11.7944 | 32.4365 | 9.5131 | 6.9397 | 11.2937 | 33.2085 | 9.2284 | 6.732 | 9.4325 | 33.8438 | 9.1852 | 6.7005 | 8.5421 | 34.3722 | 9.9699 | 7.2729 | 8.2932 | 34.7995 | 9.794 | 7.1446 | 8.3943 | 31.2882 | 10.9733 | 8.0049 | 14.4301 | 31.3667 | 10.8534 | 7.9174 | 14.145 | 31.4271 | 10.7079 | 7.8113 | 13.9805 | 31.5397 | 10.5154 | 7.6708 | 13.6642 | 31.7005 | 10.3283 | 7.5343 | 13.4056 | 31.9121 | 10.1086 | 7.3741 | 13.0636 | 32.1718 | 10.0066 | 7.2997 | 12.7661 | 32.4621 | 9.8806 | 7.2078 | 12.3695 | 32.7482 | 9.7569 | 7.1175 | 11.9885 | 33.0687 | 9.6236 | 7.0203 | 11.6206 | 34.4961 | 8.8008 | 6.4201 | 8.9605 | 35.9114 | 7.7781 | 5.674 | 3.0618 | 36.7964 | 7.7113 | 5.6253 | -1.6764 | 37.2481 | 7.1038 | 5.1821 | -4.8206 | 31.2836 | 10.9801 | 8.0098 | 14.4561 | 31.3723 | 11.0205 | 8.0393 | 14.162 | 31.4455 | 11.0084 | 8.0305 | 14.0003 | 31.5615 | 10.9227 | 7.968 | 13.7188 | 31.7247 | 10.813 | 7.8879 | 13.4925 | 31.9376 | 10.6529 | 7.7711 | 13.2014 | 32.2093 | 10.5344 | 7.6847 | 12.9535 | 32.5097 | 10.4069 | 7.5917 | 12.6148 | 32.8176 | 10.2528 | 7.4793 | 12.1008 | 33.1992 | 9.9383 | 7.2498 | 10.7223 | 34.7499 | 9.2582 | 6.7537 | 4.2432 | 35.9014 | 8.0046 | 5.8392 | -1.1548 | 36.3798 | 7.3708 | 5.3769 | -4.2955 | 36.3693 | 7.411 | 5.4062 | -3.4929
Siddick | STAINBURN & SIDDICK | HARKER / HUTTON | 300289 | 530805 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
SILLOTH | CARLISLE | HARKER / HUTTON | 311307 | 553464 | 36.2804 | 21.0749 | 15.147 | 36.2804 | 36.3314 | 21.0059 | 15.0974 | 36.3314 | 36.3454 | 20.9753 | 15.0754 | 36.3454 | 36.3774 | 20.9122 | 15.03 | 36.3774 | 36.4235 | 20.8672 | 14.9977 | 36.4235 | 36.4833 | 20.7739 | 14.9306 | 36.4833 | 36.5537 | 20.6896 | 14.8701 | 36.5537 | 36.6311 | 20.6309 | 14.8278 | 36.6311 | 36.7139 | 20.5325 | 14.7571 | 36.7139 | 36.8074 | 20.3856 | 14.6515 | 36.8074 | 37.1689 | 20.0043 | 14.3775 | 37.1689 | 37.4732 | 19.7629 | 14.204 | 37.4732 | 37.6671 | 20.0039 | 14.3772 | 37.6671 | 37.8022 | 20.3151 | 14.6009 | 37.8022 | 36.2317 | 21.104 | 15.1679 | 36.2317 | 36.2454 | 21.0554 | 15.1329 | 36.2454 | 36.2801 | 21.0157 | 15.1044 | 36.2801 | 36.3223 | 20.9564 | 15.0618 | 36.3223 | 36.3704 | 20.9177 | 15.0339 | 36.3704 | 36.4236 | 20.837 | 14.9759 | 36.4236 | 36.4841 | 20.7703 | 14.928 | 36.4841 | 36.5491 | 20.7291 | 14.8984 | 36.5491 | 36.6179 | 20.6496 | 14.8413 | 36.6179 | 36.6898 | 20.5797 | 14.791 | 36.6898 | 36.8989 | 20.4267 | 14.6811 | 36.8989 | 37.0905 | 20.2428 | 14.5489 | 37.0905 | 37.2248 | 20.3611 | 14.6339 | 37.2248 | 37.3064 | 20.5721 | 14.7856 | 37.3064 | 36.2809 | 21.104 | 15.1679 | 36.2809 | 36.3322 | 21.0547 | 15.1324 | 36.3322 | 36.3464 | 21.0078 | 15.0987 | 36.3464 | 36.3787 | 20.9399 | 15.0499 | 36.3787 | 36.4247 | 20.8918 | 15.0154 | 36.4247 | 36.4841 | 20.8032 | 14.9517 | 36.4841 | 36.5538 | 20.7247 | 14.8952 | 36.5538 | 36.6304 | 20.6714 | 14.8569 | 36.6304 | 36.7114 | 20.5787 | 14.7903 | 36.7114 | 36.7994 | 20.4951 | 14.7303 | 36.7994 | 37.1333 | 20.2628 | 14.5633 | 37.1333 | 37.3667 | 20.0455 | 14.4071 | 37.3667 | 37.5175 | 20.1971 | 14.5161 | 37.5175 | 37.5957 | 20.3255 | 14.6083 | 37.5957 | 36.2769 | 21.0754 | 15.1473 | 36.2769 | 36.3266 | 21.0027 | 15.0951 | 36.3266 | 36.3446 | 20.9709 | 15.0722 | 36.3446 | 36.3863 | 20.9016 | 15.0224 | 36.3863 | 36.45 | 20.847 | 14.9832 | 36.45 | 36.5389 | 20.7402 | 14.9064 | 36.5389 | 36.653 | 20.6369 | 14.8322 | 36.653 | 36.7865 | 20.5588 | 14.776 | 36.7865 | 36.915 | 20.4489 | 14.697 | 36.915 | 37.0356 | 20.3203 | 14.6046 | 37.0356 | 37.5505 | 19.9131 | 14.3119 | 37.5505 | 38.0264 | 19.3918 | 13.9373 | 37.4161 | 38.276 | 19.3678 | 13.92 | 36.463 | 38.3578 | 19.3489 | 13.9064 | 35.7858 | 36.2752 | 21.0777 | 15.149 | 36.2752 | 36.3297 | 21.0084 | 15.0992 | 36.3297 | 36.3534 | 20.9654 | 15.0682 | 36.3534 | 36.3979 | 20.8917 | 15.0153 | 36.3979 | 36.4647 | 20.8315 | 14.972 | 36.4647 | 36.556 | 20.7319 | 14.9004 | 36.556 | 36.6765 | 20.6373 | 14.8325 | 36.6765 | 36.8141 | 20.5348 | 14.7588 | 36.8141 | 36.932 | 20.436 | 14.6877 | 36.932 | 37.0699 | 20.2814 | 14.5767 | 37.0699 | 37.6141 | 19.7021 | 14.1603 | 37.6141 | 37.9787 | 19.2283 | 13.8197 | 36.68 | 38.0947 | 19.5129 | 14.0243 | 36.0858 | 38.0344 | 19.4787 | 13.9998 | 36.3535
SKELMERSDALE | SKELMERSDALE | WASHWAY FARM / KIRKBY | 347198 | 407434 | 9.6598 | 1.5904 | 1.1431 | 9.6598 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 6.6254 | 1.0908 | 0.78399 | 4.9166 | 15.8067 | 2.6024 | 1.8704 | 4.1545 | 11.1492 | 1.8356 | 1.3193 | 11.1492 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 11.1297 | 1.8324 | 1.317 | 11.1297 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 11.4936 | 1.8923 | 1.3601 | 6.1871 | 20.1773 | 3.322 | 2.3876 | 5.9217 | 9.6519 | 1.5891 | 1.1421 | 9.6519 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.431 | 0.44197 | 0.31765 | 1.431 | 2.6844 | 0.44197 | 0.31765 | 1.3225 | 2.6844 | 0.44197 | 0.31765 | -2.4663 | 2.6844 | 0.44197 | 0.31765 | -4.9557 | 9.6988 | 1.5968 | 1.1477 | 9.6988 | 8.9456 | 1.4728 | 1.0585 | 8.9456 | 7.9745 | 1.3129 | 0.94363 | 7.9745 | 7.131 | 1.1741 | 0.84383 | 7.131 | 5.9568 | 0.98075 | 0.70488 | 5.9568 | 4.9222 | 0.8104 | 0.58245 | 4.9222 | 3.852 | 0.6342 | 0.45581 | 3.852 | 3.1013 | 0.5106 | 0.36698 | 3.1013 | 2.3049 | 0.37949 | 0.27275 | 2.3049 | 1.2106 | 0.19931 | 0.14325 | 1.2106 | 13.8885 | 2.2866 | 1.6434 | 3.181 | 5.1672 | 0.85074 | 0.61144 | -1.5832 | 3.8517 | 0.63415 | 0.45577 | -4.052 | 2.6062 | 0.4291 | 0.3084 | -3.8211
HUTTON END & SKELTON C | PENRITH & SHAP | HARKER / HUTTON | 342672 | 538337 | 29.7375 | 28.7655 | 20.6743 | 15.5124 | 29.8148 | 28.5303 | 20.5053 | 15.3183 | 29.8755 | 28.3147 | 20.3503 | 15.316 | 29.962 | 28.0687 | 20.1735 | 15.187 | 30.0515 | 27.819 | 19.9941 | 15.0452 | 30.134 | 27.5323 | 19.788 | 14.7988 | 30.23 | 27.428 | 19.713 | 14.5173 | 30.2978 | 27.3425 | 19.6516 | 14.3504 | 30.3755 | 27.2411 | 19.5787 | 14.0898 | 30.4805 | 27.1075 | 19.4827 | 13.6538 | 30.9315 | 26.6339 | 19.1423 | 12.0813 | 31.3254 | 26.2124 | 18.8394 | 11.1961 | 31.5969 | 26.0745 | 18.7403 | 10.7302 | 31.7375 | 25.9495 | 18.6504 | 10.9413 | 29.6928 | 28.8033 | 20.7015 | 15.7079 | 29.7345 | 28.7845 | 20.688 | 15.6727 | 29.8105 | 28.7531 | 20.6654 | 15.607 | 29.8936 | 28.6903 | 20.6203 | 15.3866 | 29.9527 | 28.6436 | 20.5867 | 15.2549 | 30.0184 | 28.5744 | 20.537 | 15.0202 | 30.0942 | 28.5066 | 20.4882 | 14.7473 | 30.1743 | 28.4577 | 20.4531 | 14.5817 | 30.2576 | 28.4011 | 20.4124 | 14.3553 | 30.3443 | 28.3387 | 20.3676 | 14.0853 | 30.7034 | 28.1304 | 20.2179 | 13.2418 | 31.004 | 27.8561 | 20.0207 | 12.1162 | 31.2667 | 27.6058 | 19.8408 | 11.1484 | 31.4439 | 27.412 | 19.7015 | 10.5183 | 29.7384 | 28.8009 | 20.6998 | 15.5143 | 29.8161 | 28.5939 | 20.551 | 15.3218 | 29.8772 | 28.3671 | 20.388 | 15.321 | 29.9639 | 28.1045 | 20.1992 | 15.2546 | 30.0533 | 27.8572 | 20.0215 | 15.0904 | 30.135 | 27.5806 | 19.8228 | 14.8901 | 30.2306 | 27.4857 | 19.7545 | 14.6162 | 30.2979 | 27.4013 | 19.6939 | 14.4548 | 30.3745 | 27.2265 | 19.5683 | 14.2074 | 30.4757 | 27.2366 | 19.5755 | 13.8076 | 30.8929 | 26.9261 | 19.3523 | 12.3737 | 31.2072 | 26.5633 | 19.0916 | 11.615 | 31.4325 | 26.1912 | 18.8241 | 11.2225 | 31.5081 | 25.8792 | 18.5999 | 11.462 | 29.7337 | 28.7668 | 20.6752 | 15.5281 | 29.8075 | 28.5282 | 20.5038 | 15.3402 | 29.8659 | 28.3014 | 20.3408 | 15.3432 | 29.9558 | 28.0362 | 20.1502 | 15.1756 | 30.0715 | 27.7662 | 19.9561 | 14.9932 | 30.2142 | 27.4533 | 19.7312 | 14.6886 | 30.3338 | 27.3159 | 19.6324 | 14.3203 | 30.4564 | 27.1987 | 19.5482 | 14.0818 | 30.589 | 27.0744 | 19.4589 | 13.8069 | 30.7345 | 26.9399 | 19.3622 | 13.4973 | 31.3356 | 26.3996 | 18.9739 | 12.1936 | 31.7917 | 25.9595 | 18.6576 | 11.4101 | 31.973 | 25.7409 | 18.5005 | 11.344 | 32.0037 | 25.5026 | 18.3292 | 11.2575 | 29.7461 | 28.7666 | 20.6751 | 15.5224 | 29.8444 | 28.5374 | 20.5104 | 15.3197 | 29.9159 | 28.3098 | 20.3468 | 15.3155 | 30.0074 | 28.0417 | 20.1542 | 15.1359 | 30.1248 | 27.7643 | 19.9547 | 14.9147 | 30.2297 | 27.4508 | 19.7295 | 14.5969 | 30.3428 | 27.3145 | 19.6315 | 14.2467 | 30.4668 | 27.202 | 19.5506 | 14.0347 | 30.601 | 27.0837 | 19.4656 | 13.7875 | 30.7478 | 26.9496 | 19.3692 | 13.449 | 31.3236 | 26.4047 | 18.9776 | 12.0282 | 31.6753 | 25.9796 | 18.6721 | 11.4287 | 31.7372 | 25.8058 | 18.5472 | 11.529 | 31.6788 | 25.7032 | 18.4734 | 11.8633
SLIPWAY | EGREMONT | HARKER / HUTTON | 297180 | 518183 | 17.3237 | 17.3237 | 12.8748 | 7.4358 | 17.369 | 17.369 | 12.8476 | 7.3123 | 17.368 | 17.368 | 12.8133 | 7.3159 | 17.388 | 17.388 | 12.7443 | 7.1747 | 17.4207 | 17.4207 | 12.6916 | 7.075 | 17.4636 | 17.4636 | 12.6028 | 6.8913 | 17.5083 | 17.3558 | 12.4739 | 6.6827 | 17.5557 | 17.0878 | 12.2814 | 6.5141 | 17.6052 | 17.072 | 12.27 | 6.3765 | 17.6613 | 17.0911 | 12.2837 | 6.1154 | 17.8485 | 16.7737 | 12.0556 | 5.4087 | 17.9653 | 16.7461 | 12.0358 | 5.0577 | 18.0095 | 16.7141 | 12.0127 | 4.9825 | 18.0035 | 16.5978 | 11.9292 | 5.1805 | 17.2835 | 17.2835 | 12.8981 | 7.5212 | 17.2926 | 17.2926 | 12.8837 | 7.4761 | 17.3237 | 17.3237 | 12.8663 | 7.3845 | 17.3635 | 17.3635 | 12.8629 | 7.2102 | 17.4104 | 17.4104 | 12.8679 | 7.0861 | 17.4631 | 17.4631 | 12.8584 | 6.8782 | 17.5216 | 17.5216 | 12.8421 | 6.6346 | 17.5849 | 17.5849 | 12.8237 | 6.4231 | 17.6526 | 17.6526 | 12.8019 | 6.2163 | 17.7248 | 17.7248 | 12.7701 | 5.9371 | 17.8001 | 17.693 | 12.7163 | 5.5365 | 17.8506 | 17.6525 | 12.6872 | 5.2385 | 17.8608 | 17.7625 | 12.7663 | 5.0743 | 17.8358 | 17.8358 | 12.8263 | 5.0687 | 17.3237 | 17.3237 | 12.8986 | 7.447 | 17.369 | 17.369 | 12.8901 | 7.3408 | 17.368 | 17.368 | 12.8801 | 7.3491 | 17.388 | 17.388 | 12.8941 | 7.22 | 17.4206 | 17.4206 | 12.9068 | 7.1313 | 17.4633 | 17.4633 | 12.9185 | 6.9606 | 17.5077 | 17.5077 | 12.9016 | 6.7654 | 17.555 | 17.555 | 12.8954 | 6.609 | 17.6038 | 17.6038 | 12.8162 | 6.4862 | 17.6572 | 17.6572 | 12.7088 | 6.256 | 17.8318 | 17.4058 | 12.5099 | 5.6274 | 17.9381 | 17.1858 | 12.3518 | 5.3287 | 17.9768 | 17.0922 | 12.2845 | 5.2743 | 17.969 | 16.8476 | 12.1087 | 5.4611 | 17.3206 | 17.3206 | 12.8733 | 7.4366 | 17.3622 | 17.3622 | 12.8411 | 7.3099 | 17.3624 | 17.3624 | 12.7889 | 7.308 | 17.3882 | 17.3882 | 12.7171 | 7.1569 | 17.4309 | 17.4309 | 12.6564 | 7.047 | 17.488 | 17.465 | 12.5525 | 6.8458 | 17.5562 | 17.2227 | 12.3783 | 6.5882 | 17.6334 | 16.9418 | 12.1764 | 6.3557 | 17.715 | 17.0216 | 12.2338 | 6.183 | 17.8061 | 16.9825 | 12.2057 | 5.9346 | 18.1006 | 16.5518 | 11.8961 | 4.7382 | 18.3697 | 15.7694 | 11.3337 | 1.7454 | 18.4594 | 15.1236 | 10.8696 | -0.66945 | 18.4797 | 14.5783 | 10.4777 | -2.2898 | 17.3104 | 17.3104 | 12.8774 | 7.4601 | 17.3461 | 17.3461 | 12.8499 | 7.3373 | 17.3473 | 17.3473 | 12.7954 | 7.3493 | 17.3692 | 17.3692 | 12.7259 | 7.2178 | 17.4068 | 17.4068 | 12.6709 | 7.1232 | 17.4552 | 17.4432 | 12.5368 | 6.9368 | 17.5139 | 17.1602 | 12.3334 | 6.7252 | 17.5784 | 16.9925 | 12.2128 | 6.537 | 17.6535 | 17.0325 | 12.2416 | 6.3304 | 17.775 | 16.8717 | 12.126 | 5.5447 | 18.1023 | 16.2634 | 11.6888 | 2.1321 | 18.2471 | 15.3318 | 11.0193 | -0.57105 | 18.2519 | 14.7701 | 10.6155 | -2.178 | 18.1346 | 14.6921 | 10.5595 | -1.5948
SNIPE | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 31.1397 | 8.0608 | 5.8802 | 13.8903 | 31.1992 | 7.8419 | 5.7206 | 13.3781 | 31.2173 | 7.6713 | 5.5961 | 13.42 | 31.2675 | 7.435 | 5.4237 | 13.2093 | 31.3381 | 7.2863 | 5.3153 | 13.1328 | 31.4175 | 7.0589 | 5.1494 | 12.7728 | 31.5066 | 6.9774 | 5.0899 | 12.5451 | 31.6031 | 6.8792 | 5.0183 | 12.3053 | 31.7061 | 6.7053 | 4.8914 | 11.9363 | 31.8187 | 6.6072 | 4.8198 | 11.6375 | 32.3762 | 6.1609 | 4.4943 | 10.4324 | 32.9403 | 5.8617 | 4.2761 | 9.5726 | 33.3488 | 5.9543 | 4.3436 | 9.1597 | 33.7237 | 5.6894 | 4.1503 | 8.9608 | 31.0893 | 8.103 | 5.911 | 14.1848 | 31.1099 | 7.8815 | 5.7495 | 13.9237 | 31.153 | 7.6359 | 5.5703 | 13.8709 | 31.2057 | 7.4005 | 5.3985 | 13.6251 | 31.2665 | 7.0058 | 5.1106 | 13.5453 | 31.3343 | 6.9129 | 5.0429 | 13.2189 | 31.4095 | 6.8775 | 5.017 | 13.0161 | 31.4892 | 6.8308 | 4.9829 | 12.7993 | 31.5733 | 6.7563 | 4.9286 | 12.4527 | 31.6596 | 6.7002 | 4.8877 | 12.1993 | 31.9549 | 6.5023 | 4.7433 | 11.3862 | 32.2431 | 6.2705 | 4.5742 | 10.7107 | 32.5096 | 6.4996 | 4.7414 | 10.3187 | 32.7234 | 6.6427 | 4.8458 | 10.1282 | 31.1399 | 8.1038 | 5.9116 | 13.8964 | 31.1995 | 7.8809 | 5.749 | 13.3939 | 31.218 | 7.545 | 5.504 | 13.4437 | 31.2687 | 7.2906 | 5.3184 | 13.2397 | 31.3395 | 7.0961 | 5.1765 | 13.1707 | 31.4189 | 6.9009 | 5.0341 | 12.82 | 31.5081 | 6.8543 | 5.0001 | 12.6003 | 31.6047 | 6.7859 | 4.9502 | 12.368 | 31.7067 | 6.6891 | 4.8796 | 12.0119 | 31.8138 | 6.5855 | 4.8041 | 11.741 | 32.3087 | 6.2344 | 4.5479 | 10.6636 | 32.72 | 6.0098 | 4.3841 | 9.9765 | 33.0513 | 6.4508 | 4.7058 | 9.6437 | 33.3094 | 6.2104 | 4.5304 | 9.5495 | 31.134 | 8.0645 | 5.8829 | 13.9094 | 31.1906 | 7.854 | 5.7294 | 13.4166 | 31.2146 | 7.6792 | 5.6019 | 13.4749 | 31.2802 | 7.3834 | 5.3861 | 13.2769 | 31.3641 | 7.2587 | 5.2951 | 13.2111 | 31.4792 | 7.0289 | 5.1275 | 12.8557 | 31.6218 | 6.9018 | 5.0347 | 12.6191 | 31.7876 | 6.6603 | 4.8586 | 12.3627 | 31.9723 | 6.6248 | 4.8327 | 11.9899 | 32.179 | 6.4794 | 4.7266 | 11.7054 | 33.1618 | 5.7985 | 4.2299 | 9.897 | 29.4741 | 4.781 | 3.4877 | 6.0974 | 26.899 | 4.3633 | 3.183 | 3.1023 | 23.0304 | 3.7358 | 2.7252 | 1.2011 | 31.1294 | 8.0657 | 5.8838 | 13.9045 | 31.192 | 8.0012 | 5.8368 | 13.3837 | 31.2224 | 7.9767 | 5.8189 | 13.4307 | 31.2878 | 7.8464 | 5.7238 | 13.2421 | 31.371 | 7.8031 | 5.6923 | 13.1903 | 31.4864 | 7.6961 | 5.6142 | 12.8584 | 31.6368 | 7.5648 | 5.5184 | 12.6369 | 31.8103 | 7.419 | 5.4121 | 12.4004 | 32.0193 | 7.3178 | 5.3383 | 11.9914 | 32.3087 | 7.072 | 5.159 | 11.2159 | 33.395 | 6.0074 | 4.3823 | 7.2034 | 30.6418 | 4.9704 | 3.6258 | 3.7017 | 26.7093 | 4.3325 | 3.1605 | 1.788 | 25.8431 | 4.192 | 3.058 | 2.3943
S.E. MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 29.4416 | 12.3892 | 8.9044 | 14.6798 | 29.5168 | 12.2801 | 8.8259 | 14.0409 | 29.5866 | 12.1703 | 8.7471 | 13.6605 | 29.68 | 12.0559 | 8.6648 | 13.3358 | 29.7962 | 11.8969 | 8.5506 | 12.8243 | 29.9342 | 11.7392 | 8.4372 | 12.3616 | 30.0953 | 11.5434 | 8.2965 | 11.7948 | 30.2714 | 11.3218 | 8.1372 | 11.1494 | 30.4484 | 11.0832 | 7.9657 | 10.423 | 30.6362 | 10.9124 | 7.843 | 9.8008 | 31.4018 | 10.3097 | 7.4098 | 7.2058 | 32.0702 | 9.881 | 7.1017 | 5.672 | 32.4988 | 9.6629 | 6.9449 | 5.3504 | 32.8562 | 9.3877 | 6.7471 | 5.4631 | 29.4401 | 12.4403 | 8.9411 | 14.9364 | 29.5199 | 12.4004 | 8.9124 | 14.5274 | 29.6275 | 12.3256 | 8.8587 | 14.1013 | 29.748 | 12.2693 | 8.8182 | 13.7668 | 29.8852 | 12.1606 | 8.7401 | 13.2645 | 30.0409 | 12.0646 | 8.6711 | 12.8092 | 30.218 | 11.9343 | 8.5774 | 12.3036 | 30.4095 | 11.774 | 8.4622 | 11.6571 | 30.5957 | 11.6236 | 8.3541 | 11.0104 | 30.7927 | 11.4922 | 8.2596 | 10.4863 | 31.307 | 11.0774 | 7.9616 | 8.6559 | 31.6735 | 10.8246 | 7.7798 | 7.098 | 31.9632 | 10.6842 | 7.679 | 6.2444 | 32.1921 | 10.5207 | 7.5614 | 5.6242 | 29.4425 | 12.4335 | 8.9362 | 14.6926 | 29.5182 | 12.3742 | 8.8936 | 14.0738 | 29.5884 | 12.2693 | 8.8182 | 13.7134 | 29.6823 | 12.1717 | 8.7481 | 13.4073 | 29.7985 | 12.0352 | 8.65 | 12.9192 | 29.9356 | 11.9017 | 8.554 | 12.4786 | 30.0956 | 11.7332 | 8.4329 | 11.9604 | 30.2705 | 11.5555 | 8.3052 | 11.3076 | 30.4454 | 11.4273 | 8.213 | 10.6784 | 30.6241 | 11.3129 | 8.1308 | 10.0748 | 31.3195 | 10.8503 | 7.7984 | 7.7188 | 31.8398 | 10.4739 | 7.5278 | 6.4474 | 32.2028 | 10.1851 | 7.3202 | 6.191 | 32.4527 | 9.9119 | 7.1239 | 6.3295 | 29.4424 | 12.3878 | 8.9033 | 14.6916 | 29.5239 | 12.2673 | 8.8167 | 14.057 | 29.6122 | 12.1249 | 8.7144 | 13.6822 | 29.7361 | 11.9911 | 8.6183 | 13.3578 | 29.897 | 11.8102 | 8.4882 | 12.8609 | 30.0906 | 11.623 | 8.3537 | 12.406 | 30.2976 | 11.3863 | 8.1836 | 11.8858 | 30.5279 | 11.1744 | 8.0312 | 11.2372 | 30.7803 | 11.0416 | 7.9358 | 10.622 | 31.0617 | 10.9091 | 7.8406 | 10.1951 | 32.1743 | 10.0694 | 7.2371 | 7.2444 | 33.2907 | 8.8282 | 6.345 | 2.3982 | 33.9246 | 7.9047 | 5.6813 | -0.79267 | 34.2412 | 7.2515 | 5.2118 | -2.8975 | 29.4452 | 12.3818 | 8.899 | 14.653 | 29.539 | 12.2078 | 8.774 | 13.9734 | 29.6276 | 12.0137 | 8.6345 | 13.6131 | 29.7442 | 11.81 | 8.488 | 13.3204 | 29.8834 | 11.6875 | 8.4001 | 12.8448 | 30.0357 | 11.5866 | 8.3275 | 12.4379 | 30.2339 | 11.4287 | 8.214 | 11.9276 | 30.4574 | 11.2755 | 8.1039 | 11.3822 | 30.7119 | 11.0922 | 7.9722 | 10.7158 | 31.0229 | 10.814 | 7.7722 | 9.5927 | 32.1992 | 9.3468 | 6.7178 | 3.9076 | 33.043 | 8.0067 | 5.7545 | -0.36716 | 33.3907 | 7.4188 | 5.332 | -2.341 | 33.3994 | 7.3525 | 5.2844 | -1.5447
SOUTH PARK | LYTHAM | PENWORTHAM WEST / STANAH | 336410 | 427512 | 29.3782 | 12.5767 | 9.0391 | 19.1486 | 29.4214 | 12.4481 | 8.9467 | 18.9062 | 29.4405 | 12.3443 | 8.8721 | 18.7807 | 29.4756 | 12.1214 | 8.7119 | 18.5617 | 29.5198 | 11.849 | 8.5161 | 18.4106 | 29.5724 | 11.5287 | 8.2859 | 18.1622 | 29.6287 | 11.4407 | 8.2227 | 17.9336 | 29.6871 | 11.382 | 8.1805 | 17.6744 | 29.7477 | 11.2736 | 8.1026 | 17.4591 | 29.8119 | 11.2121 | 8.0584 | 17.182 | 30.0426 | 10.8736 | 7.8151 | 16.3466 | 30.2396 | 10.615 | 7.6292 | 15.8612 | 30.3739 | 10.373 | 7.4553 | 15.7168 | 30.485 | 10.2113 | 7.339 | 15.682 | 29.3621 | 12.6351 | 9.0811 | 19.2711 | 29.3943 | 12.4985 | 8.9829 | 19.1335 | 29.4408 | 12.4819 | 8.971 | 18.9361 | 29.4992 | 12.4004 | 8.9124 | 18.6847 | 29.5645 | 12.3588 | 8.8825 | 18.5122 | 29.6363 | 12.3131 | 8.8497 | 18.2487 | 29.7154 | 12.2512 | 8.8052 | 17.9939 | 29.8003 | 12.1876 | 8.7595 | 17.701 | 29.889 | 12.1162 | 8.7082 | 17.439 | 29.9642 | 12.0407 | 8.6539 | 17.127 | 30.1161 | 11.8324 | 8.5042 | 16.418 | 30.2374 | 11.6626 | 8.3821 | 15.9008 | 30.3262 | 11.4529 | 8.2314 | 15.6283 | 30.3916 | 11.1564 | 8.0183 | 15.4394 | 29.3782 | 12.6367 | 9.0823 | 19.1538 | 29.4215 | 12.4231 | 8.9287 | 18.9227 | 29.4406 | 11.9685 | 8.602 | 18.8087 | 29.4758 | 12.0076 | 8.6301 | 18.5996 | 29.52 | 11.9909 | 8.6181 | 18.4584 | 29.5724 | 11.7087 | 8.4152 | 18.2213 | 29.6287 | 11.5853 | 8.3266 | 18.0034 | 29.6871 | 11.4686 | 8.2427 | 17.7556 | 29.7472 | 11.3586 | 8.1637 | 17.554 | 29.8089 | 11.2376 | 8.0767 | 17.3023 | 30.0214 | 10.7379 | 7.7175 | 16.5364 | 30.1831 | 10.6602 | 7.6617 | 16.1059 | 30.2994 | 10.4966 | 7.5441 | 15.9789 | 30.3835 | 10.3405 | 7.432 | 15.954 | 29.3756 | 12.5752 | 9.0381 | 19.1621 | 29.4172 | 12.4511 | 8.9489 | 18.9334 | 29.4376 | 12.1863 | 8.7585 | 18.823 | 29.4778 | 11.8117 | 8.4893 | 18.6154 | 29.5305 | 11.7241 | 8.4263 | 18.4833 | 29.5965 | 11.6956 | 8.4058 | 18.2565 | 29.6715 | 11.547 | 8.2991 | 18.0477 | 29.7536 | 11.453 | 8.2315 | 17.8089 | 29.8421 | 11.4326 | 8.2168 | 17.6349 | 29.9381 | 11.3507 | 8.158 | 17.4159 | 30.2761 | 10.7249 | 7.7082 | 16.2548 | 30.5906 | 9.8465 | 7.0769 | 13.8093 | 30.7677 | 9.2978 | 6.6825 | 11.9511 | 30.8508 | 8.9222 | 6.4125 | 10.7004 | 29.3705 | 12.5774 | 9.0397 | 19.1581 | 29.4099 | 12.4373 | 8.9389 | 18.919 | 29.4255 | 12.3524 | 8.8779 | 18.8195 | 29.4575 | 12.0927 | 8.6912 | 18.6365 | 29.501 | 11.6662 | 8.3847 | 18.5366 | 29.5564 | 11.4738 | 8.2464 | 18.3491 | 29.6228 | 11.4846 | 8.2542 | 18.1746 | 29.6944 | 11.4404 | 8.2224 | 17.976 | 29.7747 | 11.3579 | 8.1632 | 17.7749 | 29.8783 | 11.1531 | 8.016 | 17.148 | 30.2562 | 10.2314 | 7.3535 | 14.3721 | 30.5049 | 9.3907 | 6.7493 | 12.1495 | 30.5872 | 9.031 | 6.4908 | 10.9291 | 30.5409 | 8.9636 | 6.4423 | 11.3232
S.W. MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 22.2619 | 3.6652 | 2.6343 | 8.5271 | 21.2637 | 3.5009 | 2.5162 | 7.757 | 20.4676 | 3.3698 | 2.422 | 7.2353 | 19.714 | 3.2458 | 2.3328 | 6.8168 | 18.5628 | 3.0562 | 2.1966 | 6.0087 | 17.5242 | 2.8852 | 2.0737 | 5.3205 | 16.392 | 2.6988 | 1.9397 | 4.5186 | 15.1401 | 2.4927 | 1.7916 | 3.6411 | 14.119 | 2.3246 | 1.6707 | 3.003 | 12.5996 | 2.0744 | 1.4909 | 1.9156 | 6.5403 | 1.0768 | 0.77392 | -1.5543 | 3.1514 | 0.51885 | 0.37291 | -3.612 | 4.9993 | 0.8231 | 0.59158 | -4.0048 | 6.4273 | 1.0582 | 0.76056 | -3.8899 | 22.4713 | 3.6997 | 2.6591 | 8.764 | 21.7439 | 3.58 | 2.573 | 8.2156 | 20.9871 | 3.4554 | 2.4834 | 7.6675 | 20.3733 | 3.3543 | 2.4108 | 7.293 | 19.4306 | 3.1991 | 2.2993 | 6.5824 | 18.5916 | 3.061 | 2.2 | 6.0083 | 17.7169 | 2.9169 | 2.0965 | 5.297 | 16.7309 | 2.7546 | 1.9798 | 4.5099 | 15.9911 | 2.6328 | 1.8923 | 3.9535 | 14.9807 | 2.4665 | 1.7727 | 3.0913 | 11.9121 | 1.9612 | 1.4096 | 0.64044 | 8.7522 | 1.441 | 1.0357 | -1.4981 | 8.0026 | 1.3176 | 0.94696 | -2.5405 | 9.5803 | 1.5773 | 1.1337 | -3.4196 | 22.4582 | 3.6976 | 2.6575 | 8.5422 | 21.7504 | 3.581 | 2.5738 | 7.8089 | 20.7941 | 3.4236 | 2.4606 | 7.3228 | 20.1746 | 3.3216 | 2.3873 | 6.924 | 19.1433 | 3.1518 | 2.2653 | 6.1341 | 18.1884 | 2.9946 | 2.1523 | 5.4806 | 17.1022 | 2.8158 | 2.0237 | 4.7135 | 15.9056 | 2.6187 | 1.8821 | 3.8705 | 14.9726 | 2.4651 | 1.7717 | 3.2774 | 13.7441 | 2.2629 | 1.6264 | 2.2928 | 9.4435 | 1.5548 | 1.1175 | -0.79696 | 5.5206 | 0.90893 | 0.65327 | -2.5719 | 7.0739 | 1.1647 | 0.83707 | -2.8551 | 7.5904 | 1.2497 | 0.89819 | -2.7052 | 22.2749 | 3.6674 | 2.6358 | 8.5401 | 21.2719 | 3.5023 | 2.5171 | 7.7735 | 20.3965 | 3.3581 | 2.4136 | 7.2579 | 19.5791 | 3.2235 | 2.3168 | 6.8321 | 18.3109 | 3.0148 | 2.1668 | 6.0606 | 17.1023 | 2.8158 | 2.0237 | 5.3971 | 15.7819 | 2.5984 | 1.8675 | 4.6016 | 14.2598 | 2.3478 | 1.6874 | 3.7428 | 13.0323 | 2.1457 | 1.5421 | 3.221 | 11.5076 | 1.8946 | 1.3617 | 2.3919 | 3.4882 | 0.5743 | 0.41276 | -1.6223 | 2.6844 | 0.44197 | 0.31765 | -8.6253 | 2.6844 | 0.44197 | 0.31765 | -13.32 | 2.6844 | 0.44197 | 0.31765 | -16.7182 | 22.2591 | 3.6648 | 2.634 | 8.5117 | 21.5074 | 3.541 | 2.545 | 7.6829 | 20.6367 | 3.3977 | 2.442 | 7.1723 | 19.7451 | 3.2509 | 2.3365 | 6.7898 | 18.3634 | 3.0234 | 2.173 | 6.0366 | 17.0321 | 2.8042 | 2.0154 | 5.4624 | 15.5648 | 2.5626 | 1.8418 | 4.7643 | 14.0269 | 2.3094 | 1.6598 | 4.0299 | 12.6102 | 2.0762 | 1.4922 | 3.4466 | 9.7717 | 1.6088 | 1.1563 | 1.6016 | 2.6844 | 0.44197 | 0.31765 | -6.3632 | 2.6844 | 0.44197 | 0.31765 | -12.6187 | 2.6844 | 0.44197 | 0.31765 | -15.5397 | 2.6844 | 0.44197 | 0.31765 | -14.6415
SPA RD | BOLTON | KEARSLEY | 371065 | 409109 | 34.447 | 8.1779 | 5.9656 | 7.1997 | 34.5289 | 7.9817 | 5.8226 | 6.2144 | 34.6816 | 7.9385 | 5.791 | 6.6311 | 34.8701 | 7.7403 | 5.6465 | 6.1591 | 35.0933 | 7.6055 | 5.5481 | 6.1394 | 35.3498 | 7.3736 | 5.379 | 5.2628 | 35.6475 | 7.2956 | 5.322 | 5.1758 | 35.974 | 7.113 | 5.1888 | 4.5377 | 36.3239 | 6.9427 | 5.0646 | 4.1614 | 36.7025 | 6.7278 | 4.9079 | 3.4794 | 36.1264 | 5.8601 | 4.2748 | 1.4642 | 33.6855 | 5.4641 | 3.986 | 0.29021 | 34.9062 | 5.6621 | 4.1304 | -0.44194 | 37.1242 | 6.0219 | 4.3929 | -0.6665 | 34.5087 | 8.2419 | 6.0123 | 7.7148 | 34.6477 | 8.035 | 5.8614 | 7.1554 | 34.8408 | 8.01 | 5.8432 | 7.384 | 35.0626 | 7.8397 | 5.719 | 6.7152 | 35.3126 | 7.7537 | 5.6562 | 6.6628 | 35.5989 | 7.5348 | 5.4966 | 5.9437 | 35.9262 | 7.436 | 5.4245 | 5.6024 | 36.2886 | 7.2811 | 5.3114 | 4.9534 | 36.6861 | 7.1339 | 5.2041 | 4.2359 | 37.0745 | 7.0055 | 5.1104 | 3.6716 | 38.0842 | 6.738 | 4.9153 | 2.5054 | 38.9585 | 6.5128 | 4.751 | 1.8023 | 39.5666 | 6.8129 | 4.9699 | 1.2364 | 39.9979 | 7.1737 | 5.2331 | 1.1117 | 34.4516 | 8.2367 | 6.0085 | 7.2146 | 34.5353 | 8.0452 | 5.8688 | 6.2575 | 34.6893 | 8.0162 | 5.8477 | 6.6213 | 34.8789 | 7.816 | 5.7017 | 6.1383 | 35.1017 | 7.6799 | 5.6024 | 6.2604 | 35.3546 | 7.459 | 5.4413 | 5.2505 | 35.6468 | 7.3447 | 5.3579 | 5.1761 | 35.9663 | 7.1684 | 5.2292 | 4.5563 | 36.3037 | 6.9632 | 5.0796 | 4.203 | 36.6544 | 6.7122 | 4.8964 | 3.5784 | 38.2852 | 6.2431 | 4.5542 | 1.8141 | 36.831 | 5.9743 | 4.3582 | 0.9604 | 39.1227 | 6.3461 | 4.6294 | 0.38298 | 39.7166 | 6.4424 | 4.6997 | 0.33441 | 34.454 | 8.1822 | 5.9688 | 7.2286 | 34.5428 | 7.9888 | 5.8277 | 6.2693 | 34.7123 | 7.9219 | 5.7789 | 6.7132 | 34.9392 | 7.734 | 5.6419 | 6.2484 | 35.2172 | 7.5915 | 5.5379 | 6.241 | 35.5555 | 7.3556 | 5.3658 | 5.3024 | 35.966 | 7.2573 | 5.2941 | 5.1446 | 36.4317 | 7.0359 | 5.1326 | 4.4185 | 36.943 | 6.8535 | 4.9996 | 3.9767 | 37.502 | 6.5975 | 4.8128 | 3.2335 | 34.125 | 5.5354 | 4.038 | 0.20481 | 25.6334 | 4.158 | 3.0332 | -4.8895 | 22.8103 | 3.7001 | 2.6991 | -8.8595 | 21.7581 | 3.5294 | 2.5746 | -11.2171 | 34.4533 | 8.186 | 5.9716 | 7.2347 | 34.57 | 8.0399 | 5.865 | 6.2518 | 34.7484 | 7.9462 | 5.7966 | 6.651 | 34.9614 | 7.8233 | 5.707 | 6.1728 | 35.2212 | 7.7331 | 5.6412 | 6.2616 | 35.543 | 7.4239 | 5.4157 | 5.2523 | 35.9597 | 7.2459 | 5.2858 | 5.1228 | 36.4288 | 7.0181 | 5.1196 | 4.4408 | 36.9482 | 6.8353 | 4.9862 | 3.9938 | 37.5424 | 6.3596 | 4.6393 | 2.3911 | 27.905 | 4.5265 | 3.302 | -3.6969 | 18.3702 | 2.9798 | 2.1737 | -8.0667 | 20.3929 | 3.3079 | 2.4131 | -10.5695 | 20.6562 | 3.3506 | 2.4442 | -9.4541
SPADEADAM 132/11KV | - | HARKER / HUTTON | 361282 | 570359 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795
SPOTLAND | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 15.5115 | 13.0267 | 9.5028 | 10.3516 | 15.5726 | 11.2577 | 8.2123 | 10.1656 | 15.6132 | 9.4126 | 6.8664 | 9.7197 | 15.6718 | 7.644 | 5.5762 | 9.7068 | 15.7512 | 5.8088 | 4.2374 | 9.4501 | 15.8454 | 3.9247 | 2.863 | 8.7936 | 15.9501 | 3.7573 | 2.7409 | 8.0108 | 16.0633 | 3.6563 | 2.6672 | 7.7073 | 16.186 | 3.5521 | 2.5912 | 7.4592 | 16.3256 | 3.378 | 2.4642 | 6.741 | 16.8787 | 3.1924 | 2.3288 | 5.1411 | 17.2747 | 5.7665 | 4.2066 | 4.2964 | 17.5093 | 10.1157 | 7.3793 | 4.1091 | 17.644 | 10.9902 | 8.0172 | 4.2764 | 15.4817 | 13.0481 | 9.5184 | 10.5593 | 15.5182 | 11.31 | 8.2505 | 10.5489 | 15.5769 | 9.4958 | 6.9271 | 10.0719 | 15.6394 | 7.751 | 5.6542 | 10.0668 | 15.7138 | 5.9481 | 4.3391 | 9.8581 | 15.7959 | 4.099 | 2.9901 | 9.2747 | 15.8859 | 3.9534 | 2.8839 | 8.5696 | 15.9817 | 3.9044 | 2.8482 | 8.3228 | 16.0831 | 3.853 | 2.8107 | 8.1292 | 16.1886 | 3.7333 | 2.7234 | 7.5555 | 16.4661 | 3.7246 | 2.7171 | 6.4309 | 16.6967 | 5.2477 | 3.8281 | 5.4474 | 16.8506 | 7.6787 | 5.6015 | 4.8255 | 16.9547 | 8.1317 | 5.932 | 4.3901 | 15.5115 | 13.045 | 9.5162 | 10.3586 | 15.5726 | 11.2911 | 8.2367 | 10.1797 | 15.6132 | 9.4582 | 6.8996 | 9.7441 | 15.6718 | 7.6838 | 5.6052 | 9.7358 | 15.7509 | 5.8661 | 4.2792 | 9.4887 | 15.8445 | 4.0059 | 2.9223 | 8.8462 | 15.9487 | 3.8458 | 2.8055 | 8.0783 | 16.0616 | 3.7643 | 2.746 | 7.7837 | 16.1827 | 3.6884 | 2.6906 | 7.5518 | 16.3157 | 3.5509 | 2.5903 | 6.885 | 16.8389 | 3.4327 | 2.5041 | 5.4529 | 17.2103 | 6.1347 | 4.4752 | 4.7137 | 17.432 | 10.4049 | 7.5902 | 4.5586 | 17.5628 | 11.2592 | 8.2135 | 4.7058 | 15.509 | 13.029 | 9.5045 | 10.3679 | 15.5709 | 11.2704 | 8.2216 | 10.2018 | 15.6206 | 9.4322 | 6.8807 | 9.7847 | 15.697 | 7.6363 | 5.5706 | 9.8008 | 15.8013 | 5.8178 | 4.244 | 9.602 | 15.9329 | 3.9201 | 2.8596 | 9.0115 | 16.0933 | 3.7336 | 2.7236 | 8.2747 | 16.2747 | 3.6024 | 2.6279 | 8.0177 | 16.4698 | 3.523 | 2.57 | 7.8774 | 16.6862 | 3.3633 | 2.4535 | 7.3528 | 17.5317 | 2.8767 | 2.0985 | 5.3678 | 18.6054 | 4.9156 | 3.5859 | 1.0384 | 18.9571 | 8.4869 | 6.1911 | -2.3109 | 19.1137 | 8.8588 | 6.4623 | -4.638 | 15.5067 | 13.0269 | 9.503 | 10.3443 | 15.5755 | 13.0002 | 9.4835 | 10.1189 | 15.6291 | 12.8835 | 9.3984 | 9.6816 | 15.705 | 12.7935 | 9.3327 | 9.7077 | 15.8113 | 12.6437 | 9.2234 | 9.5031 | 15.9372 | 12.3897 | 9.0381 | 8.936 | 16.0879 | 12.154 | 8.8662 | 8.2465 | 16.2525 | 11.9932 | 8.7489 | 8.0547 | 16.4516 | 11.9012 | 8.6818 | 7.8324 | 16.7739 | 11.6195 | 8.4762 | 6.5509 | 17.9 | 10.895 | 7.9477 | 1.7532 | 18.3925 | 9.9438 | 7.2539 | -2.0786 | 18.5623 | 9.3482 | 6.8194 | -4.2351 | 18.4958 | 9.2808 | 6.7702 | -3.6018
SPRING COTTAGE | NELSON | PADIHAM | 385446 | 437481 | -7.481 | -1.2135 | -0.88523 | -7.481 | -8.2239 | -1.334 | -0.97313 | -8.2239 | -8.7482 | -1.419 | -1.0352 | -8.7482 | -9.485 | -1.5386 | -1.1224 | -9.485 | -10.2105 | -1.6562 | -1.2082 | -10.2105 | -10.5851 | -1.717 | -1.2525 | -10.5851 | -11.2388 | -1.823 | -1.3299 | -11.2388 | -11.1816 | -1.8138 | -1.3231 | -11.1816 | -11.6221 | -1.8852 | -1.3752 | -11.6221 | -11.9915 | -1.9451 | -1.419 | -11.9915 | -14.5397 | -2.3585 | -1.7205 | -14.5397 | -17.6405 | -2.8615 | -2.0874 | -17.6405 | -16.9019 | -2.7417 | -2 | -16.9019 | -17.2225 | -2.7937 | -2.0379 | -17.2225 | -7.4454 | -1.2077 | -0.88102 | -7.4454 | -8.1592 | -1.3235 | -0.96548 | -8.1592 | -8.3093 | -1.3479 | -0.98324 | -8.3093 | -8.8407 | -1.434 | -1.0461 | -8.8407 | -9.7205 | -1.5768 | -1.1502 | -9.7205 | -9.8859 | -1.6036 | -1.1698 | -9.8859 | -10.2 | -1.6545 | -1.207 | -10.2 | -10.5269 | -1.7076 | -1.2456 | -10.5269 | -10.8878 | -1.7661 | -1.2883 | -10.8878 | -11.1545 | -1.8094 | -1.3199 | -11.1545 | -12.3482 | -2.003 | -1.4612 | -12.3482 | -12.7482 | -2.0679 | -1.5085 | -12.7482 | -15.2902 | -2.4802 | -1.8093 | -15.2902 | -14.09 | -2.2855 | -1.6673 | -14.09 | -7.4342 | -1.2059 | -0.87969 | -7.4342 | -8.0925 | -1.3127 | -0.95759 | -8.0925 | -8.4165 | -1.3652 | -0.99592 | -8.4165 | -9.2127 | -1.4944 | -1.0901 | -9.2127 | -9.835 | -1.5953 | -1.1638 | -9.835 | -10.5635 | -1.7135 | -1.25 | -10.5635 | -11.2594 | -1.8264 | -1.3323 | -11.2594 | -11.6114 | -1.8835 | -1.374 | -11.6114 | -11.8607 | -1.9239 | -1.4035 | -11.8607 | -12.1051 | -1.9636 | -1.4324 | -12.1051 | -13.5361 | -2.1957 | -1.6017 | -13.5361 | -15.3413 | -2.4885 | -1.8153 | -15.3413 | -15.4039 | -2.4987 | -1.8227 | -15.4039 | -15.9019 | -2.5794 | -1.8817 | -15.9019 | -7.4729 | -1.2122 | -0.88426 | -7.4729 | -8.3069 | -1.3475 | -0.98295 | -8.3069 | -8.8199 | -1.4307 | -1.0437 | -8.8199 | -9.5064 | -1.542 | -1.1249 | -9.5064 | -10.1971 | -1.6541 | -1.2066 | -10.1971 | -10.6472 | -1.7271 | -1.2599 | -10.6472 | -11.0387 | -1.7906 | -1.3062 | -11.0387 | -11.4719 | -1.8608 | -1.3575 | -11.4719 | -11.9498 | -1.9384 | -1.414 | -11.9498 | -12.4305 | -2.0164 | -1.4709 | -12.4305 | -15.9527 | -2.5877 | -1.8877 | -15.9527 | -20.0947 | -3.2596 | -2.3778 | -20.0947 | -22.4496 | -3.6415 | -2.6565 | -22.4496 | -24.2287 | -3.9301 | -2.867 | -24.2287 | -7.4592 | -1.21 | -0.88265 | -7.4592 | -7.7047 | -1.2498 | -0.9117 | -7.7047 | -8.0121 | -1.2996 | -0.94807 | -8.0121 | -8.327 | -1.3507 | -0.98533 | -8.327 | -8.8743 | -1.4395 | -1.0501 | -8.8743 | -9.1668 | -1.4869 | -1.0847 | -9.1668 | -9.9277 | -1.6104 | -1.1747 | -9.9277 | -10.858 | -1.7613 | -1.2848 | -10.858 | -11.6825 | -1.895 | -1.3824 | -11.6825 | -12.818 | -2.0792 | -1.5167 | -12.818 | -18.2185 | -2.9552 | -2.1558 | -18.2185 | -21.8974 | -3.552 | -2.5911 | -21.8974 | -23.6308 | -3.8331 | -2.7962 | -23.6308 | -23.5479 | -3.8197 | -2.7864 | -23.5479
SPRING GARDEN ST 11kV | LANCASTER | HEYSHAM | 347661 | 461494 | 39.514 | 9.3777 | 6.74 | 25.7529 | 39.5694 | 9.2555 | 6.6521 | 25.3553 | 39.6619 | 8.6322 | 6.2041 | 25.3814 | 39.7694 | 8.2964 | 5.9628 | 25.2222 | 39.8935 | 7.8048 | 5.6095 | 25.0252 | 40.028 | 7.5832 | 5.4502 | 24.7413 | 40.1762 | 7.368 | 5.2955 | 24.5181 | 40.3309 | 7.2585 | 5.2168 | 24.2665 | 40.4893 | 7.1319 | 5.1258 | 23.8913 | 40.4326 | 6.6569 | 4.7845 | 21.4665 | 37.7796 | 6.2201 | 4.4705 | 20.7131 | 35.8411 | 5.901 | 4.2411 | 19.8675 | 35.4951 | 5.844 | 4.2002 | 19.4106 | 35.2707 | 5.807 | 4.1736 | 19.4386 | 39.547 | 9.4621 | 6.8006 | 26.0072 | 39.6354 | 9.3006 | 6.6845 | 25.8432 | 39.7531 | 9.0659 | 6.5158 | 25.711 | 39.8782 | 9.097 | 6.5382 | 25.513 | 40.0175 | 9.0528 | 6.5064 | 25.2029 | 40.1744 | 8.9669 | 6.4447 | 24.8529 | 40.3497 | 8.8104 | 6.3322 | 24.4747 | 40.5397 | 8.6139 | 6.191 | 24.0693 | 40.7447 | 8.537 | 6.1357 | 23.5749 | 40.9636 | 8.4813 | 6.0957 | 23.159 | 41.2731 | 8.3654 | 6.0124 | 22.7198 | 41.4486 | 8.1601 | 5.8648 | 22.1838 | 41.5398 | 8.0978 | 5.8201 | 21.9644 | 41.5889 | 8.1415 | 5.8515 | 22.182 | 39.5141 | 9.4624 | 6.8008 | 25.7603 | 39.5694 | 9.3761 | 6.7388 | 25.3521 | 39.662 | 9.269 | 6.6618 | 25.3949 | 39.7695 | 9.1695 | 6.5903 | 25.2372 | 39.893 | 9.0423 | 6.4989 | 25.0506 | 40.0265 | 8.8903 | 6.3896 | 24.7776 | 40.174 | 8.7616 | 6.2971 | 24.5645 | 40.3283 | 8.6247 | 6.1987 | 24.3232 | 40.4842 | 8.4725 | 6.0894 | 23.9634 | 42.867 | 8.3334 | 5.9894 | 21.6246 | 43.188 | 7.9714 | 5.7292 | 20.9091 | 43.4951 | 7.6623 | 5.507 | 20.1512 | 43.9513 | 7.541 | 5.4199 | 19.7307 | 44.0526 | 7.5793 | 5.4474 | 19.7754 | 39.5152 | 9.3785 | 6.7405 | 25.7686 | 39.5714 | 9.2471 | 6.646 | 25.3818 | 39.6636 | 8.6483 | 6.2157 | 25.4161 | 39.7711 | 8.2578 | 5.935 | 25.2512 | 39.8944 | 7.8212 | 5.6212 | 25.0481 | 40.0277 | 7.5475 | 5.4245 | 24.7499 | 40.1743 | 7.3152 | 5.2575 | 24.4992 | 40.3263 | 7.183 | 5.1625 | 24.2123 | 40.479 | 7.0402 | 5.0599 | 23.817 | 39.9531 | 6.578 | 4.7277 | 21.5553 | 34.979 | 5.759 | 4.1391 | 19.1038 | 28.686 | 4.7229 | 3.3945 | 15.2632 | 24.7474 | 4.0745 | 2.9284 | 12.5127 | 22.4386 | 3.6943 | 2.6552 | 11.2492 | 39.5194 | 9.3794 | 6.7412 | 25.7659 | 39.59 | 9.243 | 6.6432 | 25.3458 | 39.6782 | 8.6865 | 6.2432 | 25.3775 | 39.7679 | 8.2195 | 5.9075 | 25.2147 | 39.8696 | 7.8054 | 5.6099 | 25.0219 | 40.5649 | 7.4273 | 5.3382 | 24.1514 | 40.7469 | 6.7087 | 4.8216 | 21.1542 | 39.042 | 6.428 | 4.6199 | 19.9914 | 38.3247 | 6.3099 | 4.535 | 19.7356 | 37.3181 | 6.1441 | 4.4159 | 19.3654 | 31.99 | 5.2669 | 3.7854 | 16.1235 | 25.3267 | 4.1698 | 2.997 | 12.5635 | 22.2015 | 3.6553 | 2.6271 | 10.4817 | 22.9335 | 3.7758 | 2.7138 | 11.8117
SPRING GARDEN ST 6.6KV | LANCASTER | HEYSHAM | 347651 | 461484 | 28.3638 | 8.7199 | 6.361 | 15.7039 | 28.3926 | 8.5995 | 6.2732 | 15.1584 | 28.4204 | 8.5632 | 6.2468 | 15.149 | 28.4567 | 8.1042 | 5.9119 | 15.0295 | 28.4997 | 7.7282 | 5.6376 | 14.8175 | 28.5475 | 7.342 | 5.3559 | 14.648 | 28.5997 | 7.131 | 5.202 | 14.4715 | 28.6555 | 7.0278 | 5.1267 | 14.2773 | 28.7154 | 6.9124 | 5.0425 | 13.9922 | 28.7869 | 6.8071 | 4.9657 | 13.8889 | 29.0429 | 6.304 | 4.5987 | 13.1888 | 29.2881 | 6.0632 | 4.423 | 12.6309 | 29.4697 | 6.0013 | 4.3779 | 12.4163 | 29.6321 | 5.9468 | 4.3381 | 12.5414 | 28.3771 | 8.7298 | 6.3683 | 16.0218 | 28.4223 | 8.6872 | 6.3372 | 15.7714 | 28.4774 | 8.5931 | 6.2685 | 15.6681 | 28.5343 | 8.5081 | 6.2065 | 15.4561 | 28.6018 | 8.4053 | 6.1316 | 15.2316 | 28.6785 | 8.2879 | 6.0459 | 14.9648 | 28.7648 | 8.1763 | 5.9645 | 14.7055 | 28.86 | 8.0691 | 5.8863 | 14.4219 | 28.9648 | 7.9579 | 5.8052 | 14.0631 | 29.0797 | 7.8151 | 5.701 | 13.5192 | 29.2266 | 7.6147 | 5.5548 | 13.1967 | 29.3639 | 7.3874 | 5.389 | 12.7591 | 29.4859 | 7.2514 | 5.2898 | 12.6147 | 29.5948 | 7.0891 | 5.1714 | 12.7293 | 28.3638 | 8.7269 | 6.3661 | 15.738 | 28.3927 | 8.6586 | 6.3163 | 15.184 | 28.4206 | 8.5355 | 6.2265 | 15.1866 | 28.4571 | 8.4103 | 6.1352 | 15.071 | 28.5002 | 8.2465 | 6.0157 | 14.8096 | 28.548 | 8.075 | 5.8906 | 14.7272 | 28.6003 | 7.9458 | 5.7964 | 14.5314 | 28.6562 | 7.8183 | 5.7033 | 14.339 | 28.7158 | 7.679 | 5.6017 | 14.1016 | 28.7855 | 7.5099 | 5.4784 | 13.971 | 29.0214 | 7.0759 | 5.1618 | 13.3047 | 29.2098 | 6.749 | 4.9233 | 12.8278 | 29.3628 | 6.7058 | 4.8918 | 12.6506 | 29.4766 | 6.5981 | 4.8132 | 12.8093 | 28.3632 | 8.7182 | 6.3598 | 15.7153 | 28.3946 | 8.5789 | 6.2582 | 15.179 | 28.4277 | 8.5765 | 6.2564 | 15.1752 | 28.4725 | 8.0503 | 5.8726 | 15.0575 | 28.5281 | 7.7021 | 5.6186 | 14.8361 | 28.5963 | 7.3421 | 5.3559 | 14.6598 | 28.6772 | 7.0982 | 5.178 | 14.4639 | 28.7683 | 6.9792 | 5.0912 | 14.2444 | 28.863 | 6.854 | 4.9999 | 13.9414 | 28.9684 | 6.7445 | 4.92 | 13.8377 | 29.4591 | 6.1302 | 4.4719 | 12.733 | 30.2072 | 5.4082 | 3.9452 | 10.2761 | 30.2444 | 4.9059 | 3.5788 | 8.3314 | 28.0013 | 4.5421 | 3.3134 | 7.2298 | 28.3531 | 8.7202 | 6.3613 | 15.7271 | 28.3762 | 8.5344 | 6.2257 | 15.1879 | 28.401 | 8.5422 | 6.2314 | 15.1939 | 28.436 | 7.9247 | 5.781 | 15.0938 | 28.481 | 7.6493 | 5.5801 | 14.8637 | 28.5389 | 7.269 | 5.3027 | 14.7437 | 28.6114 | 6.9807 | 5.0923 | 14.5719 | 28.6943 | 6.8424 | 4.9914 | 14.3711 | 28.7981 | 6.6863 | 4.8775 | 14.0794 | 29.0074 | 6.458 | 4.711 | 13.5692 | 29.8178 | 5.6743 | 4.1393 | 10.9378 | 29.1056 | 4.7212 | 3.4441 | 8.4339 | 26.491 | 4.2971 | 3.1347 | 7.0838 | 26.6711 | 4.3263 | 3.156 | 7.8008
SQUIRES GATE | BLACKPOOL | PENWORTHAM WEST / STANAH | 332037 | 432063 | 17.7538 | 2.8798 | 2.1008 | 14.6973 | 17.0278 | 2.7621 | 2.0149 | 14.1383 | 16.7239 | 2.7128 | 1.9789 | 14.0907 | 16.2439 | 2.6349 | 1.9221 | 13.8683 | 15.4712 | 2.5096 | 1.8307 | 13.7037 | 14.1242 | 2.2911 | 1.6713 | 13.4394 | 12.3228 | 1.9989 | 1.4582 | 12.3228 | 12.7885 | 2.0744 | 1.5133 | 12.7885 | 12.9499 | 2.1006 | 1.5324 | 12.6927 | 12.6111 | 2.0456 | 1.4923 | 12.4557 | 12.2569 | 1.9882 | 1.4504 | 10.9007 | 25.3241 | 4.1078 | 2.9966 | 9.9419 | 26.0551 | 7.5422 | 5.5019 | 9.6822 | 26.475 | 8.511 | 6.2087 | 9.6748 | 18.1699 | 2.9473 | 2.15 | 15.1399 | 17.8009 | 2.8875 | 2.1064 | 14.9605 | 17.5203 | 2.842 | 2.0732 | 14.8475 | 17.0441 | 2.7647 | 2.0168 | 14.5352 | 16.2436 | 2.6349 | 1.9221 | 14.3053 | 15.9359 | 2.585 | 1.8857 | 14.0024 | 15.2661 | 2.4763 | 1.8064 | 13.6582 | 14.4601 | 2.3456 | 1.7111 | 13.0306 | 13.4156 | 2.1761 | 1.5875 | 12.3408 | 12.1643 | 1.9732 | 1.4394 | 11.5465 | 11.3219 | 1.8365 | 1.3397 | 10.7513 | 22.1357 | 3.5906 | 2.6193 | 10.2718 | 24.5715 | 6.1999 | 4.5228 | 10.0911 | 24.9172 | 6.8894 | 5.0257 | 10.0704 | 18.162 | 2.946 | 2.1491 | 14.7191 | 17.6728 | 2.8667 | 2.0912 | 14.1709 | 15.7719 | 2.5584 | 1.8663 | 14.1218 | 16.1921 | 2.6265 | 1.916 | 13.9233 | 16.4446 | 2.6675 | 1.9459 | 13.7634 | 15.9439 | 2.5862 | 1.8866 | 13.5184 | 15.3194 | 2.485 | 1.8127 | 13.3456 | 14.6921 | 2.3832 | 1.7385 | 13.0884 | 13.6581 | 2.2155 | 1.6162 | 12.822 | 12.696 | 2.0594 | 1.5023 | 12.6482 | 13.0789 | 2.1215 | 1.5476 | 11.1586 | 25.1842 | 4.3694 | 3.1874 | 10.4403 | 25.6496 | 7.9943 | 5.8318 | 10.2797 | 25.9656 | 8.7947 | 6.4156 | 10.4053 | 17.78 | 2.8841 | 2.1039 | 14.7234 | 17.056 | 2.7666 | 2.0182 | 14.1944 | 15.4277 | 2.5025 | 1.8256 | 14.1787 | 15.9892 | 2.5936 | 1.892 | 13.9902 | 15.9699 | 2.5905 | 1.8897 | 13.8618 | 15.8342 | 2.5685 | 1.8737 | 13.6328 | 15.398 | 2.4977 | 1.822 | 13.4856 | 15.136 | 2.4552 | 1.791 | 13.2455 | 14.5296 | 2.3568 | 1.7193 | 12.9879 | 13.9312 | 2.2598 | 1.6485 | 12.8282 | 11.1573 | 1.8098 | 1.3202 | 10.5789 | 19.257 | 3.1237 | 2.2787 | 6.6621 | 27.6776 | 6.124 | 4.4674 | 3.8614 | 27.6743 | 6.6805 | 4.8733 | 2.1303 | 17.7719 | 2.8828 | 2.1029 | 14.7106 | 17.0762 | 2.7699 | 2.0206 | 14.1514 | 16.5815 | 2.6897 | 1.9621 | 14.1328 | 15.8382 | 2.5691 | 1.8741 | 13.9663 | 14.2597 | 2.3131 | 1.6873 | 13.8608 | 14.2689 | 2.3146 | 1.6884 | 13.6646 | 14.232 | 2.3086 | 1.6841 | 13.5299 | 14.8594 | 2.4103 | 1.7583 | 13.3155 | 15.4049 | 2.4988 | 1.8229 | 13.0853 | 15.7135 | 2.5489 | 1.8594 | 12.2738 | 26.2961 | 8.3396 | 6.0836 | 7.8012 | 27.233 | 7.0384 | 5.1344 | 4.3868 | 27.5714 | 6.5831 | 4.8023 | 2.5596 | 27.1747 | 6.5724 | 4.7945 | 3.0057
ST ANNES | LYTHAM | PENWORTHAM WEST / STANAH | 331716 | 429849 | 23.0184 | 10.7745 | 7.8598 | 13.7699 | 23.0651 | 10.6744 | 7.7869 | 13.5322 | 23.0812 | 10.6088 | 7.739 | 13.4198 | 23.1178 | 10.4698 | 7.6376 | 13.3223 | 23.1677 | 10.2789 | 7.4983 | 13.1622 | 23.2285 | 10.0204 | 7.3097 | 12.9488 | 23.2927 | 9.8995 | 7.2215 | 12.765 | 23.3568 | 9.7568 | 7.1174 | 12.5758 | 23.4238 | 9.6675 | 7.0523 | 12.3939 | 23.4967 | 9.5916 | 6.997 | 12.1576 | 23.8219 | 9.329 | 6.8053 | 11.3506 | 24.0756 | 9.0448 | 6.598 | 10.8192 | 24.2297 | 8.7273 | 6.3664 | 10.5824 | 24.3438 | 8.6593 | 6.3168 | 10.411 | 22.9792 | 10.8267 | 7.8979 | 13.9065 | 22.9947 | 10.7635 | 7.8518 | 13.7855 | 23.0259 | 10.6871 | 7.7961 | 13.6253 | 23.0683 | 10.6319 | 7.7558 | 13.5135 | 23.1159 | 10.6024 | 7.7343 | 13.3554 | 23.1671 | 10.5685 | 7.7096 | 13.1562 | 23.2223 | 10.5008 | 7.6602 | 12.9803 | 23.2796 | 10.4293 | 7.608 | 12.7961 | 23.3381 | 10.4056 | 7.5908 | 12.6168 | 23.3957 | 10.3443 | 7.546 | 12.4013 | 23.5781 | 10.1531 | 7.4066 | 11.814 | 23.7338 | 9.9874 | 7.2857 | 11.3572 | 23.8535 | 9.8577 | 7.191 | 11.0903 | 23.9396 | 9.6577 | 7.0452 | 10.8632 | 23.0184 | 10.8249 | 7.8966 | 13.7723 | 23.0652 | 10.6141 | 7.7428 | 13.5457 | 23.0814 | 10.3747 | 7.5682 | 13.4444 | 23.1182 | 10.0591 | 7.338 | 13.3526 | 23.168 | 10.0046 | 7.2982 | 13.1995 | 23.2286 | 10.0298 | 7.3166 | 12.9934 | 23.2927 | 9.9377 | 7.2494 | 12.8164 | 23.3568 | 9.861 | 7.1934 | 12.6338 | 23.4231 | 9.7674 | 7.1252 | 12.4612 | 23.4927 | 9.6833 | 7.0639 | 12.2452 | 23.7924 | 9.3376 | 6.8117 | 11.5182 | 24.0007 | 9.0253 | 6.5839 | 11.0673 | 24.1317 | 8.8363 | 6.446 | 10.8673 | 24.2186 | 8.7486 | 6.382 | 10.7282 | 23.0144 | 10.7741 | 7.8596 | 13.7816 | 23.0589 | 10.6792 | 7.7904 | 13.5519 | 23.078 | 10.5586 | 7.7024 | 13.4435 | 23.1239 | 10.3026 | 7.5156 | 13.3444 | 23.182 | 10.015 | 7.3058 | 13.1847 | 23.2561 | 9.9326 | 7.2457 | 12.9616 | 23.3431 | 9.9132 | 7.2315 | 12.7554 | 23.4402 | 9.8422 | 7.1798 | 12.5386 | 23.5455 | 9.7609 | 7.1204 | 12.3388 | 23.6622 | 9.6465 | 7.037 | 12.0997 | 24.0818 | 9.1077 | 6.6439 | 10.9424 | 24.4758 | 8.387 | 6.1182 | 8.9589 | 24.6792 | 7.8505 | 5.7268 | 7.4391 | 24.7675 | 7.3888 | 5.3901 | 6.0237 | 23.0151 | 10.7741 | 7.8595 | 13.7762 | 23.068 | 10.6804 | 7.7912 | 13.5299 | 23.093 | 10.5529 | 7.6982 | 13.4161 | 23.1363 | 10.4342 | 7.6116 | 13.3191 | 23.1946 | 10.1845 | 7.4295 | 13.1635 | 23.2679 | 9.8314 | 7.1718 | 12.9522 | 23.3558 | 9.6983 | 7.0747 | 12.7592 | 23.4484 | 9.68 | 7.0614 | 12.561 | 23.548 | 9.6193 | 7.0171 | 12.3392 | 23.6739 | 9.4891 | 6.9222 | 11.8096 | 24.123 | 8.8472 | 6.4539 | 9.5314 | 24.4206 | 8.1848 | 5.9707 | 7.6667 | 24.5077 | 7.727 | 5.6368 | 6.3558 | 24.4485 | 7.6834 | 5.6049 | 6.5764
ST MARYS | GREENHILL | WHITEGATE | 392582 | 405316 | 30.1156 | 11.3851 | 8.3053 | 18.3192 | 30.1871 | 9.9458 | 7.2554 | 18.0789 | 30.1963 | 8.5064 | 6.2053 | 18.0258 | 30.2216 | 7.0627 | 5.1521 | 18.0105 | 30.2566 | 5.631 | 4.1077 | 17.8422 | 26.4215 | 4.2858 | 3.1265 | 17.7185 | 26.0654 | 4.2281 | 3.0843 | 17.5875 | 25.6048 | 4.1534 | 3.0298 | 17.4474 | 25.0893 | 4.0697 | 2.9688 | 17.2691 | 24.7356 | 4.0124 | 2.927 | 17.0934 | 24.4175 | 3.9608 | 2.8893 | 16.3924 | 30.844 | 5.6504 | 4.1219 | 15.8414 | 30.9574 | 9.1101 | 6.6457 | 15.5094 | 31.0415 | 9.6092 | 7.0098 | 15.4406 | 30.0634 | 11.3847 | 8.3049 | 18.5368 | 30.0929 | 9.9246 | 7.2399 | 18.4786 | 30.1356 | 8.436 | 6.154 | 18.3227 | 30.1846 | 6.9506 | 5.0704 | 18.2326 | 30.2389 | 5.5308 | 4.0346 | 18.01 | 25.5224 | 4.14 | 3.0201 | 17.8508 | 25.1547 | 4.0803 | 2.9766 | 17.671 | 24.7887 | 4.021 | 2.9332 | 17.4718 | 24.3631 | 3.9519 | 2.8829 | 17.2306 | 23.9279 | 3.8813 | 2.8314 | 16.9745 | 23.8477 | 3.8683 | 2.8219 | 16.5483 | 30.7102 | 4.9815 | 3.6339 | 16.0216 | 30.9634 | 7.2356 | 5.2783 | 15.6101 | 31.026 | 8.0868 | 5.8992 | 15.3681 | 30.1156 | 11.3823 | 8.3032 | 18.327 | 30.1872 | 9.928 | 7.2423 | 18.0942 | 30.1965 | 8.3445 | 6.0872 | 18.0495 | 30.2219 | 6.8986 | 5.0324 | 18.0415 | 30.2569 | 5.4472 | 3.9737 | 17.883 | 24.2771 | 3.938 | 2.8727 | 17.7678 | 24.108 | 3.9105 | 2.8527 | 17.6457 | 23.7869 | 3.8585 | 2.8147 | 17.5148 | 23.3621 | 3.7896 | 2.7644 | 17.3497 | 22.8981 | 3.7143 | 2.7095 | 17.1974 | 22.9732 | 3.7265 | 2.7184 | 16.567 | 30.7949 | 5.5774 | 4.0686 | 16.0946 | 30.8911 | 9.2947 | 6.7803 | 15.8118 | 30.9462 | 9.8863 | 7.2119 | 15.7628 | 30.1106 | 11.3878 | 8.3072 | 18.3309 | 30.1772 | 9.9552 | 7.2622 | 18.1013 | 30.1833 | 8.5033 | 6.203 | 18.0579 | 30.2071 | 7.0517 | 5.1441 | 18.0516 | 30.2426 | 5.6398 | 4.1142 | 17.8879 | 26.3492 | 4.2741 | 3.1179 | 17.7569 | 25.9246 | 4.2052 | 3.0677 | 17.5848 | 25.3781 | 4.1166 | 3.003 | 17.4004 | 25.0503 | 4.0634 | 2.9642 | 17.1916 | 24.4538 | 3.9667 | 2.8936 | 17.0272 | 23.6777 | 3.8408 | 2.8018 | 16.1923 | 30.9856 | 5.2131 | 3.8029 | 14.7148 | 31.0841 | 8.3605 | 6.0989 | 13.6637 | 31.1022 | 8.6627 | 6.3193 | 12.855 | 30.102 | 11.3915 | 8.3099 | 18.3405 | 30.1615 | 11.3531 | 8.2819 | 18.1156 | 30.1604 | 11.2982 | 8.2419 | 18.0811 | 30.1761 | 11.2088 | 8.1767 | 18.0794 | 30.2057 | 11.0514 | 8.0618 | 17.894 | 30.2493 | 10.9658 | 7.9994 | 17.7549 | 30.2999 | 10.8668 | 7.9272 | 17.6025 | 30.354 | 10.8122 | 7.8874 | 17.4411 | 30.4113 | 10.6909 | 7.7989 | 17.2523 | 30.4781 | 10.5294 | 7.681 | 16.898 | 30.7345 | 9.7662 | 7.1243 | 15.2302 | 30.9077 | 9.0516 | 6.603 | 13.9002 | 30.9486 | 8.6461 | 6.3072 | 13.0869 | 30.9031 | 8.5222 | 6.2168 | 13.2671
ST MARYS ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 354932 | 429640 | 23.9934 | 12.3612 | 9.0174 | 10.743 | 24.0443 | 12.2347 | 8.9251 | 10.4592 | 24.0532 | 12.0971 | 8.8247 | 10.511 | 24.0952 | 11.8052 | 8.6117 | 10.2173 | 24.155 | 11.7441 | 8.5672 | 10.2538 | 24.2379 | 11.8386 | 8.6361 | 9.9933 | 24.3345 | 11.6882 | 8.5264 | 9.8515 | 24.4423 | 11.3607 | 8.2874 | 9.7403 | 24.5607 | 11.4946 | 8.3851 | 9.4846 | 24.6905 | 11.4652 | 8.3637 | 9.1999 | 25.2616 | 11.206 | 8.1746 | 8.5314 | 25.7109 | 10.8751 | 7.9332 | 8.054 | 26.0151 | 10.4162 | 7.5985 | 7.76 | 26.2227 | 10.5054 | 7.6635 | 7.7984 | 23.9606 | 12.3932 | 9.0406 | 10.8957 | 23.9876 | 12.2025 | 8.9015 | 10.6837 | 24.0401 | 12.0474 | 8.7884 | 10.6568 | 24.1185 | 12.1407 | 8.8565 | 10.275 | 24.2097 | 12.1803 | 8.8853 | 10.301 | 24.3166 | 12.1193 | 8.8409 | 9.9626 | 24.4397 | 12.0431 | 8.7853 | 9.7675 | 24.5764 | 11.9529 | 8.7195 | 9.5927 | 24.7274 | 11.8054 | 8.6119 | 9.2596 | 24.8424 | 11.5745 | 8.4434 | 8.9113 | 25.1749 | 11.7467 | 8.5691 | 8.4223 | 25.4576 | 11.65 | 8.4985 | 7.9724 | 25.6425 | 11.5353 | 8.4148 | 7.6025 | 25.7566 | 11.4801 | 8.3746 | 7.5012 | 23.9983 | 12.3846 | 9.0344 | 10.7529 | 24.0507 | 12.0467 | 8.7879 | 10.4881 | 24.0608 | 12.2232 | 8.9167 | 10.5508 | 24.1033 | 12.1262 | 8.8459 | 10.2782 | 24.1631 | 11.8888 | 8.6727 | 10.332 | 24.243 | 12.009 | 8.7604 | 10.0819 | 24.3345 | 12.0197 | 8.7682 | 9.9541 | 24.4351 | 11.9864 | 8.7439 | 9.8565 | 24.5437 | 11.8973 | 8.6789 | 9.6211 | 24.6599 | 11.7801 | 8.5934 | 9.3663 | 25.2012 | 11.4826 | 8.3764 | 8.7738 | 25.5228 | 11.2955 | 8.2399 | 8.3937 | 25.7165 | 11.1085 | 8.1035 | 8.1612 | 25.8235 | 10.7177 | 7.8184 | 8.2491 | 23.9949 | 12.3621 | 9.018 | 10.7573 | 24.043 | 12.2294 | 8.9211 | 10.4804 | 24.0515 | 12.0126 | 8.7631 | 10.5473 | 24.0971 | 11.6997 | 8.5348 | 10.2489 | 24.1643 | 11.8657 | 8.6559 | 10.2944 | 24.2667 | 11.7962 | 8.6051 | 10.0193 | 24.3957 | 11.5089 | 8.3956 | 9.8574 | 24.5472 | 11.5551 | 8.4293 | 9.7224 | 24.7191 | 11.5199 | 8.4036 | 9.4591 | 24.9107 | 11.499 | 8.3884 | 9.1907 | 25.5762 | 10.9936 | 8.0197 | 8.1771 | 26.3822 | 10.1549 | 7.4079 | 5.9091 | 26.9197 | 9.5676 | 6.9794 | 4.1295 | 27.071 | 9.2714 | 6.7634 | 3.1468 | 23.9861 | 12.3651 | 9.0202 | 10.7735 | 24.0302 | 12.2522 | 8.9378 | 10.5182 | 24.0373 | 12.0666 | 8.8024 | 10.5822 | 24.0793 | 11.6768 | 8.5181 | 10.3332 | 24.1438 | 11.8172 | 8.6205 | 10.3711 | 24.2545 | 11.7437 | 8.5669 | 10.1561 | 24.4054 | 11.7628 | 8.5808 | 10.0339 | 24.5877 | 11.6684 | 8.5119 | 9.9014 | 24.7575 | 11.5699 | 8.4401 | 9.6584 | 24.9374 | 11.41 | 8.3234 | 9.0161 | 25.6979 | 10.5512 | 7.697 | 6.5206 | 26.3811 | 9.6115 | 7.0115 | 4.4873 | 26.766 | 9.1056 | 6.6424 | 3.2848 | 26.6216 | 9.1715 | 6.6905 | 3.8429
ST THOMAS RD | LYTHAM | PENWORTHAM WEST / STANAH | 332713 | 428643 | 30.0398 | 13.8926 | 10.1345 | 18.0914 | 30.0894 | 13.6123 | 9.93 | 17.8016 | 30.1243 | 13.2988 | 9.7013 | 17.6688 | 30.1848 | 13.3046 | 9.7055 | 17.3631 | 30.2585 | 13.104 | 9.5592 | 17.1574 | 30.3438 | 13.1644 | 9.6033 | 16.8383 | 30.4367 | 13.0617 | 9.5283 | 16.5576 | 30.535 | 12.9395 | 9.4392 | 16.2459 | 30.639 | 12.7919 | 9.3315 | 15.9333 | 30.7519 | 12.6339 | 9.2163 | 15.5541 | 31.1088 | 12.0063 | 8.7584 | 14.2851 | 31.3473 | 11.5611 | 8.4336 | 13.4909 | 31.4979 | 11.3453 | 8.2763 | 13.1374 | 31.591 | 11.1867 | 8.1605 | 13.0843 | 30.0401 | 13.8911 | 10.1333 | 18.1246 | 30.098 | 13.83 | 10.0888 | 17.8502 | 30.1755 | 13.7465 | 10.0278 | 17.6285 | 30.2728 | 13.6304 | 9.9432 | 17.2964 | 30.3818 | 13.552 | 9.886 | 17.0842 | 30.503 | 13.4321 | 9.7985 | 16.7017 | 30.629 | 13.298 | 9.7007 | 16.3603 | 30.7362 | 13.2288 | 9.6502 | 16.0082 | 30.8511 | 13.1502 | 9.5929 | 15.5873 | 30.9736 | 13.0675 | 9.5325 | 15.1583 | 31.1489 | 12.8377 | 9.365 | 14.2538 | 31.2886 | 12.6494 | 9.2276 | 13.4173 | 31.3827 | 12.5457 | 9.1519 | 12.857 | 31.4437 | 12.4742 | 9.0997 | 12.3998 | 30.0398 | 13.8845 | 10.1286 | 18.0965 | 30.0894 | 13.7362 | 10.0203 | 17.8412 | 30.1243 | 13.7515 | 10.0315 | 17.73 | 30.1848 | 13.5713 | 9.9001 | 17.4558 | 30.2583 | 13.2347 | 9.6545 | 17.2426 | 30.3432 | 13.1153 | 9.5674 | 16.9775 | 30.4357 | 12.9888 | 9.4751 | 16.6854 | 30.5338 | 12.8611 | 9.382 | 16.3948 | 30.6367 | 12.724 | 9.282 | 16.1084 | 30.7452 | 12.5816 | 9.1781 | 15.7736 | 31.0853 | 11.9859 | 8.7436 | 14.6351 | 31.3085 | 11.8453 | 8.641 | 13.9316 | 31.4505 | 11.6026 | 8.4639 | 13.6042 | 31.5404 | 11.379 | 8.3008 | 13.5144 | 30.037 | 13.891 | 10.1333 | 18.096 | 30.0861 | 13.6053 | 9.9249 | 17.8033 | 30.1265 | 13.5044 | 9.8513 | 17.6688 | 30.2005 | 13.4375 | 9.8024 | 17.3527 | 30.2962 | 13.3432 | 9.7337 | 17.1385 | 30.4127 | 13.069 | 9.5336 | 16.7789 | 30.5479 | 12.8782 | 9.3945 | 16.4296 | 30.6975 | 12.6872 | 9.2552 | 16.0645 | 30.8488 | 12.4699 | 9.0966 | 15.7156 | 31.0026 | 12.192 | 8.8939 | 15.3564 | 31.4385 | 11.6468 | 8.4962 | 13.5851 | 31.7826 | 10.6495 | 7.7686 | 10.1498 | 31.9273 | 9.9525 | 7.2602 | 7.6568 | 31.9963 | 9.4171 | 6.8697 | 5.8628 | 30.0241 | 13.895 | 10.1362 | 18.1195 | 30.067 | 13.5893 | 9.9132 | 17.8356 | 30.0993 | 13.3271 | 9.7219 | 17.7215 | 30.1591 | 13.3039 | 9.705 | 17.4373 | 30.2399 | 13.1751 | 9.6111 | 17.2173 | 30.3358 | 13.0593 | 9.5266 | 16.915 | 30.4492 | 12.9064 | 9.415 | 16.6134 | 30.571 | 12.7347 | 9.2898 | 16.3005 | 30.6898 | 12.5504 | 9.1554 | 15.9897 | 30.8332 | 12.2616 | 8.9446 | 15.1157 | 31.2858 | 11.0318 | 8.0475 | 11.1152 | 31.5489 | 9.9587 | 7.2648 | 7.9767 | 31.6086 | 9.4739 | 6.911 | 6.248 | 31.5326 | 9.4064 | 6.8618 | 6.6925
STAINBURN | STAINBURN & SIDDICK | HARKER / HUTTON | 302535 | 529330 | 12.7225 | 12.7225 | 12.0803 | 10.8698 | 12.7559 | 12.7559 | 11.067 | 10.4703 | 12.7858 | 12.7858 | 10.1076 | 10.5612 | 12.8316 | 12.6719 | 9.1075 | 10.3766 | 12.8944 | 11.3054 | 8.1254 | 10.2155 | 12.9701 | 9.8165 | 7.0553 | 9.8967 | 13.0587 | 9.7576 | 7.013 | 9.4983 | 13.1569 | 9.8107 | 7.0511 | 9.1069 | 13.2626 | 9.7289 | 6.9923 | 8.7226 | 13.3815 | 9.6914 | 6.9654 | 8.2478 | 13.8853 | 9.4394 | 6.7843 | 6.6507 | 14.2307 | 9.8888 | 7.1073 | 5.9876 | 14.4304 | 14.4304 | 11.0747 | 5.9638 | 14.531 | 14.531 | 11.0131 | 6.3002 | 12.7045 | 12.7045 | 12.0924 | 11.0012 | 12.7237 | 12.7237 | 11.0766 | 10.7197 | 12.7614 | 12.7614 | 10.0707 | 10.7731 | 12.803 | 12.6379 | 9.0831 | 10.6054 | 12.8517 | 11.2996 | 8.1212 | 10.4811 | 12.906 | 9.9102 | 7.1226 | 10.2361 | 12.9672 | 9.8613 | 7.0875 | 9.9475 | 13.0332 | 9.7864 | 7.0337 | 9.655 | 13.1031 | 9.7089 | 6.978 | 9.3632 | 13.1757 | 9.6944 | 6.9675 | 9.0486 | 13.3755 | 9.4495 | 6.7915 | 8.0022 | 13.5275 | 9.1977 | 6.6106 | 7.3239 | 13.6321 | 12.2981 | 8.8389 | 6.984 | 13.7018 | 13.7018 | 11.1337 | 6.8287 | 12.7225 | 12.7225 | 12.0899 | 10.8724 | 12.756 | 12.756 | 11.0441 | 10.4818 | 12.7859 | 12.7859 | 10.0907 | 10.5783 | 12.8318 | 12.6899 | 9.1205 | 10.4007 | 12.8944 | 11.3097 | 8.1285 | 10.2488 | 12.9696 | 9.8844 | 7.1041 | 9.9434 | 13.0577 | 9.7966 | 7.041 | 9.557 | 13.1557 | 9.6964 | 6.969 | 9.1766 | 13.2598 | 9.5203 | 6.8425 | 8.8094 | 13.3721 | 9.3862 | 6.746 | 8.3789 | 13.8391 | 9.1254 | 6.5586 | 6.9555 | 14.1501 | 9.4481 | 6.7906 | 6.4107 | 14.3321 | 14.3321 | 10.8807 | 6.4261 | 14.4126 | 14.4126 | 10.7361 | 6.7601 | 12.7208 | 12.7208 | 12.081 | 10.8791 | 12.7555 | 12.7555 | 11.0707 | 10.4837 | 12.7944 | 12.7944 | 10.1115 | 10.5739 | 12.8576 | 12.6149 | 9.0666 | 10.3868 | 12.9484 | 11.154 | 8.0166 | 10.2252 | 13.0642 | 9.8983 | 7.1141 | 9.9133 | 13.2083 | 9.8832 | 7.1033 | 9.624 | 13.3761 | 9.8211 | 7.0586 | 9.2848 | 13.5574 | 9.7092 | 6.9782 | 8.9854 | 13.73 | 9.4161 | 6.7675 | 8.6638 | 14.3622 | 9.294 | 6.6798 | 7.0632 | 14.9065 | 9.0882 | 6.5319 | 4.6363 | 15.1548 | 14.3661 | 10.3252 | 3.0504 | 15.2841 | 13.9994 | 10.0617 | 2.005 | 12.719 | 12.719 | 12.0806 | 10.8712 | 12.7619 | 12.7619 | 12.03 | 10.4441 | 12.8099 | 12.8099 | 12.0011 | 10.5174 | 12.8772 | 12.8772 | 11.9104 | 10.3241 | 12.9711 | 12.9711 | 11.9814 | 10.157 | 13.0842 | 13.0842 | 11.9696 | 9.8572 | 13.253 | 13.253 | 11.9058 | 9.5636 | 13.4108 | 13.4108 | 11.7445 | 9.2767 | 13.586 | 13.586 | 11.7993 | 8.9783 | 13.7924 | 13.7924 | 11.6196 | 8.3156 | 14.4055 | 14.4055 | 11.2314 | 5.3625 | 14.7326 | 14.7326 | 10.702 | 3.366 | 14.8245 | 14.5038 | 10.4242 | 2.4408 | 14.7746 | 14.4244 | 10.3671 | 2.9377
STANDISH | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 356139 | 410059 | 17.7903 | 13.2221 | 9.503 | 10.6765 | 17.879 | 10.9181 | 7.8471 | 10.212 | 17.9247 | 8.8514 | 6.3617 | 9.9724 | 18.0067 | 6.8058 | 4.8915 | 9.5986 | 18.1185 | 4.6065 | 3.3107 | 9.2126 | 15.2027 | 2.503 | 1.799 | 8.467 | 13.8839 | 2.2859 | 1.6429 | 7.7082 | 12.4616 | 2.0517 | 1.4746 | 6.8973 | 10.9482 | 1.8025 | 1.2955 | 6.1465 | 9.4979 | 1.5638 | 1.1239 | 5.189 | 7.2504 | 1.1937 | 0.85795 | 1.9878 | 6.3179 | 1.0402 | 0.74761 | 0.49974 | 6.2715 | 1.0326 | 0.74211 | 0.43973 | 6.208 | 1.0221 | 0.7346 | 1.008 | 17.7271 | 13.3898 | 9.6235 | 11.0933 | 17.7653 | 13.3894 | 9.6232 | 10.9791 | 17.8416 | 13.2139 | 9.4971 | 10.6405 | 17.9284 | 12.8857 | 9.2612 | 10.2795 | 18.028 | 12.7354 | 9.1532 | 9.9811 | 18.1392 | 12.6135 | 9.0656 | 9.4418 | 18.2631 | 12.4859 | 8.9738 | 8.8734 | 18.3954 | 12.3446 | 8.8723 | 8.2565 | 18.536 | 12.1729 | 8.7489 | 7.6485 | 18.6822 | 12.0423 | 8.6551 | 7.0031 | 19.1017 | 11.446 | 8.2265 | 5.0159 | 19.4813 | 11.3892 | 8.1856 | 3.7046 | 19.8148 | 11.5482 | 8.2999 | 3.0594 | 20.0767 | 11.6376 | 8.3642 | 2.7169 | 17.7904 | 13.4025 | 9.6326 | 10.684 | 17.8793 | 11.3128 | 8.1307 | 10.2349 | 17.9254 | 9.198 | 6.6108 | 10.0142 | 18.0079 | 7.0387 | 5.0588 | 9.6662 | 18.1199 | 5.1184 | 3.6787 | 9.272 | 18.2575 | 3.3562 | 2.4122 | 8.5503 | 18.4137 | 3.233 | 2.3236 | 7.8147 | 18.5839 | 3.1407 | 2.2573 | 7.0262 | 18.4669 | 3.0404 | 2.1852 | 6.3037 | 17.6719 | 2.9095 | 2.0911 | 5.4307 | 14.4379 | 2.3771 | 1.7085 | 2.5589 | 10.8727 | 1.7901 | 1.2866 | 1.3322 | 11.4346 | 1.8826 | 1.3531 | 1.344 | 11.2672 | 1.8551 | 1.3333 | 1.9341 | 17.7847 | 13.2222 | 9.503 | 10.7045 | 17.8741 | 10.8888 | 7.826 | 10.2484 | 17.9331 | 8.8731 | 6.3773 | 10.0095 | 18.0386 | 6.6183 | 4.7567 | 9.6463 | 18.1908 | 4.5734 | 3.287 | 9.3154 | 13.7749 | 2.2679 | 1.63 | 8.7136 | 12.4163 | 2.0442 | 1.4692 | 7.9971 | 12.1346 | 1.9979 | 1.4359 | 7.2264 | 11.7307 | 1.9314 | 1.3881 | 6.6055 | 10.9623 | 1.8049 | 1.2972 | 5.9337 | 6.9725 | 1.148 | 0.82507 | 2.6375 | 2.6844 | 0.44197 | 0.31765 | -3.1133 | 2.6844 | 0.44197 | 0.31765 | -7.0289 | 2.6844 | 0.44197 | 0.31765 | -10.04 | 17.7812 | 13.2217 | 9.5027 | 10.7009 | 17.883 | 10.9413 | 7.8637 | 10.2089 | 17.9536 | 8.9346 | 6.4215 | 9.9534 | 18.0632 | 6.8655 | 4.9344 | 9.59 | 18.2176 | 4.7391 | 3.4061 | 9.2647 | 16.0525 | 2.6429 | 1.8995 | 8.6629 | 14.5153 | 2.3898 | 1.7176 | 8.0408 | 12.9744 | 2.1361 | 1.5353 | 7.4102 | 11.2622 | 1.8542 | 1.3327 | 6.8292 | 10.6221 | 1.7488 | 1.2569 | 5.3845 | 6.9652 | 1.1468 | 0.8242 | -1.1991 | 2.6844 | 0.44197 | 0.31765 | -5.9505 | 2.6844 | 0.44197 | 0.31765 | -8.4217 | 2.6844 | 0.44197 | 0.31765 | -7.4951
STRANGEWAYS | RED BANK | KEARSLEY | 383780 | 399743 | 33.8335 | 10.3041 | 7.5167 | 15.7109 | 33.9179 | 10.1722 | 7.4205 | 15.3444 | 33.9349 | 10.0691 | 7.3453 | 15.1055 | 33.9832 | 9.9788 | 7.2794 | 15.0637 | 34.05 | 9.8388 | 7.1772 | 14.7491 | 34.1357 | 9.6672 | 7.0521 | 14.448 | 34.2289 | 9.4936 | 6.9255 | 14.288 | 34.3272 | 9.3715 | 6.8364 | 14.014 | 34.43 | 9.3098 | 6.7914 | 13.6506 | 34.5408 | 9.1707 | 6.6899 | 13.3142 | 34.959 | 8.8855 | 6.4819 | 12.2313 | 35.2751 | 8.5454 | 6.2337 | 11.5365 | 35.4758 | 8.5827 | 6.2609 | 11.2277 | 35.6389 | 8.4927 | 6.1953 | 11.1729 | 33.7739 | 10.3691 | 7.5642 | 16.0378 | 33.8185 | 10.2768 | 7.4968 | 15.9292 | 33.8935 | 10.1798 | 7.426 | 15.5705 | 33.9922 | 10.1174 | 7.3805 | 15.428 | 34.1039 | 10.0409 | 7.3247 | 15.0404 | 34.2281 | 9.9439 | 7.254 | 14.6867 | 34.3659 | 9.8507 | 7.186 | 14.4531 | 34.4788 | 9.7303 | 7.0981 | 14.0921 | 34.5964 | 9.583 | 6.9906 | 13.6253 | 34.7199 | 9.4979 | 6.9286 | 13.2082 | 35.0446 | 9.3949 | 6.8535 | 12.3937 | 35.2464 | 9.2392 | 6.7399 | 11.7624 | 35.3957 | 9.3236 | 6.8014 | 11.3825 | 35.4896 | 9.2792 | 6.769 | 11.1699 | 33.8335 | 10.3629 | 7.5596 | 15.7239 | 33.9181 | 10.2092 | 7.4474 | 15.3747 | 33.9352 | 10.0376 | 7.3223 | 15.1566 | 33.9838 | 10.0246 | 7.3128 | 15.1281 | 34.0505 | 9.939 | 7.2504 | 14.8333 | 34.1361 | 9.8518 | 7.1867 | 14.551 | 34.2293 | 9.771 | 7.1278 | 14.4068 | 34.3276 | 9.6559 | 7.0438 | 14.1514 | 34.4296 | 9.4997 | 6.9299 | 13.8123 | 34.5365 | 9.381 | 6.8433 | 13.5104 | 34.919 | 9.2225 | 6.7277 | 12.517 | 35.1733 | 9.0435 | 6.5971 | 11.9133 | 35.339 | 9.0127 | 6.5747 | 11.6441 | 35.4435 | 8.9802 | 6.5509 | 11.6263 | 33.8267 | 10.3042 | 7.5167 | 15.7244 | 33.9063 | 10.1655 | 7.4156 | 15.371 | 33.9236 | 10.0487 | 7.3304 | 15.1442 | 33.9786 | 9.9503 | 7.2586 | 15.108 | 34.058 | 9.8114 | 7.1573 | 14.7995 | 34.1665 | 9.6303 | 7.0251 | 14.5001 | 34.2943 | 9.4101 | 6.8646 | 14.3283 | 34.4377 | 9.3969 | 6.8549 | 14.0394 | 34.5946 | 9.2828 | 6.7717 | 13.682 | 34.7465 | 9.0795 | 6.6234 | 13.3937 | 35.2574 | 8.799 | 6.4188 | 12.0683 | 35.7813 | 8.0989 | 5.9081 | 9.3798 | 36.0315 | 7.656 | 5.5849 | 7.2833 | 36.0894 | 7.1572 | 5.2211 | 5.8046 | 33.8169 | 10.3071 | 7.5189 | 15.7386 | 33.8924 | 10.1423 | 7.3987 | 15.3889 | 33.9027 | 9.9667 | 7.2706 | 15.1784 | 33.9454 | 9.7325 | 7.0997 | 15.1678 | 34.0117 | 9.6001 | 7.0031 | 14.8874 | 34.1057 | 9.5242 | 6.9477 | 14.6248 | 34.2227 | 9.5154 | 6.9413 | 14.4906 | 34.3525 | 9.4598 | 6.9008 | 14.2459 | 34.4954 | 9.3515 | 6.8218 | 13.9093 | 34.6639 | 9.1593 | 6.6816 | 13.2128 | 35.2813 | 8.3634 | 6.101 | 10.1515 | 35.6483 | 7.5384 | 5.4992 | 7.6936 | 35.7308 | 7.13 | 5.2013 | 6.2429 | 35.6406 | 7.0386 | 5.1345 | 6.6076
STRAWBERRY BANK | HUNCOAT | PADIHAM | 376338 | 429396 | 19.8722 | 4.2842 | 3.1253 | 14.9547 | 19.9572 | 3.9758 | 2.9003 | 14.7297 | 20.1301 | 3.7205 | 2.7141 | 14.6414 | 20.3321 | 3.4812 | 2.5395 | 14.4716 | 19.7832 | 3.209 | 2.3409 | 14.2846 | 18.0786 | 2.9325 | 2.1392 | 14.0433 | 17.5211 | 2.8421 | 2.0733 | 13.7862 | 16.8654 | 2.7357 | 1.9957 | 13.5142 | 16.1316 | 2.6167 | 1.9089 | 13.2284 | 15.3948 | 2.4972 | 1.8217 | 12.9106 | 14.1304 | 2.2921 | 1.672 | 11.8868 | 23.0544 | 4.5019 | 3.2841 | 11.2147 | 23.373 | 8.7188 | 6.3602 | 11.061 | 23.6601 | 9.4825 | 6.9174 | 11.0646 | 19.8996 | 4.3098 | 3.1439 | 15.1753 | 20.0009 | 3.98 | 2.9033 | 15.1192 | 20.1666 | 3.6405 | 2.6557 | 14.9422 | 20.3221 | 3.3154 | 2.4186 | 14.7392 | 18.6063 | 3.0181 | 2.2017 | 14.5479 | 16.9589 | 2.7509 | 2.0067 | 14.3188 | 16.521 | 2.6799 | 1.9549 | 14.067 | 16.0865 | 2.6094 | 1.9035 | 13.8059 | 15.626 | 2.5347 | 1.849 | 13.5181 | 15.141 | 2.456 | 1.7916 | 13.228 | 15.056 | 2.4422 | 1.7816 | 12.4823 | 22.4322 | 3.8086 | 2.7783 | 11.9833 | 22.6522 | 6.4055 | 4.6727 | 11.7385 | 22.8071 | 7.3048 | 5.3288 | 11.6607 | 19.8723 | 4.3111 | 3.1449 | 14.9604 | 19.9574 | 3.9692 | 2.8955 | 14.7413 | 20.1305 | 3.6051 | 2.6299 | 14.6595 | 20.1425 | 3.2673 | 2.3835 | 14.4965 | 18.1964 | 2.9516 | 2.1532 | 14.3169 | 16.1537 | 2.6203 | 1.9115 | 14.0837 | 15.8648 | 2.5734 | 1.8773 | 13.8346 | 15.4196 | 2.5012 | 1.8246 | 13.58 | 14.9 | 2.4169 | 1.7631 | 13.3083 | 14.3596 | 2.3293 | 1.6992 | 13.022 | 14.6024 | 2.3687 | 1.7279 | 12.1138 | 22.8539 | 4.5887 | 3.3474 | 11.6356 | 23.1026 | 8.9238 | 6.5098 | 11.5588 | 23.2665 | 9.7512 | 7.1134 | 11.6698 | 19.8797 | 4.2924 | 3.1313 | 14.9709 | 19.9725 | 4.0014 | 2.9189 | 14.7638 | 20.1454 | 3.762 | 2.7444 | 14.699 | 20.3398 | 3.4983 | 2.5519 | 14.5585 | 19.8354 | 3.2175 | 2.3471 | 14.406 | 18.0286 | 2.9244 | 2.1333 | 14.2031 | 17.3904 | 2.8209 | 2.0578 | 13.9662 | 16.6725 | 2.7045 | 1.9729 | 13.7249 | 16.0029 | 2.5958 | 1.8936 | 13.5061 | 15.2582 | 2.475 | 1.8055 | 13.2205 | 13.6345 | 2.2116 | 1.6134 | 11.7248 | 22.9145 | 3.717 | 2.7115 | 8.2505 | 24.9099 | 7.1732 | 5.2328 | 5.5631 | 24.9166 | 7.5528 | 5.5097 | 3.9036 | 19.8815 | 4.295 | 3.1332 | 14.9787 | 20.0085 | 4.3204 | 3.1517 | 14.7536 | 20.2034 | 4.3286 | 3.1577 | 14.6795 | 20.3939 | 4.2893 | 3.129 | 14.551 | 20.6068 | 4.1837 | 3.052 | 14.4131 | 20.9112 | 4.0422 | 2.9487 | 14.1437 | 21.1478 | 3.9175 | 2.8577 | 13.932 | 21.3851 | 3.9072 | 2.8502 | 13.721 | 21.6888 | 3.9103 | 2.8525 | 13.4322 | 22.4881 | 3.8681 | 2.8218 | 12.6113 | 23.728 | 9.2356 | 6.7372 | 8.8833 | 24.4667 | 8.2124 | 5.9908 | 5.619 | 24.7253 | 7.6572 | 5.5858 | 3.9711 | 24.4478 | 7.6609 | 5.5885 | 4.6678
STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 31.341 | 10.6083 | 7.7386 | 15.2931 | 31.4192 | 10.0646 | 7.342 | 14.2343 | 31.4194 | 9.9072 | 7.2272 | 13.8795 | 31.4537 | 9.6045 | 7.0064 | 13.7146 | 31.5045 | 9.3201 | 6.7989 | 13.6097 | 31.5689 | 9.2782 | 6.7683 | 13.4539 | 31.6379 | 9.167 | 6.6872 | 13.1841 | 31.7101 | 9.0996 | 6.6381 | 13.0164 | 31.7857 | 9.0275 | 6.5854 | 12.8152 | 31.8685 | 8.9658 | 6.5404 | 12.5453 | 32.341 | 8.6391 | 6.3021 | 11.4814 | 32.8878 | 8.4164 | 6.1396 | 10.7108 | 33.2696 | 8.3871 | 6.1183 | 10.3607 | 33.6141 | 8.3145 | 6.0653 | 10.2634 | 31.2548 | 10.7688 | 7.8557 | 15.8743 | 31.2602 | 10.521 | 7.675 | 15.4177 | 31.2943 | 10.2507 | 7.4778 | 15.1129 | 31.3491 | 9.884 | 7.2103 | 14.9203 | 31.4118 | 9.8532 | 7.1878 | 14.8305 | 31.4782 | 9.7667 | 7.1247 | 14.6264 | 31.5492 | 9.6803 | 7.0616 | 14.415 | 31.6232 | 9.6262 | 7.0222 | 14.2052 | 31.7003 | 9.5586 | 6.9728 | 13.9418 | 31.7798 | 9.4936 | 6.9254 | 13.699 | 32.1142 | 9.3075 | 6.7897 | 12.845 | 32.4565 | 9.1867 | 6.7016 | 12.2001 | 32.7515 | 9.2003 | 6.7115 | 11.7603 | 32.9779 | 9.1997 | 6.711 | 11.465 | 31.3422 | 10.7702 | 7.8567 | 15.3066 | 31.421 | 10.472 | 7.6391 | 14.2461 | 31.4218 | 10.0519 | 7.3327 | 13.9145 | 31.4567 | 10.0787 | 7.3523 | 13.7573 | 31.5072 | 9.936 | 7.2481 | 13.6614 | 31.5715 | 9.7479 | 7.111 | 13.4967 | 31.6402 | 9.6317 | 7.0262 | 13.2542 | 31.7118 | 9.5617 | 6.9751 | 13.0953 | 31.7858 | 9.4825 | 6.9173 | 12.8565 | 31.8648 | 9.4088 | 6.8636 | 12.6084 | 32.2808 | 9.123 | 6.6551 | 11.6157 | 32.6553 | 8.9494 | 6.5284 | 11.0554 | 32.9605 | 8.988 | 6.5566 | 10.7926 | 33.1695 | 8.8524 | 6.4577 | 10.753 | 31.3352 | 10.609 | 7.7391 | 15.3061 | 31.4083 | 10.103 | 7.37 | 14.2616 | 31.4084 | 9.9017 | 7.2232 | 13.9119 | 31.447 | 9.5715 | 6.9823 | 13.7488 | 31.5024 | 9.3476 | 6.8189 | 13.6462 | 31.5873 | 9.2754 | 6.7663 | 13.4806 | 31.6916 | 9.1431 | 6.6698 | 13.18 | 31.8106 | 9.0615 | 6.6102 | 12.9744 | 31.94 | 8.9802 | 6.551 | 12.7596 | 32.0827 | 8.8919 | 6.4865 | 12.4988 | 32.917 | 8.4194 | 6.1419 | 11.0659 | 33.8094 | 7.7278 | 5.6373 | 8.3196 | 34.2479 | 7.285 | 5.3143 | 6.083 | 34.4001 | 6.9418 | 5.0639 | 4.6293 | 31.3346 | 10.6104 | 7.7402 | 15.3101 | 31.4133 | 10.1877 | 7.4318 | 14.2582 | 31.4188 | 10.1175 | 7.3806 | 13.9135 | 31.452 | 9.8124 | 7.158 | 13.7583 | 31.5087 | 9.785 | 7.138 | 13.6582 | 31.6023 | 9.694 | 7.0716 | 13.5002 | 31.7233 | 9.5036 | 6.9327 | 13.2107 | 31.864 | 9.4146 | 6.8678 | 13.0166 | 32.0281 | 9.3374 | 6.8115 | 12.7647 | 32.2536 | 9.1692 | 6.6888 | 12.0695 | 33.2259 | 8.3532 | 6.0935 | 8.9399 | 33.8971 | 7.5842 | 5.5325 | 6.3625 | 34.1488 | 7.1961 | 5.2495 | 4.8516 | 34.1109 | 7.145 | 5.2122 | 5.2022
STUBBINS | ROSSENDALE | PADIHAM | 379112 | 418005 | 44.0044 | 11.3025 | 8.1233 | 29.2443 | 44.1752 | 11.1256 | 7.9962 | 28.891 | 44.1938 | 11.0168 | 7.918 | 28.9204 | 44.2535 | 10.9267 | 7.8533 | 28.8486 | 44.3412 | 10.7939 | 7.7578 | 28.7401 | 44.455 | 10.4901 | 7.5394 | 28.5716 | 44.5708 | 10.5403 | 7.5755 | 28.4018 | 44.686 | 10.6091 | 7.625 | 28.2468 | 47.6947 | 10.155 | 7.2986 | 25.2123 | 47.608 | 10.1053 | 7.2628 | 25.2012 | 47.7231 | 9.7882 | 7.035 | 24.5381 | 47.927 | 9.8325 | 7.0668 | 24.1689 | 47.949 | 9.6994 | 6.9712 | 24.2559 | 47.9253 | 9.5418 | 6.8579 | 24.4842 | 43.8231 | 11.4375 | 8.2203 | 29.6762 | 43.8461 | 11.492 | 8.2595 | 29.675 | 43.9265 | 11.4124 | 8.2023 | 29.561 | 44.0252 | 11.311 | 8.1294 | 29.3965 | 44.1329 | 11.1674 | 8.0262 | 29.2313 | 44.2452 | 11.0683 | 7.955 | 29.0559 | 44.3642 | 10.9944 | 7.9019 | 28.867 | 44.4853 | 10.8975 | 7.8323 | 28.6869 | 44.6081 | 10.854 | 7.801 | 28.4497 | 44.7297 | 10.7654 | 7.7373 | 28.2375 | 45.051 | 10.4922 | 7.541 | 27.5801 | 45.2987 | 10.7584 | 7.7323 | 27.1253 | 45.4557 | 10.909 | 7.8405 | 26.9252 | 45.5118 | 10.993 | 7.9009 | 26.8902 | 44.0045 | 11.4165 | 8.2053 | 29.2461 | 44.1754 | 11.4383 | 8.221 | 28.895 | 44.1942 | 11.3378 | 8.1487 | 28.9264 | 44.2541 | 11.254 | 8.0885 | 28.8568 | 44.3416 | 11.1093 | 7.9845 | 28.7508 | 44.4551 | 10.9589 | 7.8764 | 28.5852 | 44.5707 | 10.7517 | 7.7274 | 28.4184 | 44.6857 | 10.7481 | 7.7249 | 28.2662 | 47.693 | 10.8329 | 7.7858 | 25.236 | 47.6068 | 10.8484 | 7.797 | 25.2628 | 47.6923 | 10.7273 | 7.7099 | 24.7176 | 47.8114 | 10.6304 | 7.6403 | 24.4444 | 47.8012 | 10.5245 | 7.5642 | 24.5708 | 47.7064 | 10.3403 | 7.4318 | 24.8506 | 43.9886 | 11.3088 | 8.1278 | 29.2797 | 44.1443 | 11.1459 | 8.0108 | 28.961 | 44.1503 | 11.0542 | 7.9448 | 29.0234 | 44.1988 | 10.919 | 7.8477 | 28.987 | 44.2772 | 10.6888 | 7.6823 | 28.9123 | 44.3879 | 10.5634 | 7.5921 | 28.7724 | 44.5062 | 10.6992 | 7.6897 | 28.6249 | 44.6291 | 10.6947 | 7.6865 | 28.4865 | 47.448 | 10.1884 | 7.3226 | 25.669 | 47.3937 | 10.1882 | 7.3224 | 25.7177 | 51.8952 | 9.0789 | 6.5252 | 20.8643 | 52.0425 | 8.6825 | 6.2403 | 19.7221 | 49.8357 | 8.2051 | 5.8971 | 19.5473 | 47.9255 | 7.8906 | 5.6711 | 19.4315 | 43.9938 | 11.3099 | 8.1287 | 29.2817 | 44.1641 | 11.2275 | 8.0694 | 28.959 | 44.1756 | 11.1326 | 8.0012 | 29.0214 | 44.2214 | 11.0332 | 7.9297 | 28.9892 | 44.2954 | 11.1618 | 8.0222 | 28.9201 | 44.3995 | 11.2139 | 8.0596 | 28.7879 | 47.3543 | 10.7045 | 7.6936 | 25.8052 | 47.2918 | 10.6731 | 7.6709 | 25.8553 | 47.2466 | 10.5876 | 7.6095 | 25.8955 | 47.21 | 10.4413 | 7.5044 | 25.8118 | 48.0915 | 9.9491 | 7.1506 | 23.8534 | 48.1238 | 9.1286 | 6.5609 | 22.8541 | 47.8205 | 8.6233 | 6.1978 | 22.6827 | 47.4975 | 8.5525 | 6.1468 | 23.4021
SWINTON | AGECROFT | KEARSLEY | 378367 | 401718 | 30.6206 | 15.3749 | 11.0502 | 17.7478 | 30.685 | 13.6126 | 9.7836 | 17.4963 | 30.721 | 11.8524 | 8.5185 | 17.351 | 30.7814 | 9.9598 | 7.1583 | 17.0617 | 30.8666 | 8.292 | 5.9597 | 16.8582 | 30.9689 | 6.6289 | 4.7643 | 16.5112 | 31.0825 | 6.4564 | 4.6404 | 16.1382 | 31.2055 | 6.448 | 4.6343 | 15.7698 | 31.3228 | 6.3931 | 4.5948 | 15.3872 | 31.4399 | 6.3036 | 4.5305 | 14.9645 | 32.0791 | 6.0595 | 4.3551 | 13.3156 | 32.8184 | 8.5511 | 6.1458 | 12.1112 | 33.3817 | 12.4357 | 8.9378 | 11.4482 | 33.9192 | 13.1731 | 9.4678 | 11.0945 | 30.5949 | 15.2811 | 10.9828 | 17.7886 | 30.6401 | 13.6648 | 9.8211 | 17.568 | 30.7039 | 12.0696 | 8.6747 | 17.3434 | 30.7753 | 10.3774 | 7.4584 | 17.0297 | 30.865 | 8.6471 | 6.2148 | 16.8165 | 30.9652 | 6.9996 | 5.0308 | 16.4591 | 31.076 | 6.9125 | 4.9681 | 16.0673 | 31.1946 | 6.8124 | 4.8962 | 15.675 | 31.3211 | 6.6931 | 4.8105 | 15.2183 | 31.4541 | 6.5755 | 4.726 | 14.7953 | 31.9201 | 6.3783 | 4.5842 | 13.5164 | 32.3677 | 7.9316 | 5.7006 | 12.4604 | 32.7589 | 10.4424 | 7.5052 | 11.6905 | 33.0846 | 10.9718 | 7.8857 | 11.1586 | 30.622 | 15.2802 | 10.9822 | 17.7598 | 30.6871 | 13.7089 | 9.8529 | 17.5306 | 30.7239 | 12.0742 | 8.678 | 17.4061 | 30.7849 | 10.3255 | 7.4211 | 17.134 | 30.8706 | 8.485 | 6.0983 | 16.9511 | 30.9724 | 6.7713 | 4.8666 | 16.6279 | 31.085 | 6.6161 | 4.7551 | 16.2792 | 31.2065 | 6.5951 | 4.7401 | 15.935 | 31.3222 | 6.5401 | 4.7005 | 15.5821 | 31.4339 | 6.4705 | 4.6505 | 15.2063 | 32.002 | 6.5172 | 4.6841 | 13.7109 | 32.5287 | 8.9531 | 6.4348 | 12.7281 | 32.9615 | 12.88 | 9.2571 | 12.1856 | 33.3091 | 13.6315 | 9.7973 | 11.9612 | 30.6195 | 15.3726 | 11.0486 | 17.7507 | 30.685 | 13.5957 | 9.7715 | 17.5024 | 30.7304 | 11.8078 | 8.4865 | 17.3584 | 30.8112 | 9.9248 | 7.1332 | 17.0577 | 30.9206 | 8.284 | 5.9538 | 16.8679 | 31.0672 | 6.5683 | 4.7208 | 16.5294 | 31.2129 | 6.5051 | 4.6754 | 16.1502 | 31.3741 | 6.4588 | 4.6421 | 15.7721 | 31.5519 | 6.3798 | 4.5853 | 15.4173 | 31.7488 | 6.2663 | 4.5037 | 15.0618 | 32.8745 | 5.8678 | 4.2173 | 12.8163 | 34.2306 | 7.6709 | 5.5133 | 8.6001 | 34.9025 | 10.8118 | 7.7706 | 5.2335 | 35.2231 | 11.2349 | 8.0748 | 2.9806 | 30.6105 | 15.3787 | 11.053 | 17.7826 | 30.6748 | 15.1172 | 10.865 | 17.5431 | 30.7243 | 14.7871 | 10.6277 | 17.4068 | 30.808 | 14.5469 | 10.4551 | 17.1318 | 30.9197 | 14.5676 | 10.47 | 16.9759 | 31.0462 | 14.5177 | 10.4342 | 16.6813 | 31.2088 | 14.3928 | 10.3444 | 16.3419 | 31.3993 | 14.2672 | 10.2541 | 16.0062 | 31.6266 | 14.1362 | 10.1599 | 15.6028 | 31.9259 | 13.861 | 9.9622 | 14.6372 | 33.2499 | 13.2321 | 9.5102 | 9.9964 | 34.2376 | 12.122 | 8.7123 | 6.1568 | 34.6661 | 11.4483 | 8.2281 | 3.7749 | 34.7255 | 11.32 | 8.1359 | 4.0304
TAME VALLEY | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 32.4407 | 12.2903 | 8.9656 | 13.1599 | 32.5634 | 12.1408 | 8.8566 | 12.8522 | 32.6992 | 11.929 | 8.7021 | 12.7023 | 32.8808 | 11.787 | 8.5985 | 12.4952 | 33.1059 | 11.5453 | 8.4221 | 12.3492 | 33.3621 | 11.433 | 8.3402 | 12.0192 | 33.6531 | 11.2519 | 8.2081 | 11.6965 | 33.9529 | 10.9415 | 7.9817 | 11.3954 | 34.1177 | 11.0076 | 8.0299 | 11.0518 | 34.3302 | 10.8911 | 7.9449 | 10.5643 | 35.49 | 10.1441 | 7.3999 | 8.3613 | 36.7121 | 9.5437 | 6.962 | 6.9256 | 37.4375 | 9.4424 | 6.8881 | 6.306 | 38.1728 | 9.2437 | 6.7431 | 5.6666 | 32.4129 | 12.3349 | 8.9981 | 13.3812 | 32.5201 | 12.1114 | 8.8351 | 13.2519 | 32.6971 | 11.9637 | 8.7273 | 13.0149 | 32.8934 | 11.7559 | 8.5758 | 12.7972 | 33.1137 | 11.7039 | 8.5378 | 12.6658 | 33.3606 | 11.5907 | 8.4552 | 12.3731 | 33.6354 | 11.5101 | 8.3964 | 12.083 | 33.8754 | 11.4094 | 8.323 | 11.7007 | 34.0308 | 11.2871 | 8.2338 | 11.2431 | 34.1932 | 11.1388 | 8.1256 | 10.7541 | 34.8194 | 10.7811 | 7.8646 | 9.3461 | 35.4485 | 10.443 | 7.618 | 8.1652 | 36.0129 | 10.4632 | 7.6328 | 7.3062 | 36.4836 | 10.5682 | 7.7094 | 6.7114 | 32.4409 | 12.3309 | 8.9952 | 13.1661 | 32.5641 | 12.1265 | 8.8461 | 12.8666 | 32.7005 | 11.8342 | 8.6329 | 12.7254 | 32.8831 | 11.7373 | 8.5622 | 12.5272 | 33.1082 | 11.6476 | 8.4968 | 12.3906 | 33.3635 | 11.4376 | 8.3436 | 12.0716 | 33.6538 | 11.3094 | 8.2501 | 11.7598 | 33.959 | 11.2073 | 8.1756 | 11.4695 | 34.1232 | 11.0653 | 8.072 | 11.1424 | 34.3301 | 10.9333 | 7.9757 | 10.7379 | 35.3761 | 10.3982 | 7.5853 | 8.9111 | 36.293 | 9.9324 | 7.2455 | 7.802 | 36.8624 | 9.9584 | 7.2645 | 7.2938 | 37.3115 | 9.6794 | 7.061 | 6.8967 | 32.4349 | 12.2895 | 8.965 | 13.1705 | 32.5543 | 12.1361 | 8.8531 | 12.8648 | 32.6928 | 11.9012 | 8.6817 | 12.7058 | 32.8848 | 11.6967 | 8.5326 | 12.4767 | 33.1282 | 11.5572 | 8.4308 | 12.3007 | 33.4228 | 11.2705 | 8.2217 | 11.905 | 33.7747 | 10.9315 | 7.9744 | 11.46 | 34.1627 | 10.9459 | 7.9849 | 11.0083 | 34.5771 | 10.8017 | 7.8797 | 10.5398 | 35.0218 | 10.5675 | 7.7089 | 10.0079 | 37.0311 | 9.3893 | 6.8494 | 6.6373 | 38.5865 | 7.6075 | 5.5496 | -0.23246 | 39.5427 | 6.4964 | 4.7391 | -6.0017 | 34.5963 | 5.6119 | 4.0938 | -9.9699 | 32.4404 | 12.2921 | 8.9669 | 13.1706 | 32.5952 | 12.2109 | 8.9077 | 12.8436 | 32.752 | 12.0181 | 8.767 | 12.6736 | 32.9367 | 11.9443 | 8.7132 | 12.4419 | 33.1681 | 11.7494 | 8.571 | 12.2501 | 33.4456 | 11.6348 | 8.4874 | 11.8467 | 33.7985 | 11.3273 | 8.2631 | 11.3985 | 34.18 | 11.2453 | 8.2033 | 10.9451 | 34.5947 | 11.1225 | 8.1137 | 10.3215 | 35.0788 | 10.7189 | 7.8193 | 8.7463 | 37.2727 | 8.9409 | 6.5223 | 1.2557 | 38.7785 | 7.1987 | 5.2513 | -5.3821 | 39.2842 | 6.3723 | 4.6485 | -9.2911 | 38.3997 | 6.2288 | 4.5438 | -8.7064
TARDY GATE | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353958 | 426066 | 30.5943 | 11.9874 | 8.6156 | 14.6511 | 30.6794 | 11.8103 | 8.4883 | 14.1148 | 30.7177 | 11.8072 | 8.486 | 13.9392 | 30.7852 | 11.6885 | 8.4007 | 13.5104 | 30.8772 | 11.695 | 8.4054 | 13.3682 | 30.9933 | 11.8529 | 8.5189 | 12.9073 | 31.1277 | 11.8169 | 8.493 | 12.5303 | 31.2729 | 11.754 | 8.4479 | 12.1796 | 31.43 | 11.7436 | 8.4404 | 11.7019 | 31.6028 | 11.6198 | 8.3514 | 11.1423 | 32.4205 | 11.2121 | 8.0584 | 9.3545 | 33.2096 | 10.8793 | 7.8192 | 8.4377 | 33.6921 | 10.4541 | 7.5136 | 8.1315 | 34.0416 | 10.0914 | 7.2529 | 8.2421 | 30.5317 | 12.0444 | 8.6566 | 14.845 | 30.5668 | 11.9731 | 8.6053 | 14.4815 | 30.6324 | 12.0035 | 8.6272 | 14.2799 | 30.7098 | 12.0673 | 8.673 | 13.8641 | 30.797 | 12.087 | 8.6872 | 13.7537 | 30.8951 | 12.0559 | 8.6648 | 13.3423 | 31.0057 | 12.0158 | 8.636 | 13.0116 | 31.1227 | 12.0114 | 8.6328 | 12.7059 | 31.2479 | 11.9662 | 8.6004 | 12.2769 | 31.3777 | 11.9094 | 8.5595 | 11.8324 | 31.7679 | 11.7376 | 8.4361 | 10.5975 | 32.1396 | 11.5998 | 8.337 | 9.6441 | 32.4803 | 11.4634 | 8.2389 | 8.9403 | 32.7549 | 11.3338 | 8.1458 | 8.5773 | 30.5944 | 12.0388 | 8.6525 | 14.6576 | 30.6798 | 12.0254 | 8.6429 | 14.1353 | 30.7185 | 12.1752 | 8.7506 | 13.9714 | 30.7865 | 12.2268 | 8.7877 | 13.5548 | 30.8787 | 12.2923 | 8.8347 | 13.426 | 30.9947 | 12.2784 | 8.8247 | 12.9822 | 31.1289 | 12.2129 | 8.7776 | 12.6203 | 31.2743 | 12.1588 | 8.7388 | 12.2836 | 31.4296 | 12.0952 | 8.6931 | 11.8292 | 31.5937 | 11.9959 | 8.6217 | 11.3204 | 32.3281 | 11.5945 | 8.3332 | 9.7826 | 32.9304 | 11.2607 | 8.0933 | 9.0777 | 33.3901 | 10.88 | 7.8197 | 8.7868 | 33.6173 | 10.5429 | 7.5774 | 8.9654 | 30.5907 | 11.989 | 8.6167 | 14.6628 | 30.6779 | 11.7906 | 8.4742 | 14.1433 | 30.7309 | 11.7307 | 8.4311 | 13.9913 | 30.8243 | 11.6842 | 8.3976 | 13.5885 | 30.9559 | 11.8316 | 8.5036 | 13.4956 | 31.1336 | 11.8852 | 8.5421 | 13.087 | 31.3566 | 11.8974 | 8.5509 | 12.7436 | 31.6137 | 11.841 | 8.5104 | 12.4328 | 31.9036 | 11.7155 | 8.4202 | 12.0504 | 32.2288 | 11.6645 | 8.3835 | 11.6545 | 33.2646 | 10.9954 | 7.9026 | 9.496 | 34.3204 | 9.6366 | 6.926 | 5.1281 | 34.9838 | 8.5203 | 6.1237 | 1.6074 | 35.3213 | 7.6895 | 5.5266 | -0.59848 | 30.5958 | 11.9866 | 8.615 | 14.6404 | 30.6998 | 11.8083 | 8.4869 | 14.0843 | 30.7602 | 11.7691 | 8.4587 | 13.9465 | 30.8529 | 11.6968 | 8.4067 | 13.5807 | 30.9842 | 11.8817 | 8.5396 | 13.5098 | 31.1614 | 11.9613 | 8.5968 | 13.1422 | 31.3942 | 11.9452 | 8.5853 | 12.8467 | 31.6572 | 11.9335 | 8.5768 | 12.5919 | 31.959 | 11.8644 | 8.5272 | 12.1287 | 32.3134 | 11.6345 | 8.362 | 11.0219 | 33.5139 | 10.5078 | 7.5522 | 6.1541 | 34.398 | 9.2743 | 6.6656 | 2.2284 | 34.7739 | 8.4769 | 6.0925 | -0.13735 | 34.7152 | 8.2612 | 5.9375 | 0.5291
TARLETON | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 344741 | 422417 | 15.2928 | 12.634 | 9.0803 | 9.9207 | 15.4174 | 11.5767 | 8.3204 | 9.4772 | 15.5096 | 10.5325 | 7.5699 | 9.0862 | 15.6521 | 9.4869 | 6.8184 | 8.5902 | 15.8075 | 8.4592 | 6.0798 | 8.062 | 15.9816 | 7.4548 | 5.3579 | 7.4611 | 16.1753 | 7.2671 | 5.223 | 6.7746 | 16.3799 | 7.0799 | 5.0885 | 6.071 | 16.5883 | 6.8929 | 4.9541 | 5.3805 | 16.8994 | 6.6683 | 4.7926 | 4.4999 | 18.145 | 5.8939 | 4.2361 | 1.237 | 19.2451 | 6.4601 | 4.643 | -0.49589 | 19.9988 | 12.4193 | 8.926 | -0.96352 | 20.6478 | 17.1276 | 12.3099 | -0.63125 | 15.2306 | 12.6606 | 9.0994 | 10.1599 | 15.2991 | 11.6865 | 8.3993 | 9.9435 | 15.4099 | 10.671 | 7.6694 | 9.507 | 15.5021 | 9.6717 | 6.9513 | 9.0892 | 15.6117 | 8.697 | 6.2507 | 8.6937 | 15.7365 | 7.8128 | 5.6152 | 8.2199 | 15.8767 | 7.6701 | 5.5126 | 7.6439 | 16.0244 | 7.526 | 5.4091 | 7.0602 | 16.1798 | 7.3757 | 5.301 | 6.4296 | 16.3415 | 7.22 | 5.1891 | 5.7672 | 16.9233 | 6.8821 | 4.9463 | 4.0858 | 17.6206 | 7.2735 | 5.2276 | 2.5947 | 18.1984 | 11.8321 | 8.5039 | 1.6397 | 18.5249 | 15.5366 | 11.1665 | 1.112 | 15.2929 | 12.6574 | 9.0971 | 9.9239 | 15.4178 | 11.5977 | 8.3355 | 9.4975 | 15.5104 | 10.5075 | 7.5519 | 9.1259 | 15.6534 | 9.455 | 6.7955 | 8.6503 | 15.8089 | 8.4431 | 6.0682 | 8.1444 | 15.9829 | 7.4669 | 5.3666 | 7.5667 | 16.1765 | 7.3076 | 5.2521 | 6.903 | 16.3812 | 7.1466 | 5.1364 | 6.2209 | 16.5878 | 6.9785 | 5.0156 | 5.5634 | 16.8898 | 6.7999 | 4.8872 | 4.7699 | 18.0142 | 6.3089 | 4.5343 | 1.8652 | 18.8741 | 6.9387 | 4.987 | 0.47457 | 19.5044 | 12.7396 | 9.1562 | 0.1552 | 19.963 | 17.0966 | 12.2877 | 0.56336 | 15.2904 | 12.6364 | 9.082 | 9.9483 | 15.4348 | 11.5746 | 8.3189 | 9.5099 | 15.5573 | 10.4966 | 7.5441 | 9.129 | 15.728 | 9.4441 | 6.7876 | 8.6579 | 15.9434 | 8.4072 | 6.0424 | 8.1451 | 16.2151 | 7.3803 | 5.3044 | 7.5346 | 16.5636 | 7.1645 | 5.1493 | 6.7876 | 16.9535 | 6.9411 | 4.9887 | 6.0232 | 17.3447 | 6.7298 | 4.8369 | 5.3557 | 17.7759 | 6.5065 | 4.6763 | 4.6586 | 19.7558 | 5.5265 | 3.972 | 1.3703 | 21.2217 | 5.5509 | 3.9895 | -2.3688 | 21.1187 | 11.0266 | 7.925 | -4.2604 | 20.5923 | 15.2285 | 10.945 | -5.5062 | 15.2951 | 12.6201 | 9.0703 | 9.8494 | 15.4549 | 12.3685 | 8.8895 | 9.2809 | 15.5876 | 12.1098 | 8.7035 | 8.8761 | 15.7816 | 11.839 | 8.5089 | 8.4106 | 15.9967 | 11.5643 | 8.3115 | 7.8789 | 16.2669 | 11.313 | 8.1309 | 7.2974 | 16.622 | 11.0867 | 7.9682 | 6.6132 | 17.0221 | 10.8647 | 7.8087 | 5.9491 | 17.4637 | 10.657 | 7.6594 | 5.3703 | 17.976 | 10.3636 | 7.4486 | 4.3675 | 19.8369 | 9.0011 | 6.4692 | -0.32526 | 20.7237 | 8.6982 | 6.2515 | -3.2113 | 20.2851 | 16.2566 | 11.6839 | -4.1309 | 19.5727 | 16.0068 | 11.5044 | -3.5887
THE HEIGHT | AGECROFT | KEARSLEY | 379792 | 400497 | 29.7443 | 10.3457 | 7.547 | 15.7537 | 29.791 | 10.0296 | 7.3164 | 15.5135 | 29.813 | 9.8472 | 7.1834 | 15.3152 | 29.8706 | 9.6543 | 7.0427 | 14.9239 | 29.9485 | 9.4189 | 6.871 | 14.6458 | 30.0449 | 9.3675 | 6.8334 | 14.1002 | 30.1539 | 9.3125 | 6.7933 | 13.6732 | 30.2728 | 9.2306 | 6.7336 | 13.2286 | 30.4832 | 9.1247 | 6.6563 | 12.679 | 30.6224 | 8.9888 | 6.5572 | 12.0854 | 31.4346 | 8.3238 | 6.0721 | 9.9954 | 32.3301 | 8.2802 | 6.0403 | 8.5302 | 33.0474 | 8.1795 | 5.9669 | 7.7551 | 33.8156 | 8.1059 | 5.9132 | 7.3311 | 29.714 | 10.4577 | 7.6288 | 15.7665 | 29.7343 | 10.3913 | 7.5803 | 15.5493 | 29.7755 | 10.2292 | 7.4621 | 15.3575 | 29.839 | 9.9942 | 7.2906 | 14.9928 | 29.9118 | 9.7242 | 7.0937 | 14.7633 | 29.9934 | 9.5933 | 6.9982 | 14.2691 | 30.0838 | 9.4824 | 6.9173 | 13.8903 | 30.1801 | 9.3608 | 6.8286 | 13.494 | 30.2822 | 9.2272 | 6.7311 | 13.073 | 30.3883 | 9.0695 | 6.6161 | 12.582 | 30.8697 | 8.9371 | 6.5195 | 10.9616 | 31.4105 | 8.7923 | 6.4139 | 9.631 | 31.9849 | 8.8054 | 6.4234 | 8.6271 | 32.5054 | 8.7049 | 6.3501 | 7.89 | 29.7446 | 10.4621 | 7.632 | 15.7624 | 29.7918 | 10.3996 | 7.5864 | 15.5255 | 29.8146 | 10.2129 | 7.4502 | 15.3378 | 29.8733 | 9.8852 | 7.2111 | 14.9551 | 29.9523 | 9.6105 | 7.0107 | 14.6873 | 30.0493 | 9.5239 | 6.9476 | 14.1552 | 30.1591 | 9.4754 | 6.9122 | 13.7397 | 30.2787 | 9.4122 | 6.866 | 13.306 | 30.4886 | 9.3321 | 6.8077 | 12.7745 | 30.6221 | 9.2267 | 6.7307 | 12.2252 | 31.3354 | 8.8423 | 6.4503 | 10.3401 | 31.9313 | 8.7087 | 6.3529 | 9.1585 | 32.4982 | 8.7799 | 6.4048 | 8.5068 | 32.9876 | 8.605 | 6.2772 | 8.2533 | 29.741 | 10.3419 | 7.5443 | 15.7601 | 29.7871 | 9.9971 | 7.2928 | 15.5287 | 29.8172 | 9.8676 | 7.1983 | 15.3462 | 29.8945 | 9.6133 | 7.0127 | 14.9557 | 30.0023 | 9.4614 | 6.9019 | 14.7108 | 30.1531 | 9.3785 | 6.8415 | 14.1898 | 30.3433 | 9.3004 | 6.7845 | 13.7639 | 30.5673 | 9.2003 | 6.7115 | 13.3207 | 30.8734 | 9.0638 | 6.6119 | 12.831 | 31.1087 | 8.9316 | 6.5155 | 12.346 | 32.4419 | 8.1464 | 5.9427 | 9.5863 | 33.9402 | 7.2835 | 5.3132 | 4.8526 | 34.8742 | 6.6056 | 4.8187 | 1.316 | 35.3174 | 6.0406 | 4.4065 | -0.9432 | 29.7414 | 10.3441 | 7.5458 | 15.7669 | 29.7989 | 10.0463 | 7.3287 | 15.49 | 29.8418 | 9.8684 | 7.1989 | 15.2892 | 29.927 | 9.8493 | 7.1849 | 14.9084 | 30.0436 | 9.7576 | 7.118 | 14.676 | 30.3009 | 9.598 | 7.0016 | 14.093 | 30.5216 | 9.4725 | 6.9101 | 13.6995 | 30.7402 | 9.3467 | 6.8183 | 13.2925 | 30.9939 | 9.1639 | 6.6849 | 12.8055 | 31.3085 | 8.8074 | 6.4249 | 11.6505 | 32.8468 | 8.2778 | 6.0386 | 6.349 | 34.1607 | 7.1366 | 5.2061 | 2.1039 | 34.7203 | 6.4935 | 4.7369 | -0.27573 | 34.7778 | 6.4173 | 4.6813 | 0.15955
THORNTON | BISPHAM | PENWORTHAM WEST / STANAH | 334207 | 442111 | 29.3789 | 12.44 | 8.9408 | 14.5593 | 29.4456 | 12.0028 | 8.6267 | 14.1892 | 29.4833 | 11.5092 | 8.2719 | 13.8722 | 29.5591 | 10.9423 | 7.8645 | 13.5283 | 29.6643 | 10.3094 | 7.4096 | 13.2771 | 29.7936 | 10.2007 | 7.3315 | 12.8351 | 29.9419 | 10.1779 | 7.3151 | 12.3963 | 30.105 | 10.1245 | 7.2767 | 11.9335 | 30.2645 | 10.0442 | 7.2189 | 11.4181 | 30.4324 | 9.9129 | 7.1246 | 10.8278 | 35.4587 | 8.9028 | 6.3986 | 4.5805 | 38.2191 | 8.5353 | 6.1345 | 1.3664 | 38.6294 | 9.6872 | 6.9624 | 1.1122 | 39.0035 | 10.8044 | 7.7653 | 1.2259 | 29.3316 | 12.322 | 8.8561 | 14.7029 | 29.3612 | 11.7572 | 8.4502 | 14.4625 | 29.4233 | 11.0066 | 7.9106 | 14.1396 | 29.5039 | 10.6161 | 7.63 | 13.8065 | 29.5962 | 10.6778 | 7.6743 | 13.6017 | 29.6984 | 10.5671 | 7.5948 | 13.2178 | 29.8125 | 10.463 | 7.52 | 12.8223 | 29.9341 | 10.3187 | 7.4163 | 12.4013 | 30.0624 | 10.227 | 7.3503 | 11.9327 | 30.1928 | 10.1949 | 7.3273 | 11.3764 | 30.5768 | 10.0645 | 7.2335 | 10.0794 | 30.8838 | 9.9827 | 7.1747 | 8.9413 | 31.1226 | 10.8746 | 7.8158 | 8.2689 | 31.3019 | 11.7683 | 8.4581 | 7.7615 | 29.3789 | 12.3171 | 8.8526 | 14.5647 | 29.4458 | 11.6586 | 8.3793 | 14.2062 | 29.4837 | 10.9989 | 7.9051 | 13.9012 | 29.5598 | 10.8755 | 7.8164 | 13.5673 | 29.6648 | 10.885 | 7.8233 | 13.3406 | 29.7935 | 10.79 | 7.755 | 12.9358 | 29.9414 | 10.7293 | 7.7114 | 12.5237 | 30.1042 | 10.6638 | 7.6643 | 12.063 | 30.2622 | 10.6127 | 7.6275 | 11.5918 | 30.4215 | 10.4917 | 7.5406 | 11.0591 | 35.3861 | 10.276 | 7.3856 | 5.0078 | 38.0359 | 10.3589 | 7.4451 | 1.9261 | 38.3886 | 12.6611 | 9.0998 | 1.7682 | 38.6819 | 12.5396 | 9.0125 | 1.9083 | 29.3736 | 12.4396 | 8.9406 | 14.5693 | 29.4402 | 11.9961 | 8.6218 | 14.2132 | 29.4924 | 11.3106 | 8.1292 | 13.9176 | 29.5986 | 10.5691 | 7.5962 | 13.5933 | 29.7521 | 10.3044 | 7.406 | 13.4026 | 29.9521 | 10.3901 | 7.4676 | 13.018 | 30.164 | 10.2691 | 7.3806 | 12.6092 | 30.4036 | 10.0921 | 7.2534 | 12.1776 | 32.5435 | 9.7889 | 7.0355 | 9.899 | 32.822 | 9.7506 | 7.0079 | 9.5088 | 40.0639 | 8.1358 | 5.8474 | 1.0426 | 41.1484 | 7.2395 | 5.2032 | -3.8565 | 41.7002 | 7.5831 | 5.4501 | -7.4634 | 42.0094 | 7.9027 | 5.6798 | -10.0044 | 29.3697 | 12.4454 | 8.9448 | 14.5939 | 29.4495 | 12.0786 | 8.6811 | 14.2216 | 29.5139 | 11.6002 | 8.3373 | 13.9381 | 29.622 | 10.8515 | 7.7992 | 13.6465 | 29.7768 | 10.5205 | 7.5613 | 13.4345 | 29.9592 | 10.6169 | 7.6306 | 13.0985 | 30.427 | 10.6372 | 7.6451 | 12.4895 | 30.6426 | 10.6435 | 7.6497 | 12.1453 | 30.8911 | 10.6006 | 7.6188 | 11.6819 | 32.2157 | 10.2401 | 7.3597 | 9.4987 | 38.4755 | 9.0287 | 6.4891 | -0.90724 | 39.1484 | 7.9769 | 5.7331 | -5.1641 | 39.4431 | 8.8723 | 6.3767 | -7.5566 | 39.3544 | 8.7249 | 6.2707 | -6.9543
TOWNLEY ST | CHADDERTON | WHITEGATE | 387242 | 405960 | 34.6264 | 14.057 | 10.1031 | 23.244 | 34.7134 | 12.6897 | 9.1203 | 23.0309 | 34.7824 | 11.4182 | 8.2065 | 22.9607 | 34.8676 | 10.1029 | 7.2612 | 22.7243 | 34.984 | 8.8547 | 6.364 | 22.4594 | 35.1077 | 7.5671 | 5.4386 | 22.1442 | 35.2015 | 7.4453 | 5.3511 | 21.8314 | 35.2998 | 7.3396 | 5.2751 | 21.461 | 35.4038 | 7.2615 | 5.219 | 21.1151 | 35.5237 | 7.1518 | 5.1402 | 20.7703 | 36.0017 | 6.9738 | 5.0122 | 19.6232 | 36.2897 | 8.7829 | 6.3125 | 19.188 | 36.4624 | 11.8807 | 8.5389 | 19.2184 | 36.5727 | 12.5999 | 9.0558 | 19.4388 | 34.585 | 14.0534 | 10.1005 | 23.3956 | 34.6342 | 12.8099 | 9.2068 | 23.3084 | 34.7159 | 11.5443 | 8.2971 | 23.0921 | 34.7887 | 10.261 | 7.3748 | 22.8374 | 34.8772 | 9.0079 | 6.4741 | 22.5826 | 34.9743 | 7.7348 | 5.5591 | 22.2846 | 35.0807 | 7.654 | 5.5011 | 21.9851 | 35.1828 | 7.5634 | 5.4359 | 21.622 | 35.2684 | 7.4674 | 5.367 | 21.2706 | 35.3552 | 7.3716 | 5.2981 | 20.9371 | 35.6473 | 7.2794 | 5.2319 | 20.0291 | 35.8943 | 8.4619 | 6.0818 | 19.4789 | 36.0254 | 10.5809 | 7.6047 | 19.2085 | 36.0836 | 10.9389 | 7.862 | 19.0979 | 34.6264 | 14.0533 | 10.1004 | 23.2482 | 34.7134 | 12.7863 | 9.1897 | 23.0381 | 34.7825 | 11.4929 | 8.2602 | 22.9653 | 34.8677 | 10.1547 | 7.2984 | 22.7555 | 34.9836 | 8.8333 | 6.3487 | 22.4989 | 35.1073 | 7.6219 | 5.478 | 22.1933 | 35.2008 | 7.5536 | 5.429 | 21.8897 | 35.2989 | 7.4665 | 5.3663 | 21.5289 | 35.4018 | 7.3723 | 5.2986 | 21.1972 | 35.5171 | 7.272 | 5.2266 | 20.8839 | 35.9696 | 7.1075 | 5.1083 | 19.8202 | 36.2262 | 9.1465 | 6.5738 | 19.4314 | 36.3823 | 12.3927 | 8.9069 | 19.4633 | 36.4766 | 13.0603 | 9.3867 | 19.6796 | 34.6243 | 14.0582 | 10.1039 | 23.2586 | 34.7168 | 12.6946 | 9.1239 | 23.0608 | 34.8047 | 11.4156 | 8.2046 | 23.0048 | 34.8938 | 10.127 | 7.2785 | 22.8265 | 35.0061 | 8.8572 | 6.3659 | 22.6174 | 35.1408 | 7.5671 | 5.4386 | 22.3734 | 35.2963 | 7.4591 | 5.361 | 22.1431 | 35.4658 | 7.3677 | 5.2953 | 21.8703 | 35.6481 | 7.2588 | 5.217 | 21.6503 | 35.8199 | 7.0914 | 5.0968 | 21.4605 | 36.3662 | 6.8894 | 4.9515 | 20.4008 | 36.8827 | 8.2533 | 5.9318 | 18.1926 | 37.1871 | 10.8947 | 7.8303 | 16.4906 | 37.3388 | 11.2788 | 8.1063 | 15.4227 | 34.6378 | 14.0597 | 10.105 | 23.2539 | 34.7482 | 13.8814 | 9.9768 | 23.042 | 34.8322 | 13.7371 | 9.8731 | 22.9707 | 34.9114 | 13.6655 | 9.8217 | 22.7976 | 35.0152 | 13.4811 | 9.6892 | 22.6213 | 35.1346 | 13.2673 | 9.5355 | 22.4265 | 35.278 | 13.2216 | 9.5026 | 22.2401 | 35.4282 | 13.1546 | 9.4545 | 22.0247 | 35.5968 | 13.0647 | 9.3898 | 21.8162 | 35.8103 | 12.8737 | 9.2526 | 21.3809 | 36.4304 | 12.7014 | 9.1287 | 18.7787 | 36.795 | 11.822 | 8.4967 | 16.7439 | 36.8572 | 11.4189 | 8.207 | 15.6739 | 36.7632 | 11.3912 | 8.187 | 16.1825
TRAFFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 22.633 | 7.456 | 5.439 | 9.0792 | 22.8079 | 7.1808 | 5.2383 | 7.6862 | 22.8275 | 7.1341 | 5.2043 | 7.6845 | 22.8562 | 7.0717 | 5.1587 | 7.6144 | 22.9054 | 6.9678 | 5.0829 | 7.4312 | 22.9812 | 6.8388 | 4.9888 | 7.1431 | 23.0597 | 6.7291 | 4.9088 | 6.8048 | 23.1403 | 6.7334 | 4.912 | 6.7168 | 23.2219 | 6.6765 | 4.8704 | 6.5942 | 23.3033 | 6.6011 | 4.8154 | 6.4039 | 24.2086 | 6.2765 | 4.5786 | 5.401 | 25.8733 | 6.1474 | 4.4844 | 3.951 | 27.0707 | 6.4932 | 4.7367 | 2.8169 | 28.0261 | 6.5837 | 4.8027 | 1.5441 | 22.4516 | 7.6252 | 5.5625 | 9.9476 | 22.4758 | 7.4955 | 5.4679 | 9.3464 | 22.5535 | 7.4768 | 5.4542 | 9.257 | 22.6447 | 7.4235 | 5.4154 | 9.0734 | 22.7291 | 7.3521 | 5.3632 | 8.8007 | 22.8194 | 7.284 | 5.3136 | 8.4895 | 22.9176 | 7.1909 | 5.2457 | 8.1187 | 23.0208 | 7.1444 | 5.2118 | 7.9628 | 23.1285 | 7.0847 | 5.1682 | 7.7581 | 23.2384 | 7.0092 | 5.1131 | 7.5183 | 23.8987 | 6.8001 | 4.9606 | 6.6555 | 24.7534 | 6.8627 | 5.0063 | 5.6513 | 25.7439 | 7.2268 | 5.2719 | 4.6707 | 26.5745 | 7.3415 | 5.3555 | 3.899 | 22.6336 | 7.6212 | 5.5595 | 9.0834 | 22.8095 | 7.4848 | 5.46 | 7.6999 | 22.8315 | 7.4487 | 5.4337 | 7.6944 | 22.8629 | 7.3802 | 5.3837 | 7.6239 | 22.9152 | 7.3202 | 5.34 | 7.4568 | 22.9938 | 7.2318 | 5.2755 | 7.1687 | 23.075 | 7.1229 | 5.1961 | 6.8348 | 23.1582 | 7.0399 | 5.1355 | 6.7462 | 23.2417 | 6.9446 | 5.066 | 6.6256 | 23.3227 | 6.8193 | 4.9746 | 6.4509 | 24.015 | 6.7532 | 4.9264 | 5.6174 | 24.9198 | 6.8166 | 4.9726 | 4.7651 | 26.0086 | 7.4605 | 5.4423 | 3.9265 | 26.7004 | 7.6567 | 5.5854 | 3.2296 | 22.6193 | 7.4614 | 5.443 | 9.1131 | 22.7819 | 7.1866 | 5.2425 | 7.7588 | 22.7977 | 7.1209 | 5.1946 | 7.8 | 22.8244 | 7.0614 | 5.1512 | 7.7557 | 22.8761 | 6.9606 | 5.0776 | 7.613 | 22.9907 | 6.7761 | 4.9431 | 7.3442 | 23.1435 | 6.8018 | 4.9618 | 7.0426 | 23.3311 | 6.7679 | 4.9371 | 6.9364 | 23.5496 | 6.6995 | 4.8872 | 6.7157 | 23.7944 | 6.6257 | 4.8334 | 6.5242 | 25.7759 | 6.1048 | 4.4534 | 4.5114 | 28.2626 | 5.5995 | 4.0847 | 1.4786 | 29.4514 | 5.7269 | 4.1777 | -0.63787 | 29.7483 | 5.7531 | 4.1968 | -1.6532 | 22.6445 | 7.4576 | 5.4402 | 9.0945 | 22.8403 | 7.1703 | 5.2306 | 7.7142 | 22.8488 | 7.0775 | 5.1629 | 7.7338 | 22.8993 | 6.8612 | 5.0052 | 7.6738 | 22.9793 | 6.9673 | 5.0825 | 7.5285 | 23.16 | 6.8763 | 5.0162 | 7.2115 | 23.4186 | 6.776 | 4.943 | 6.8601 | 23.7444 | 6.6859 | 4.8772 | 6.6218 | 24.1305 | 6.5885 | 4.8062 | 6.2794 | 24.556 | 6.4542 | 4.7083 | 5.741 | 26.9448 | 6.4135 | 4.6785 | 2.577 | 29.0822 | 5.5407 | 4.0418 | -0.28647 | 29.6766 | 5.5593 | 4.0554 | -1.691 | 29.5446 | 5.5608 | 4.0565 | -1.5141
TRAFFORD PARK NORTH | BARTON | CARRINGTON | 378738 | 397694 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -2.7706 | 2.6914 | 0.43658 | 0.31848 | -3.2928 | 7.3286 | 1.1888 | 0.86719 | -3.0603 | 36.446 | 8.0657 | 5.8838 | -2.8381 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.1863 | 0.84127 | 0.6137 | 5.1863 | 28.1668 | 6.5716 | 4.7939 | 5.5278 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -2.6844 | 2.6914 | 0.43658 | 0.31848 | -2.8047 | 17.9749 | 2.9157 | 2.127 | -2.5197 | 35.6476 | 9.598 | 7.0016 | -2.0155 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -2.2452 | 2.6914 | 0.43658 | 0.31848 | -3.3933 | 6.0522 | 0.98172 | 0.71615 | -3.6341 | 36.4841 | 7.8399 | 5.7191 | -3.1641 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -3.936 | 2.6914 | 0.43658 | 0.31848 | -3.2832 | 2.6914 | 0.43658 | 0.31848 | -2.8762 | 2.6914 | 0.43658 | 0.31848 | -2.5261 | 2.6914 | 0.43658 | 0.31848 | -3.0407 | 2.6914 | 0.43658 | 0.31848 | -4.2535 | 37.1034 | 7.6814 | 5.6035 | -4.3072 | 36.6268 | 7.8677 | 5.7394 | -3.3097
TRIMPELL | - | HEYSHAM | 341861 | 458979 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795
TRINITY | FREDERICK RD | KEARSLEY | 382649 | 398230 | -15.3042 | -2.4825 | -1.8109 | -15.3042 | -18.0078 | -2.921 | -2.1309 | -18.0078 | -19.0675 | -3.0929 | -2.2563 | -19.0675 | -19.4484 | -3.1547 | -2.3013 | -19.4484 | -19.8438 | -3.2189 | -2.3481 | -19.8438 | -20.4565 | -3.3182 | -2.4206 | -20.4565 | -20.4202 | -3.3124 | -2.4163 | -20.4202 | -20.6864 | -3.3555 | -2.4478 | -20.6864 | -20.8871 | -3.3881 | -2.4716 | -20.8871 | -21.4147 | -3.4737 | -2.534 | -21.4147 | -22.7352 | -3.6879 | -2.6902 | -22.7352 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | -13.7247 | -2.2263 | -1.624 | -13.7247 | -15.2418 | -2.4724 | -1.8036 | -15.2418 | -16.1441 | -2.6187 | -1.9103 | -16.1441 | -16.7483 | -2.7167 | -1.9818 | -16.7483 | -17.3984 | -2.8222 | -2.0588 | -17.3984 | -17.8661 | -2.8981 | -2.1141 | -17.8661 | -18.3214 | -2.9719 | -2.168 | -18.3214 | -18.6981 | -3.033 | -2.2125 | -18.6981 | -19.0489 | -3.0899 | -2.2541 | -19.0489 | -19.5673 | -3.174 | -2.3154 | -19.5673 | -20.7315 | -3.3629 | -2.4532 | -20.7315 | -20.8261 | -3.3782 | -2.4644 | -20.8261 | -20.3218 | -3.2964 | -2.4047 | -20.3218 | -20.4719 | -3.3207 | -2.4224 | -20.4719 | -13.7259 | -2.2265 | -1.6242 | -13.7259 | -15.1395 | -2.4558 | -1.7915 | -15.1395 | -16.1315 | -2.6167 | -1.9088 | -16.1315 | -16.9106 | -2.7431 | -2.001 | -16.9106 | -17.5339 | -2.8442 | -2.0748 | -17.5339 | -18.3503 | -2.9766 | -2.1714 | -18.3503 | -18.7613 | -3.0433 | -2.22 | -18.7613 | -19.1697 | -3.1095 | -2.2684 | -19.1697 | -19.6605 | -3.1891 | -2.3264 | -19.6605 | -20.2218 | -3.2802 | -2.3928 | -20.2218 | -20.8154 | -3.3765 | -2.4631 | -20.8154 | -21.7969 | -3.5357 | -2.5792 | -21.7969 | -21.2728 | -3.4507 | -2.5172 | -21.2728 | -21.5441 | -3.4947 | -2.5493 | -21.5441 | -15.2624 | -2.4757 | -1.806 | -15.2624 | -17.8649 | -2.8979 | -2.114 | -17.8649 | -18.8836 | -3.0631 | -2.2345 | -18.8836 | -19.3125 | -3.1327 | -2.2852 | -19.3125 | -19.7356 | -3.2013 | -2.3353 | -19.7356 | -20.1573 | -3.2697 | -2.3852 | -20.1573 | -20.2672 | -3.2875 | -2.3982 | -20.2672 | -20.5598 | -3.335 | -2.4328 | -20.5598 | -20.9096 | -3.3917 | -2.4742 | -20.9096 | -21.4773 | -3.4838 | -2.5414 | -21.4773 | -22.9936 | -3.7298 | -2.7208 | -22.9936 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | -15.2423 | -2.4725 | -1.8036 | -15.2423 | -17.4587 | -2.832 | -2.0659 | -17.4587 | -18.2031 | -2.9527 | -2.154 | -18.2031 | -18.4853 | -2.9985 | -2.1874 | -18.4853 | -18.7783 | -3.046 | -2.222 | -18.7783 | -18.9266 | -3.0701 | -2.2396 | -18.9266 | -19.549 | -3.171 | -2.3132 | -19.549 | -19.6643 | -3.1897 | -2.3269 | -19.6643 | -19.8999 | -3.228 | -2.3548 | -19.8999 | -20.5269 | -3.3297 | -2.4289 | -20.5269 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
TULKETH | RIBBLE | PENWORTHAM EAST / ROCHDALE | 352393 | 431036 | 30.839 | 9.202 | 6.7127 | 10.6826 | 30.9125 | 9.0765 | 6.6212 | 9.6193 | 30.9502 | 9.0034 | 6.5679 | 8.9229 | 31.0247 | 8.9103 | 6.5 | 8.4341 | 31.1189 | 8.7612 | 6.3911 | 8.2703 | 31.2357 | 8.6593 | 6.3168 | 7.7435 | 31.367 | 8.5784 | 6.2578 | 7.1741 | 31.5086 | 8.4415 | 6.158 | 6.6829 | 31.6602 | 8.2961 | 6.0519 | 6.2207 | 31.8266 | 8.0922 | 5.9032 | 5.5232 | 32.4535 | 7.2263 | 5.2715 | 3.4203 | 32.9141 | 6.6262 | 4.8337 | 2.4951 | 33.1805 | 6.448 | 4.7037 | 2.2282 | 33.3235 | 6.2576 | 4.5648 | 2.5727 | 30.7938 | 9.2158 | 6.7228 | 11.2606 | 30.8359 | 9.1158 | 6.6498 | 10.7269 | 30.914 | 9.008 | 6.5712 | 10.14 | 31.0114 | 8.887 | 6.4829 | 9.6611 | 31.1205 | 8.7946 | 6.4155 | 9.5075 | 31.2437 | 8.6162 | 6.2854 | 9.0162 | 31.3809 | 8.5155 | 6.212 | 8.4736 | 31.5281 | 8.3954 | 6.1244 | 7.9964 | 31.6865 | 8.2609 | 6.0262 | 7.5324 | 31.8544 | 8.1095 | 5.9158 | 6.9061 | 32.2227 | 7.768 | 5.6667 | 5.3248 | 32.499 | 7.4537 | 5.4374 | 4.3831 | 32.6398 | 7.2312 | 5.275 | 3.801 | 32.692 | 7.1074 | 5.1847 | 3.6357 | 30.8399 | 9.2155 | 6.7226 | 10.6934 | 30.9137 | 9.1326 | 6.6621 | 9.6482 | 30.9517 | 8.9851 | 6.5545 | 8.989 | 31.0262 | 8.7774 | 6.403 | 8.5087 | 31.1196 | 8.6836 | 6.3345 | 8.3728 | 31.2353 | 8.5236 | 6.2179 | 7.8684 | 31.3653 | 8.3946 | 6.1237 | 7.3212 | 31.5054 | 8.248 | 6.0168 | 6.8505 | 31.6538 | 8.0928 | 5.9036 | 6.4166 | 31.8109 | 7.9319 | 5.7862 | 5.7829 | 32.3954 | 7.2874 | 5.316 | 3.8828 | 32.8029 | 6.7587 | 4.9304 | 3.089 | 33.024 | 6.3469 | 4.63 | 2.8736 | 33.145 | 6.251 | 4.56 | 3.2003 | 30.8354 | 9.2114 | 6.7196 | 10.6985 | 30.9089 | 9.1025 | 6.6401 | 9.648 | 30.9587 | 9.0393 | 6.5941 | 8.9661 | 31.0446 | 8.8873 | 6.4832 | 8.4853 | 31.1665 | 8.736 | 6.3728 | 8.356 | 31.3246 | 8.6636 | 6.32 | 7.8629 | 31.5131 | 8.5313 | 6.2235 | 7.3139 | 31.7261 | 8.3647 | 6.1019 | 6.8411 | 31.9607 | 8.192 | 5.9759 | 6.4664 | 32.2207 | 7.9605 | 5.807 | 5.9241 | 33.1027 | 6.6772 | 4.8709 | 2.8171 | 29.2631 | 4.7468 | 3.4627 | -4.0166 | 22.4655 | 3.6441 | 2.6583 | -9.6982 | 16.2386 | 2.6341 | 1.9215 | -13.3029 | 30.8288 | 9.2147 | 6.722 | 10.7032 | 30.9093 | 9.1794 | 6.6963 | 9.6199 | 30.946 | 9.1043 | 6.6415 | 8.9354 | 31.0194 | 8.9669 | 6.5412 | 8.4871 | 31.1273 | 8.8423 | 6.4503 | 8.4034 | 31.2651 | 8.7338 | 6.3712 | 7.9804 | 31.4362 | 8.6119 | 6.2822 | 7.5001 | 31.6236 | 8.4527 | 6.1661 | 7.1117 | 31.838 | 8.2637 | 6.0282 | 6.5993 | 32.123 | 7.8071 | 5.6952 | 4.8183 | 33.0819 | 5.7289 | 4.1791 | -3.0649 | 24.834 | 4.0283 | 2.9386 | -9.2108 | 19.5283 | 3.1677 | 2.3108 | -13.0281 | 19.3025 | 3.1311 | 2.2841 | -11.7862
ULVERSTON | ULVERSTON | HARKER / HUTTON | 327495 | 477808 | 15.2514 | 11.1079 | 7.9834 | 7.5878 | 15.308 | 10.902 | 7.8355 | 6.7558 | 15.3507 | 10.7511 | 7.727 | 6.2723 | 15.4137 | 10.5876 | 7.6095 | 6.0424 | 15.4964 | 10.3105 | 7.4104 | 5.8012 | 15.5958 | 10.0975 | 7.2573 | 5.4791 | 15.7132 | 9.8388 | 7.0714 | 5.1274 | 15.8418 | 9.7208 | 6.9866 | 4.8161 | 15.9805 | 9.5766 | 6.8829 | 4.4877 | 16.1108 | 9.4036 | 6.7585 | 4.0593 | 16.5006 | 8.712 | 6.2615 | 2.6027 | 16.7934 | 8.1891 | 5.8856 | 1.834 | 16.9571 | 7.8849 | 5.667 | 1.619 | 17.0385 | 7.8132 | 5.6155 | 1.7878 | 15.2353 | 11.1754 | 8.032 | 8.0031 | 15.2823 | 11.0588 | 7.9482 | 7.5647 | 15.3542 | 10.9379 | 7.8613 | 7.1668 | 15.4353 | 10.8214 | 7.7775 | 6.9297 | 15.5282 | 10.6914 | 7.6841 | 6.6906 | 15.6321 | 10.5989 | 7.6176 | 6.3786 | 15.7505 | 10.4976 | 7.5449 | 6.0318 | 15.8791 | 10.3904 | 7.4678 | 5.7158 | 16.0092 | 10.2729 | 7.3833 | 5.3769 | 16.1029 | 10.1521 | 7.2965 | 5.0046 | 16.2918 | 9.7828 | 7.0311 | 4.0442 | 16.4519 | 9.4491 | 6.7912 | 3.2805 | 16.5607 | 9.2176 | 6.6249 | 2.8208 | 16.6258 | 9.0591 | 6.511 | 2.5667 | 15.2514 | 11.1727 | 8.03 | 7.596 | 15.3081 | 11.0434 | 7.9371 | 6.776 | 15.3508 | 10.8956 | 7.8309 | 6.3055 | 15.4139 | 10.7311 | 7.7127 | 6.0889 | 15.4963 | 10.6184 | 7.6316 | 5.8618 | 15.5952 | 10.4469 | 7.5084 | 5.5553 | 15.7121 | 10.2864 | 7.393 | 5.2191 | 15.8404 | 10.1375 | 7.286 | 4.9221 | 15.9773 | 9.9827 | 7.1747 | 4.6136 | 16.103 | 9.8208 | 7.0584 | 4.2275 | 16.4701 | 9.2346 | 6.6371 | 2.9081 | 16.7259 | 8.8071 | 6.3298 | 2.2377 | 16.874 | 8.5157 | 6.1204 | 2.0595 | 16.9351 | 8.35 | 6.0013 | 2.2238 | 15.2492 | 11.1077 | 7.9833 | 7.596 | 15.3078 | 10.8781 | 7.8183 | 6.7637 | 15.3619 | 10.7012 | 7.6911 | 6.2786 | 15.4458 | 10.4628 | 7.5198 | 6.0454 | 15.562 | 10.2064 | 7.3356 | 5.8053 | 15.7098 | 9.9191 | 7.1291 | 5.4773 | 15.8959 | 9.7492 | 7.007 | 5.0999 | 16.0536 | 9.5766 | 6.8829 | 4.7629 | 16.1878 | 9.3753 | 6.7382 | 4.4579 | 16.3377 | 9.1866 | 6.6026 | 4.1222 | 16.9124 | 8.151 | 5.8583 | 2.1721 | 17.5399 | 6.7566 | 4.8561 | -1.7784 | 17.7648 | 5.8518 | 4.2058 | -4.7654 | 17.8654 | 5.2507 | 3.7738 | -6.7492 | 15.2425 | 11.1121 | 7.9865 | 7.6068 | 15.3045 | 10.9432 | 7.8651 | 6.7642 | 15.3606 | 10.762 | 7.7349 | 6.2811 | 15.44 | 10.5234 | 7.5634 | 6.0638 | 15.5506 | 10.2364 | 7.3571 | 5.8339 | 15.6861 | 9.8935 | 7.1106 | 5.537 | 15.8534 | 9.7159 | 6.983 | 5.2046 | 15.9862 | 9.5357 | 6.8535 | 4.9247 | 16.1342 | 9.3202 | 6.6986 | 4.5662 | 16.3269 | 8.9717 | 6.4481 | 3.57 | 16.9916 | 7.4868 | 5.3809 | -0.97032 | 17.3795 | 6.1882 | 4.4476 | -4.4861 | 17.4674 | 5.6501 | 4.0608 | -6.424 | 17.3748 | 5.5474 | 3.987 | -5.7478
UNION RD | BOLTON | KEARSLEY | 372174 | 410598 | 31.8308 | 9.9132 | 7.2315 | 11.6149 | 31.8854 | 8.3613 | 6.0995 | 11.0335 | 31.9097 | 7.1549 | 5.2194 | 11.1931 | 31.9759 | 5.7391 | 4.1866 | 10.6934 | 26.9788 | 4.3762 | 3.1924 | 10.7196 | 17.9508 | 2.9118 | 2.1241 | 10.2022 | 17.1708 | 2.7853 | 2.0318 | 9.8246 | 16.4255 | 2.6644 | 1.9436 | 9.6092 | 15.2799 | 2.4786 | 1.8081 | 9.0436 | 13.5729 | 2.2017 | 1.6061 | 7.9471 | 10.6256 | 1.7236 | 1.2573 | 6.2069 | 20.962 | 3.4002 | 2.4804 | 4.4719 | 36.0847 | 6.4601 | 4.7125 | 3.8291 | 36.4438 | 7.0872 | 5.17 | 3.8063 | 31.8068 | 10.0351 | 7.3205 | 11.7537 | 31.8484 | 8.6085 | 6.2798 | 11.2771 | 31.9229 | 7.2504 | 5.289 | 11.3165 | 32.0264 | 5.7553 | 4.1984 | 10.7779 | 27.1469 | 4.4035 | 3.2123 | 10.7892 | 18.2439 | 2.9593 | 2.1588 | 10.2709 | 17.5836 | 2.8522 | 2.0807 | 9.8823 | 17.0161 | 2.7602 | 2.0135 | 9.5733 | 16.1642 | 2.622 | 1.9127 | 9.0538 | 15.3255 | 2.486 | 1.8135 | 8.5058 | 14.608 | 2.3696 | 1.7286 | 7.2104 | 21.2914 | 3.4537 | 2.5194 | 6.2939 | 32.2362 | 5.229 | 3.8145 | 5.5283 | 34.6732 | 5.7353 | 4.1839 | 5.1557 | 31.8348 | 10.031 | 7.3175 | 11.5882 | 31.8909 | 8.593 | 6.2685 | 11.0776 | 31.9163 | 7.1959 | 5.2493 | 11.2555 | 31.9831 | 5.7068 | 4.163 | 10.7785 | 26.598 | 4.3145 | 3.1473 | 10.8188 | 17.5441 | 2.8458 | 2.076 | 10.3251 | 16.8724 | 2.7369 | 1.9965 | 9.9678 | 16.2338 | 2.6333 | 1.9209 | 9.7689 | 15.2777 | 2.4782 | 1.8078 | 9.2344 | 14.1796 | 2.3001 | 1.6779 | 8.1928 | 12.0672 | 1.9574 | 1.4279 | 6.6283 | 24.4056 | 3.9588 | 2.8879 | 5.1122 | 35.632 | 7.0138 | 5.1165 | 4.7161 | 35.8374 | 7.5647 | 5.5184 | 4.8423 | 31.8313 | 9.9058 | 7.2262 | 11.6209 | 31.8844 | 8.4172 | 6.1402 | 11.0439 | 31.9136 | 7.2068 | 5.2573 | 11.2076 | 31.9934 | 5.7172 | 4.1706 | 10.7057 | 26.8583 | 4.3567 | 3.1781 | 10.7298 | 17.8038 | 2.888 | 2.1067 | 10.1954 | 16.833 | 2.7305 | 1.9918 | 9.7689 | 15.4754 | 2.5103 | 1.8312 | 8.9562 | 14.237 | 2.3094 | 1.6847 | 8.4132 | 13.034 | 2.1142 | 1.5423 | 7.9266 | 8.3202 | 1.3496 | 0.98452 | 4.6073 | 13.0666 | 2.1195 | 1.5462 | -0.8593 | 26.9655 | 4.3741 | 3.1908 | -5.2132 | 27.2916 | 4.427 | 3.2294 | -7.9255 | 31.8179 | 9.912 | 7.2307 | 11.6521 | 31.8657 | 9.8361 | 7.1753 | 11.0893 | 31.8921 | 9.8767 | 7.2049 | 11.2753 | 31.9626 | 9.6872 | 7.0666 | 10.8248 | 32.0694 | 9.6155 | 7.0144 | 10.8855 | 33.5168 | 9.1922 | 6.7056 | 9.1069 | 34.2357 | 8.9306 | 6.5147 | 8.2448 | 34.3872 | 8.7771 | 6.4027 | 8.1342 | 34.5866 | 8.5253 | 6.2191 | 7.6358 | 34.8386 | 8.0285 | 5.8567 | 6.2874 | 36.1827 | 6.6428 | 4.8458 | 0.33877 | 32.1141 | 5.2092 | 3.8001 | -4.4512 | 27.6255 | 4.4811 | 3.2689 | -7.3353 | 27.8038 | 4.5101 | 3.29 | -6.3066
UPHOLLAND | ORRELL | WASHWAY FARM / KIRKBY | 352531 | 404369 | 22.6941 | 12.055 | 8.6642 | 7.0455 | 22.7516 | 11.8744 | 8.5344 | 6.5929 | 22.8027 | 11.7304 | 8.4309 | 6.2661 | 22.8795 | 11.5469 | 8.299 | 5.8334 | 22.98 | 11.3698 | 8.1717 | 5.2851 | 23.1005 | 11.1845 | 8.0385 | 4.6926 | 23.2391 | 11.0081 | 7.9117 | 4.0452 | 23.3909 | 10.8272 | 7.7817 | 3.3735 | 23.5522 | 10.6399 | 7.6471 | 2.7191 | 23.7368 | 10.4346 | 7.4995 | 1.9063 | 24.4455 | 9.5569 | 6.8687 | -0.93971 | 24.9127 | 9.0886 | 6.5322 | -2.2218 | 25.165 | 9.1214 | 6.5557 | -2.2761 | 25.3054 | 9.2036 | 6.6148 | -1.6665 | 22.6763 | 12.0879 | 8.6878 | 7.2536 | 22.7216 | 11.969 | 8.6024 | 7.0037 | 22.7935 | 11.8063 | 8.4854 | 6.6113 | 22.8736 | 11.6649 | 8.3838 | 6.2651 | 22.9658 | 11.5181 | 8.2783 | 5.8454 | 23.069 | 11.3732 | 8.1742 | 5.3935 | 23.1741 | 11.2492 | 8.085 | 4.892 | 23.2871 | 11.1209 | 7.9928 | 4.3679 | 23.4077 | 10.9958 | 7.9029 | 3.8354 | 23.5342 | 10.8685 | 7.8114 | 3.2983 | 23.8316 | 10.4226 | 7.4909 | 1.5531 | 24.0582 | 10.1379 | 7.2863 | 0.32011 | 24.2131 | 10.0422 | 7.2176 | -0.3506 | 24.3159 | 9.91 | 7.1225 | -0.68768 | 22.6941 | 12.0849 | 8.6857 | 7.0618 | 22.7517 | 11.956 | 8.593 | 6.6472 | 22.8028 | 11.7721 | 8.4609 | 6.3122 | 22.8796 | 11.6074 | 8.3424 | 5.8987 | 22.9797 | 11.4335 | 8.2175 | 5.3761 | 23.0994 | 11.252 | 8.087 | 4.81 | 23.2374 | 11.0895 | 7.9702 | 4.1887 | 23.3888 | 10.9319 | 7.857 | 3.5421 | 23.5477 | 10.7747 | 7.744 | 2.9218 | 23.7229 | 10.6209 | 7.6335 | 2.1924 | 24.3849 | 9.9701 | 7.1657 | -0.44833 | 24.8071 | 9.6184 | 6.9129 | -1.5583 | 25.0378 | 9.5768 | 6.8831 | -1.5734 | 25.1638 | 9.453 | 6.7941 | -1.0693 | 22.6923 | 12.057 | 8.6656 | 7.0722 | 22.7534 | 11.8763 | 8.5358 | 6.6544 | 22.8194 | 11.7115 | 8.4173 | 6.3168 | 22.9188 | 11.5204 | 8.2799 | 5.9283 | 23.0449 | 11.3476 | 8.1558 | 5.4469 | 23.2023 | 11.1236 | 7.9947 | 4.9142 | 23.3937 | 10.9174 | 7.8466 | 4.2943 | 23.6116 | 10.7095 | 7.6971 | 3.6531 | 23.8507 | 10.506 | 7.5508 | 3.1149 | 24.1189 | 10.2996 | 7.4025 | 2.568 | 25.0224 | 9.1578 | 6.5819 | -0.41716 | 25.8 | 7.8548 | 5.6454 | -5.9198 | 26.2482 | 7.1108 | 5.1107 | -9.8091 | 26.5193 | 6.5769 | 4.7269 | -12.5132 | 22.6901 | 12.0548 | 8.664 | 7.0206 | 22.7624 | 11.9065 | 8.5574 | 6.5075 | 22.8332 | 11.7635 | 8.4547 | 6.175 | 22.9233 | 11.5956 | 8.334 | 5.7989 | 23.0424 | 11.4381 | 8.2208 | 5.3267 | 23.1843 | 11.241 | 8.0791 | 4.8517 | 23.3616 | 11.0578 | 7.9475 | 4.3218 | 23.5556 | 10.8736 | 7.8151 | 3.8085 | 23.7712 | 10.6894 | 7.6827 | 3.2478 | 24.0582 | 10.2838 | 7.3912 | 1.882 | 25.0165 | 8.9748 | 6.4504 | -4.4061 | 25.5793 | 7.7628 | 5.5793 | -9.0304 | 25.7798 | 7.3043 | 5.2498 | -11.4283 | 25.6944 | 7.2681 | 5.2238 | -10.4215
URMSTON | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 28.9657 | 8.0962 | 5.9061 | 16.1207 | 29.0256 | 8.032 | 5.8592 | 15.7778 | 29.0829 | 7.98 | 5.8213 | 15.6517 | 29.1542 | 7.9292 | 5.7843 | 15.4569 | 29.2511 | 7.8885 | 5.7546 | 15.1463 | 29.3617 | 7.821 | 5.7053 | 14.7664 | 29.4854 | 7.7528 | 5.6556 | 14.3159 | 29.6198 | 7.6759 | 5.5995 | 14.0185 | 29.7655 | 7.5979 | 5.5426 | 13.6145 | 29.9404 | 7.4911 | 5.4647 | 13.1817 | 30.713 | 7.0375 | 5.1338 | 11.6644 | 31.3054 | 6.8981 | 5.0321 | 10.9069 | 31.5356 | 8.0407 | 5.8656 | 10.7417 | 31.6427 | 8.2176 | 5.9946 | 10.8506 | 28.9527 | 7.8765 | 5.7458 | 16.2639 | 28.9999 | 7.85 | 5.7265 | 16.0409 | 29.0669 | 7.817 | 5.7024 | 15.8409 | 29.1228 | 7.7729 | 5.6702 | 15.6405 | 29.1965 | 7.6879 | 5.6082 | 15.3535 | 29.279 | 7.6085 | 5.5503 | 15.0083 | 29.37 | 7.4983 | 5.4699 | 14.5905 | 29.4663 | 7.41 | 5.4055 | 14.321 | 29.5674 | 7.301 | 5.326 | 13.939 | 29.6716 | 7.1838 | 5.2405 | 13.5703 | 30.0348 | 7.0315 | 5.1294 | 12.4609 | 30.3283 | 6.9727 | 5.0865 | 11.7205 | 30.5221 | 7.8452 | 5.723 | 11.3409 | 30.676 | 8.3116 | 6.0632 | 11.1275 | 28.9657 | 7.8703 | 5.7413 | 16.1311 | 29.0256 | 7.8223 | 5.7062 | 15.8045 | 29.0829 | 7.7685 | 5.667 | 15.6933 | 29.1542 | 7.6869 | 5.6075 | 15.5097 | 29.2507 | 7.5799 | 5.5294 | 15.2148 | 29.3607 | 7.4589 | 5.4411 | 14.8513 | 29.484 | 7.3253 | 5.3437 | 14.4175 | 29.618 | 7.3303 | 5.3473 | 14.1336 | 29.7619 | 7.2914 | 5.319 | 13.7506 | 29.9297 | 7.2413 | 5.2824 | 13.359 | 30.6685 | 7.0365 | 5.133 | 11.9823 | 31.2316 | 7.1845 | 5.241 | 11.314 | 31.459 | 8.1892 | 5.9739 | 11.175 | 31.5618 | 8.4209 | 6.1429 | 11.2846 | 28.9661 | 8.099 | 5.9081 | 16.1339 | 29.0342 | 8.0434 | 5.8676 | 15.8054 | 29.1138 | 7.9948 | 5.8321 | 15.6948 | 29.2221 | 7.9423 | 5.7938 | 15.5127 | 29.3668 | 7.8903 | 5.7559 | 15.2285 | 29.5467 | 7.817 | 5.7024 | 14.877 | 29.7667 | 7.7468 | 5.6511 | 14.4482 | 30.0192 | 7.6826 | 5.6043 | 14.1704 | 30.2835 | 7.5958 | 5.541 | 13.8319 | 30.5767 | 7.499 | 5.4704 | 13.5045 | 31.4764 | 6.8203 | 4.9753 | 11.3224 | 32.0425 | 5.8491 | 4.2668 | 6.5426 | 32.3692 | 6.3615 | 4.6407 | 2.6758 | 32.5475 | 5.9682 | 4.3537 | -0.024257 | 28.9616 | 8.1017 | 5.9101 | 16.1319 | 29.0356 | 8.0802 | 5.8944 | 15.7755 | 29.1197 | 8.0495 | 5.872 | 15.6666 | 29.2281 | 7.9865 | 5.826 | 15.5152 | 29.3708 | 7.9713 | 5.815 | 15.2682 | 29.5414 | 7.8987 | 5.762 | 14.9718 | 29.7521 | 7.7938 | 5.6855 | 14.5943 | 29.9871 | 7.7335 | 5.6415 | 14.3792 | 30.3128 | 7.6263 | 5.5633 | 13.9517 | 30.7747 | 7.4017 | 5.3994 | 12.7981 | 31.4717 | 7.4281 | 5.4187 | 7.4459 | 31.8803 | 6.4163 | 4.6806 | 3.1192 | 32.0156 | 6.1353 | 4.4756 | 0.55078 | 31.9129 | 6.1296 | 4.4714 | 1.1953
VICTORIA PARK | LONGSIGHT | BREDBURY | 385373 | 395948 | 23.4492 | 14.4214 | 10.5202 | 10.5739 | 23.5813 | 13.1214 | 9.5719 | 10.2178 | 23.5685 | 11.4788 | 8.3736 | 8.0263 | 23.5872 | 9.8544 | 7.1886 | 5.9306 | 23.6204 | 8.2524 | 6.02 | 3.8257 | 23.6716 | 6.8815 | 5.02 | 1.5962 | 23.7198 | 6.4492 | 4.7046 | -0.66806 | 23.7621 | 6.2185 | 4.5363 | -1.7421 | 23.7997 | 6.0267 | 4.3964 | -2.8856 | 23.8357 | 5.8062 | 4.2355 | -3.9818 | 23.9648 | 5.7011 | 4.1589 | -4.0836 | 24.0193 | 5.72 | 4.1727 | -4.2656 | 24.0129 | 8.5483 | 6.2359 | -4.2009 | 23.9564 | 11.2482 | 8.2054 | -3.894 | 23.2921 | 14.5089 | 10.584 | 11.1793 | 23.2887 | 12.9478 | 9.4453 | 11.3307 | 23.3224 | 11.4306 | 8.3385 | 8.9675 | 23.3725 | 9.9056 | 7.226 | 6.7224 | 23.4275 | 8.3781 | 6.1117 | 4.5123 | 23.4829 | 6.8733 | 5.014 | 2.2421 | 23.5389 | 6.4502 | 4.7053 | -0.085114 | 23.5928 | 6.237 | 4.5498 | -1.2396 | 23.644 | 6.0069 | 4.382 | -2.4778 | 23.6922 | 5.7735 | 4.2117 | -3.68 | 23.8309 | 5.6992 | 4.1575 | -3.8983 | 23.9276 | 5.7183 | 4.1714 | -4.2782 | 23.9557 | 7.9169 | 5.7752 | -4.3774 | 23.9157 | 10.0475 | 7.3295 | -4.131 | 23.4492 | 14.5009 | 10.5782 | 10.5742 | 23.5813 | 13.2442 | 9.6614 | 10.2215 | 23.5685 | 11.6028 | 8.4641 | 8.0345 | 23.5872 | 10.0968 | 7.3655 | 5.9504 | 23.6204 | 8.6058 | 6.2778 | 3.8509 | 23.6714 | 7.1044 | 5.1826 | 1.6275 | 23.7195 | 6.6769 | 4.8707 | -0.63014 | 23.7619 | 6.4563 | 4.7098 | -1.698 | 23.7993 | 6.2225 | 4.5392 | -2.834 | 23.8344 | 5.983 | 4.3646 | -3.9341 | 23.96 | 5.8756 | 4.2862 | -4.0095 | 24.0117 | 5.9424 | 4.3349 | -4.1971 | 24.0038 | 8.8071 | 6.4246 | -4.1155 | 23.9469 | 11.5311 | 8.4118 | -3.8126 | 23.4377 | 14.4294 | 10.526 | 10.6198 | 23.5593 | 13.1326 | 9.5801 | 10.3113 | 23.5379 | 11.4862 | 8.379 | 8.168 | 23.5436 | 9.8433 | 7.1806 | 6.1214 | 23.5668 | 8.3488 | 6.0904 | 4.0661 | 23.6112 | 6.9314 | 5.0564 | 1.8878 | 23.6562 | 6.454 | 4.7081 | -0.32314 | 23.698 | 6.3195 | 4.61 | -1.3447 | 23.735 | 6.1138 | 4.4599 | -2.4335 | 23.7666 | 5.899 | 4.3033 | -3.475 | 23.8367 | 5.7884 | 4.2225 | -3.2913 | 23.8424 | 5.7334 | 4.1825 | -3.274 | 23.7655 | 8.5112 | 6.2088 | -2.9864 | 23.6413 | 11.2376 | 8.1976 | -2.4405 | 23.4432 | 14.4298 | 10.5263 | 10.6155 | 23.568 | 14.2236 | 10.3759 | 10.3022 | 23.5417 | 13.6612 | 9.9657 | 8.1633 | 23.5474 | 13.087 | 9.5468 | 6.1265 | 23.5723 | 12.6149 | 9.2024 | 4.0816 | 23.6171 | 12.263 | 8.9457 | 1.9167 | 23.6604 | 11.8552 | 8.6482 | -0.28105 | 23.6997 | 11.6688 | 8.5122 | -1.2864 | 23.7321 | 11.4494 | 8.3522 | -2.3565 | 23.7665 | 11.1649 | 8.1447 | -3.4078 | 23.8516 | 11.1164 | 8.1093 | -3.2808 | 23.8355 | 10.9015 | 7.9525 | -3.2308 | 23.735 | 11.139 | 8.1258 | -2.8874 | 23.5702 | 11.193 | 8.1651 | -2.2273
WARBRECK | BISPHAM | PENWORTHAM WEST / STANAH | 331775 | 438420 | 23.2484 | 13.2018 | 9.6305 | 10.8972 | 23.2611 | 12.6455 | 9.2247 | 10.7429 | 23.2706 | 12.3952 | 9.0421 | 10.6421 | 23.3012 | 11.9816 | 8.7404 | 10.4099 | 23.3439 | 11.6659 | 8.5101 | 10.2642 | 23.3977 | 11.4888 | 8.381 | 9.9993 | 23.4602 | 11.4046 | 8.3195 | 9.7432 | 23.5302 | 11.3105 | 8.2508 | 9.4542 | 23.6071 | 11.2136 | 8.1802 | 9.1805 | 23.6942 | 11.1055 | 8.1013 | 8.8358 | 24.1336 | 10.7106 | 7.8132 | 7.7784 | 24.6365 | 10.6641 | 7.7793 | 7.201 | 25.0226 | 11.354 | 8.2826 | 7.0821 | 25.4106 | 11.428 | 8.3365 | 7.1173 | 23.2352 | 12.8955 | 9.4071 | 10.9994 | 23.2426 | 12.7748 | 9.3191 | 10.9287 | 23.2679 | 12.1146 | 8.8375 | 10.7854 | 23.3091 | 12.0698 | 8.8047 | 10.5665 | 23.3518 | 11.7228 | 8.5516 | 10.4557 | 23.4021 | 11.5413 | 8.4192 | 10.2312 | 23.4599 | 11.4692 | 8.3667 | 10.0123 | 23.5236 | 11.4047 | 8.3195 | 9.7606 | 23.5929 | 11.3403 | 8.2726 | 9.5152 | 23.6667 | 11.2693 | 8.2208 | 9.2354 | 23.8949 | 11.0933 | 8.0924 | 8.5016 | 24.1311 | 11.0928 | 8.092 | 8.0038 | 24.371 | 11.5651 | 8.4365 | 7.7497 | 24.5817 | 11.9047 | 8.6843 | 7.6039 | 23.2486 | 12.8837 | 9.3985 | 10.9029 | 23.2615 | 12.7558 | 9.3052 | 10.7564 | 23.2713 | 12.354 | 9.0121 | 10.6637 | 23.3025 | 12.008 | 8.7596 | 10.438 | 23.3456 | 11.6464 | 8.4959 | 10.2988 | 23.3996 | 11.4706 | 8.3676 | 10.0417 | 23.4624 | 11.3933 | 8.3112 | 9.7927 | 23.5327 | 11.31 | 8.2505 | 9.5105 | 23.6089 | 11.2103 | 8.1777 | 9.2483 | 23.6924 | 11.1347 | 8.1226 | 8.9352 | 24.0723 | 10.899 | 7.9507 | 8.0066 | 24.413 | 10.9998 | 8.0242 | 7.6071 | 24.7176 | 11.9487 | 8.7164 | 7.5502 | 24.9673 | 11.9288 | 8.7019 | 7.6831 | 23.2464 | 13.2045 | 9.6325 | 10.9084 | 23.2611 | 12.6311 | 9.2142 | 10.767 | 23.2756 | 12.4129 | 9.0551 | 10.6854 | 23.3182 | 11.8967 | 8.6785 | 10.4765 | 23.3801 | 11.6638 | 8.5086 | 10.3609 | 23.4662 | 11.4892 | 8.3812 | 10.1244 | 23.5758 | 11.3909 | 8.3095 | 9.8886 | 23.7055 | 11.2848 | 8.2321 | 9.6196 | 23.8487 | 11.1625 | 8.1429 | 9.4046 | 24.0109 | 11.0842 | 8.0858 | 9.1537 | 24.8979 | 10.5116 | 7.668 | 7.5591 | 25.9987 | 9.9185 | 7.2354 | 4.1802 | 26.5328 | 10.0774 | 7.3514 | 1.6024 | 26.7728 | 9.7073 | 7.0813 | -0.17301 | 23.2432 | 13.2052 | 9.633 | 10.9078 | 23.2598 | 12.7214 | 9.2801 | 10.7375 | 23.2762 | 12.6106 | 9.1993 | 10.6481 | 23.3165 | 11.968 | 8.7305 | 10.46 | 23.3775 | 12.0624 | 8.7994 | 10.3689 | 23.4681 | 11.9245 | 8.6987 | 10.168 | 23.5896 | 11.8323 | 8.6315 | 9.9591 | 23.7321 | 11.737 | 8.562 | 9.7237 | 23.9067 | 11.6279 | 8.4824 | 9.4524 | 24.1975 | 11.4357 | 8.3422 | 8.6328 | 25.3967 | 11.0907 | 8.0905 | 4.8537 | 26.1381 | 10.2335 | 7.4652 | 1.7851 | 26.4236 | 9.8517 | 7.1867 | 0.14129 | 26.3597 | 9.8652 | 7.1965 | 0.73548
WARDLEWORTH | BELFIELD | ROCHDALE | 390339 | 414050 | 31.5868 | 8.5014 | 6.2016 | 14.0372 | 31.6768 | 8.3784 | 6.1119 | 13.8721 | 31.706 | 8.1225 | 5.9253 | 13.6466 | 31.7675 | 8.0623 | 5.8813 | 13.6011 | 31.854 | 7.9412 | 5.793 | 13.4467 | 31.9621 | 7.7679 | 5.6666 | 13.0344 | 32.0636 | 7.5814 | 5.5305 | 12.6501 | 32.1713 | 7.5433 | 5.5028 | 12.3485 | 32.279 | 7.4735 | 5.4518 | 12.2369 | 32.3979 | 7.3189 | 5.339 | 11.7775 | 32.8973 | 6.7225 | 4.9039 | 10.234 | 33.3193 | 6.4231 | 4.6856 | 9.4421 | 33.5974 | 6.6088 | 4.821 | 9.2215 | 33.8146 | 6.7032 | 4.8899 | 9.0517 | 31.5145 | 8.5732 | 6.254 | 14.2829 | 31.5448 | 8.5222 | 6.2168 | 14.3163 | 31.6077 | 8.3947 | 6.1238 | 13.9862 | 31.6853 | 8.2966 | 6.0522 | 13.8869 | 31.7729 | 8.1798 | 5.9671 | 13.7091 | 31.8679 | 8.0583 | 5.8784 | 13.3048 | 31.9712 | 7.9565 | 5.8042 | 12.9182 | 32.0797 | 7.8754 | 5.745 | 12.6077 | 32.1934 | 7.7952 | 5.6865 | 12.3078 | 32.2994 | 7.6926 | 5.6116 | 11.8866 | 32.5954 | 7.4324 | 5.4218 | 10.6842 | 32.8645 | 7.295 | 5.3216 | 9.83 | 33.0745 | 7.4014 | 5.3992 | 9.2958 | 33.2196 | 7.4856 | 5.4606 | 8.9809 | 31.5869 | 8.5739 | 6.2546 | 14.044 | 31.6769 | 8.5177 | 6.2135 | 13.8858 | 31.7064 | 8.3643 | 6.1017 | 13.6694 | 31.7681 | 8.2102 | 5.9893 | 13.6307 | 31.8545 | 8.042 | 5.8665 | 13.4851 | 31.9623 | 7.987 | 5.8264 | 13.0839 | 32.0637 | 7.8937 | 5.7584 | 12.7103 | 32.1713 | 7.81 | 5.6973 | 12.4187 | 32.278 | 7.7207 | 5.6321 | 12.3227 | 32.3921 | 7.6192 | 5.5581 | 11.9613 | 32.8544 | 7.2313 | 5.2751 | 10.5306 | 33.2044 | 7.022 | 5.1224 | 9.8154 | 33.4463 | 7.154 | 5.2188 | 9.61 | 33.6081 | 7.2091 | 5.259 | 9.5108 | 31.5799 | 8.5014 | 6.2017 | 14.0526 | 31.6665 | 8.3816 | 6.1143 | 13.8999 | 31.7025 | 8.169 | 5.9592 | 13.6823 | 31.7813 | 8.0238 | 5.8533 | 13.6363 | 31.8841 | 7.8678 | 5.7394 | 13.4809 | 32.0039 | 7.7061 | 5.6215 | 13.0559 | 32.1369 | 7.5829 | 5.5316 | 12.6335 | 32.2864 | 7.4616 | 5.4431 | 12.2848 | 32.4482 | 7.3448 | 5.358 | 12.1509 | 32.6267 | 7.1057 | 5.1835 | 11.768 | 33.3713 | 6.4717 | 4.721 | 10.0642 | 34.2078 | 5.5589 | 4.0552 | 6.0882 | 31.4549 | 5.1023 | 3.7221 | 2.9598 | 29.5403 | 4.7917 | 3.4955 | 0.82407 | 31.5732 | 8.5467 | 6.2347 | 14.073 | 31.6645 | 8.4814 | 6.1871 | 13.9244 | 31.7068 | 8.3407 | 6.0845 | 13.7151 | 31.7643 | 8.1639 | 5.9554 | 13.6899 | 31.8487 | 8.0652 | 5.8835 | 13.5492 | 31.96 | 7.7608 | 5.6614 | 13.1525 | 32.0954 | 7.7286 | 5.6379 | 12.7646 | 32.246 | 7.6513 | 5.5815 | 12.4559 | 32.4168 | 7.5314 | 5.494 | 12.2847 | 32.6592 | 7.2553 | 5.2926 | 11.3774 | 33.6172 | 6.1584 | 4.4924 | 7.0686 | 31.9752 | 5.1867 | 3.7836 | 3.4483 | 31.0999 | 5.0447 | 3.68 | 1.3622 | 30.7757 | 4.9921 | 3.6417 | 1.8222
WARTON | PEEL | PENWORTHAM WEST / STANAH | 341290 | 428540 | 29.9882 | 13.39 | 9.7678 | 13.543 | 30.0944 | 13.4052 | 9.7789 | 13.1178 | 30.1156 | 13.5848 | 9.9099 | 13.0105 | 30.1638 | 13.6689 | 9.9712 | 12.841 | 30.2311 | 13.6771 | 9.9773 | 12.5967 | 30.3174 | 13.5452 | 9.8811 | 12.3329 | 30.4091 | 13.418 | 9.7883 | 12.0387 | 30.569 | 13.2975 | 9.7003 | 11.6504 | 30.6494 | 13.1456 | 9.5896 | 11.3947 | 30.7325 | 12.9194 | 9.4245 | 11.1951 | 31.0662 | 13.0759 | 9.5387 | 10.1824 | 31.292 | 12.8748 | 9.392 | 9.7224 | 31.3933 | 12.6948 | 9.2606 | 9.6896 | 31.4099 | 12.7226 | 9.281 | 9.9484 | 29.8952 | 13.3917 | 9.7691 | 13.9313 | 29.9199 | 13.3356 | 9.7282 | 13.8469 | 29.9749 | 13.255 | 9.6693 | 13.6306 | 30.0409 | 13.353 | 9.7408 | 13.4156 | 30.1137 | 13.3767 | 9.7581 | 13.1596 | 30.1903 | 13.3763 | 9.7579 | 12.9267 | 30.2722 | 13.3658 | 9.7502 | 12.6529 | 30.3561 | 13.338 | 9.7299 | 12.345 | 30.4382 | 13.2926 | 9.6968 | 12.0716 | 30.5102 | 13.2725 | 9.6821 | 11.9044 | 30.7274 | 13.1739 | 9.6102 | 11.1823 | 30.8888 | 13.1143 | 9.5667 | 10.7008 | 30.969 | 13.1807 | 9.6151 | 10.4733 | 30.9871 | 13.3134 | 9.7119 | 10.4546 | 29.9894 | 13.3771 | 9.7584 | 13.5454 | 30.096 | 13.644 | 9.9531 | 13.1229 | 30.1174 | 13.6961 | 9.9911 | 13.0184 | 30.1658 | 13.5662 | 9.8963 | 12.852 | 30.2328 | 13.4451 | 9.808 | 12.6115 | 30.318 | 13.03 | 9.5052 | 12.352 | 30.4081 | 12.9313 | 9.4332 | 12.0622 | 30.5659 | 12.9305 | 9.4326 | 11.6785 | 30.6464 | 12.8965 | 9.4078 | 11.4294 | 30.7256 | 12.8563 | 9.3785 | 11.2427 | 31.0425 | 12.5249 | 9.1368 | 10.2634 | 31.2455 | 12.3786 | 9.03 | 9.8224 | 31.3259 | 12.359 | 9.0157 | 9.7935 | 31.3324 | 12.4024 | 9.0474 | 10.0466 | 29.9818 | 13.3965 | 9.7725 | 13.5741 | 30.0827 | 13.4186 | 9.7887 | 13.1721 | 30.1035 | 14.1444 | 10.3182 | 13.0884 | 30.1544 | 13.9822 | 10.1998 | 12.9575 | 30.231 | 13.7258 | 10.0128 | 12.7499 | 30.3905 | 13.5028 | 9.8501 | 12.4446 | 30.4707 | 13.5047 | 9.8515 | 12.1708 | 30.556 | 13.4276 | 9.7952 | 11.863 | 30.6433 | 13.3779 | 9.759 | 11.6326 | 30.7356 | 13.312 | 9.7109 | 11.5133 | 32.274 | 12.7546 | 9.3043 | 9.6178 | 32.5822 | 12.3835 | 9.0336 | 8.7698 | 32.7001 | 12.1563 | 8.8679 | 8.1733 | 32.7359 | 11.9841 | 8.7422 | 7.5293 | 29.9792 | 13.3977 | 9.7734 | 13.5785 | 30.0835 | 13.434 | 9.7999 | 13.1683 | 30.1086 | 13.6238 | 9.9383 | 13.0801 | 30.1616 | 13.7083 | 10 | 12.9456 | 30.3125 | 13.671 | 9.9728 | 12.667 | 30.3908 | 13.5492 | 9.8839 | 12.4507 | 30.4704 | 13.3788 | 9.7596 | 12.2021 | 31.9959 | 13.1623 | 9.6017 | 10.4823 | 32.0081 | 13.1792 | 9.614 | 10.3707 | 32.0421 | 13.1578 | 9.5984 | 10.2534 | 32.304 | 12.8334 | 9.3618 | 9.1978 | 32.5493 | 12.3785 | 9.0299 | 8.5549 | 32.5999 | 12.3807 | 9.0315 | 8.2371 | 32.5241 | 12.2745 | 8.9541 | 8.4497
WATERHEAD | GREENHILL | WHITEGATE | 394942 | 405940 | 29.9683 | 13.3962 | 9.7723 | 19.1953 | 30.0164 | 13.1011 | 9.5571 | 19.0358 | 30.0405 | 12.7818 | 9.3241 | 18.8968 | 30.0806 | 12.4366 | 9.0723 | 18.7655 | 30.1352 | 12.0584 | 8.7964 | 18.4935 | 30.2014 | 11.7707 | 8.5866 | 18.2314 | 30.2742 | 11.7206 | 8.55 | 17.9841 | 30.3526 | 11.6423 | 8.4929 | 17.693 | 30.4361 | 11.5685 | 8.4391 | 17.3775 | 30.5298 | 11.4586 | 8.3589 | 17.0297 | 30.9155 | 11.0893 | 8.0895 | 15.8329 | 31.2173 | 10.9708 | 8.0031 | 15.1826 | 31.4115 | 11.7132 | 8.5446 | 14.9828 | 31.5501 | 11.5582 | 8.4315 | 15.027 | 29.9391 | 13.3111 | 9.7102 | 19.2384 | 29.9651 | 12.9245 | 9.4282 | 19.1109 | 30.0114 | 12.5626 | 9.1643 | 18.9252 | 30.0641 | 12.1694 | 8.8774 | 18.8006 | 30.1223 | 11.7794 | 8.5929 | 18.5522 | 30.1865 | 11.5077 | 8.3947 | 18.3156 | 30.257 | 11.4492 | 8.352 | 18.0908 | 30.3322 | 11.3779 | 8.3 | 17.8226 | 30.4119 | 11.3057 | 8.2474 | 17.5265 | 30.4952 | 11.2328 | 8.1942 | 17.2441 | 30.6934 | 11.0213 | 8.0399 | 16.3962 | 30.8625 | 10.9091 | 7.958 | 15.7618 | 30.9861 | 11.3974 | 8.3142 | 15.3677 | 31.0753 | 11.8036 | 8.6106 | 15.0977 | 29.9684 | 13.3112 | 9.7103 | 19.2023 | 30.0164 | 12.9357 | 9.4364 | 19.0502 | 30.0406 | 12.5071 | 9.1238 | 18.9186 | 30.0807 | 12.0732 | 8.8072 | 18.7942 | 30.1352 | 11.7412 | 8.565 | 18.5318 | 30.2011 | 11.3818 | 8.3029 | 18.2791 | 30.2737 | 11.2831 | 8.2308 | 18.0404 | 30.3519 | 11.205 | 8.1739 | 17.7582 | 30.4345 | 11.1206 | 8.1123 | 17.4564 | 30.524 | 11.0388 | 8.0527 | 17.1406 | 30.8861 | 10.799 | 7.8777 | 16.0534 | 31.1559 | 10.6503 | 7.7693 | 15.4836 | 31.3334 | 11.7348 | 8.5604 | 15.3043 | 31.4536 | 11.6407 | 8.4917 | 15.3416 | 29.9655 | 13.3985 | 9.774 | 19.1985 | 30.0129 | 13.1096 | 9.5632 | 19.0395 | 30.0423 | 12.7688 | 9.3146 | 18.9025 | 30.096 | 12.4195 | 9.0598 | 18.7744 | 30.1703 | 12.0277 | 8.774 | 18.5156 | 30.2661 | 11.7394 | 8.5637 | 18.2625 | 30.3816 | 11.6786 | 8.5194 | 18.0073 | 30.5129 | 11.6088 | 8.4685 | 17.7072 | 30.6533 | 11.5081 | 8.395 | 17.4264 | 30.8086 | 11.3977 | 8.3144 | 17.1588 | 31.3896 | 10.8507 | 7.9154 | 15.3966 | 31.8641 | 10.0123 | 7.3038 | 11.4611 | 32.1566 | 10.0518 | 7.3326 | 8.347 | 32.3234 | 9.4955 | 6.9268 | 6.2351 | 29.9563 | 13.4065 | 9.7798 | 19.2301 | 30.0019 | 13.4388 | 9.8034 | 19.0777 | 30.0301 | 13.4064 | 9.7798 | 18.9462 | 30.0769 | 13.3638 | 9.7487 | 18.8445 | 30.1466 | 13.2328 | 9.6531 | 18.6097 | 30.2337 | 13.1133 | 9.566 | 18.3972 | 30.3404 | 13.0437 | 9.5152 | 18.1883 | 30.4588 | 12.9778 | 9.4671 | 17.9427 | 30.6041 | 12.8615 | 9.3823 | 17.5919 | 30.8141 | 12.6412 | 9.2216 | 16.642 | 31.3791 | 11.5253 | 8.4075 | 12.2488 | 31.7383 | 10.4648 | 7.634 | 8.7156 | 31.8804 | 9.8378 | 7.1766 | 6.6698 | 31.8348 | 9.7718 | 7.1284 | 7.2367
WATERSWALLOWS | BUXTON | STALYBRIDGE | 407734 | 375459 | 29.5002 | 12.0709 | 8.6756 | 17.0082 | 29.5689 | 11.5838 | 8.3255 | 16.6086 | 29.6205 | 11.1534 | 8.0162 | 16.5642 | 29.6919 | 10.7217 | 7.7059 | 16.466 | 29.7827 | 10.3435 | 7.4341 | 16.3985 | 29.8917 | 9.97 | 7.1657 | 16.1505 | 30.0196 | 9.8564 | 7.084 | 15.862 | 30.1587 | 9.6924 | 6.9661 | 15.6129 | 30.3089 | 9.743 | 7.0025 | 15.3383 | 30.4811 | 9.7283 | 6.9919 | 15.0363 | 31.5559 | 9.5795 | 6.885 | 13.7101 | 32.6307 | 9.5137 | 6.8377 | 12.6236 | 33.6052 | 12.7244 | 9.1453 | 11.7587 | 34.3297 | 12.4319 | 8.9351 | 10.8461 | 29.4565 | 12.1475 | 8.7307 | 17.3581 | 29.4857 | 11.5056 | 8.2693 | 17.2617 | 29.5403 | 10.8231 | 7.7788 | 17.1309 | 29.595 | 10.3124 | 7.4117 | 16.9855 | 29.657 | 9.9106 | 7.1229 | 16.8664 | 29.7268 | 9.489 | 6.8199 | 16.6255 | 29.8065 | 9.4466 | 6.7894 | 16.437 | 29.8902 | 9.4095 | 6.7628 | 16.2773 | 29.9773 | 9.3572 | 6.7252 | 16.0391 | 30.0651 | 9.3051 | 6.6878 | 15.7978 | 30.5905 | 9.0981 | 6.539 | 14.8663 | 31.1891 | 8.9597 | 6.4395 | 14.0736 | 31.8256 | 10.4975 | 7.5448 | 13.4063 | 32.3891 | 13.2157 | 9.4984 | 12.9658 | 29.5005 | 12.1329 | 8.7202 | 17.0086 | 29.5698 | 11.4949 | 8.2616 | 16.611 | 29.6223 | 10.8753 | 7.8163 | 16.5685 | 29.6949 | 10.3368 | 7.4293 | 16.4729 | 29.7867 | 9.8865 | 7.1056 | 16.4086 | 29.8963 | 9.4206 | 6.7708 | 16.1925 | 30.0249 | 9.3687 | 6.7335 | 15.9049 | 30.1648 | 9.3145 | 6.6945 | 15.6591 | 30.3139 | 9.2671 | 6.6604 | 15.3926 | 30.4782 | 9.2097 | 6.6192 | 15.1152 | 31.4256 | 9.0678 | 6.5172 | 13.9738 | 32.0772 | 9.1438 | 6.5719 | 13.2811 | 32.8364 | 13.1343 | 9.4399 | 12.5685 | 33.4503 | 12.9914 | 9.3372 | 11.9951 | 29.4988 | 12.0677 | 8.6733 | 17.0275 | 29.5742 | 11.5723 | 8.3173 | 16.6426 | 29.6457 | 11.1287 | 7.9984 | 16.6079 | 29.7491 | 10.7012 | 7.6912 | 16.5165 | 29.889 | 10.3184 | 7.4161 | 16.4426 | 30.0803 | 9.9349 | 7.1404 | 16.1941 | 30.3287 | 9.7707 | 7.0224 | 15.9022 | 30.6206 | 9.7587 | 7.0137 | 15.5675 | 30.9484 | 9.7399 | 7.0002 | 15.2083 | 31.3101 | 9.6844 | 6.9604 | 14.8185 | 32.9079 | 9.2862 | 6.6742 | 12.6138 | 33.8935 | 8.9617 | 6.4409 | 10.2108 | 34.279 | 11.9046 | 8.5561 | 8.8462 | 34.2865 | 11.6276 | 8.357 | 8.2243 | 29.5153 | 12.0663 | 8.6723 | 17.0161 | 29.6203 | 12.1604 | 8.7399 | 16.6118 | 29.7149 | 12.2243 | 8.7859 | 16.5626 | 29.8371 | 12.2563 | 8.8088 | 16.4575 | 29.998 | 12.2211 | 8.7836 | 16.3226 | 30.219 | 12.116 | 8.708 | 16.0468 | 30.6008 | 12.0522 | 8.6622 | 15.6241 | 30.9395 | 11.9924 | 8.6192 | 15.2469 | 31.3339 | 11.927 | 8.5722 | 14.8238 | 31.8037 | 11.8429 | 8.5117 | 14.2931 | 33.3607 | 12.8051 | 9.2033 | 11.7683 | 34.092 | 12.2162 | 8.78 | 9.8218 | 34.2516 | 11.9121 | 8.5615 | 9.1172 | 34.0585 | 11.8039 | 8.4837 | 9.2378
WEASTE | FREDERICK RD | KEARSLEY | 378751 | 398897 | 29.1441 | 7.8073 | 5.6953 | 11.9827 | 29.2959 | 7.7327 | 5.6409 | 11.4304 | 29.3274 | 7.6535 | 5.5832 | 11.2628 | 29.3882 | 7.5515 | 5.5087 | 11.1384 | 29.4739 | 7.5246 | 5.4891 | 10.9794 | 29.5794 | 7.4158 | 5.4097 | 10.5408 | 29.6878 | 7.3404 | 5.3547 | 10.3074 | 29.798 | 7.2618 | 5.2974 | 10.1194 | 29.9119 | 7.1425 | 5.2104 | 9.724 | 30.0392 | 7.0725 | 5.1593 | 9.4188 | 30.8902 | 6.5017 | 4.7429 | 8.3676 | 32.0289 | 5.9588 | 4.3469 | 7.1797 | 32.9474 | 7.0894 | 5.1716 | 6.4691 | 33.9321 | 8.4015 | 6.1288 | 5.6781 | 29.0227 | 7.9312 | 5.7857 | 12.3972 | 29.0661 | 7.8701 | 5.7412 | 12.1941 | 29.1446 | 7.7795 | 5.675 | 11.9203 | 29.2282 | 7.696 | 5.6141 | 11.6729 | 29.3265 | 7.631 | 5.5667 | 11.4575 | 29.43 | 7.5066 | 5.4759 | 11.0458 | 29.5403 | 7.4298 | 5.42 | 10.7925 | 29.6531 | 7.3377 | 5.3527 | 10.5759 | 29.7687 | 7.2556 | 5.2928 | 10.1466 | 29.8853 | 7.1366 | 5.2061 | 9.7281 | 30.5028 | 7.0045 | 5.1097 | 8.8862 | 31.2139 | 6.7507 | 4.9245 | 7.9922 | 31.9332 | 7.8792 | 5.7478 | 7.2647 | 32.5532 | 8.983 | 6.553 | 6.7228 | 29.1445 | 7.9296 | 5.7845 | 11.9864 | 29.2969 | 7.8627 | 5.7357 | 11.4435 | 29.3294 | 7.7594 | 5.6604 | 11.2747 | 29.3915 | 7.6409 | 5.5739 | 11.1595 | 29.4787 | 7.4008 | 5.3988 | 10.9985 | 29.5855 | 7.4149 | 5.4091 | 10.566 | 29.6952 | 7.3237 | 5.3426 | 10.3375 | 29.8066 | 7.242 | 5.283 | 10.154 | 29.921 | 7.1303 | 5.2014 | 9.7674 | 30.0465 | 7.0279 | 5.1267 | 9.4798 | 30.7837 | 6.686 | 4.8774 | 8.5532 | 31.5362 | 6.3428 | 4.627 | 7.6941 | 32.2609 | 7.6319 | 5.5674 | 7.1247 | 32.8736 | 8.781 | 6.4056 | 6.7051 | 29.1349 | 7.8136 | 5.6999 | 12.0146 | 29.282 | 7.7338 | 5.6417 | 11.4833 | 29.3165 | 7.6426 | 5.5752 | 11.3656 | 29.3886 | 7.5972 | 5.5421 | 11.2388 | 29.4891 | 7.5592 | 5.5143 | 11.1049 | 29.6376 | 7.4256 | 5.4169 | 10.735 | 29.8202 | 7.348 | 5.3603 | 10.5131 | 30.0275 | 7.2767 | 5.3083 | 10.3237 | 30.249 | 7.1105 | 5.187 | 9.9259 | 30.49 | 7.0014 | 5.1074 | 9.6131 | 32.214 | 6.2036 | 4.5255 | 7.8528 | 32.8117 | 5.3224 | 3.8826 | 4.7286 | 34.898 | 6.18 | 4.5082 | 2.4245 | 35.2944 | 7.3283 | 5.3459 | 1.0515 | 29.1357 | 7.8122 | 5.6989 | 12.0055 | 29.2894 | 7.7187 | 5.6307 | 11.4671 | 29.3343 | 7.6145 | 5.5546 | 11.3192 | 29.4198 | 7.4394 | 5.4269 | 11.2166 | 29.5372 | 7.4448 | 5.4308 | 11.0831 | 29.7183 | 7.339 | 5.3537 | 10.6919 | 29.9486 | 7.2424 | 5.2832 | 10.4486 | 30.2184 | 7.1578 | 5.2215 | 10.2352 | 30.5295 | 6.9812 | 5.0927 | 9.7984 | 30.9819 | 6.7568 | 4.929 | 9.2756 | 32.8277 | 5.5378 | 4.0398 | 5.8676 | 29.1899 | 4.7349 | 3.454 | 3.025 | 34.9154 | 7.5731 | 5.5245 | 1.456 | 34.9625 | 7.3289 | 5.3463 | 1.6453
WERNETH | GREENHILL | WHITEGATE | 391273 | 403453 | 30.1501 | 13.2939 | 9.6977 | 18.2527 | 30.199 | 12.8654 | 9.3851 | 18.0673 | 30.2275 | 12.3673 | 9.0218 | 17.9097 | 30.2753 | 12.1015 | 8.8279 | 17.6536 | 30.3402 | 11.7989 | 8.6071 | 17.473 | 30.4212 | 11.4392 | 8.3448 | 17.1783 | 30.513 | 11.2675 | 8.2195 | 16.9155 | 30.6132 | 11.2669 | 8.219 | 16.593 | 30.7206 | 11.2448 | 8.2029 | 16.2406 | 30.8383 | 11.1951 | 8.1667 | 15.8792 | 31.3622 | 10.9055 | 7.9554 | 14.4861 | 31.8656 | 10.8222 | 7.8947 | 13.6164 | 32.2207 | 11.5507 | 8.4261 | 13.2746 | 32.5049 | 11.4504 | 8.3529 | 13.2015 | 30.1272 | 13.3239 | 9.7196 | 18.2928 | 30.1593 | 12.8849 | 9.3994 | 18.1352 | 30.2118 | 12.6207 | 9.2066 | 17.9299 | 30.2737 | 12.384 | 9.0339 | 17.6798 | 30.3452 | 12.1279 | 8.8471 | 17.5226 | 30.4265 | 11.8741 | 8.662 | 17.2518 | 30.5178 | 11.8233 | 8.6249 | 17.0086 | 30.6172 | 11.7593 | 8.5782 | 16.704 | 30.7242 | 11.6842 | 8.5234 | 16.3611 | 30.838 | 11.6097 | 8.4691 | 16.0279 | 31.1712 | 11.3537 | 8.2824 | 15.004 | 31.465 | 11.2788 | 8.2277 | 14.2996 | 31.6844 | 11.6921 | 8.5293 | 13.8917 | 31.8465 | 11.9797 | 8.739 | 13.6516 | 30.1516 | 13.3277 | 9.7224 | 18.2609 | 30.2012 | 12.7812 | 9.3237 | 18.0842 | 30.2301 | 12.6858 | 9.2541 | 17.9352 | 30.2783 | 12.4019 | 9.047 | 17.6881 | 30.3431 | 12.0833 | 8.8146 | 17.5165 | 30.423 | 11.7723 | 8.5878 | 17.2329 | 30.513 | 11.7118 | 8.5436 | 16.9802 | 30.611 | 11.6283 | 8.4827 | 16.6685 | 30.7146 | 11.5352 | 8.4147 | 16.3328 | 30.8241 | 11.4302 | 8.3382 | 16.0077 | 31.2999 | 11.1371 | 8.1244 | 14.7452 | 31.6872 | 11.1177 | 8.1102 | 14.0217 | 31.9558 | 12.007 | 8.7589 | 13.7688 | 32.1503 | 11.9398 | 8.7099 | 13.7615 | 30.1502 | 13.2948 | 9.6984 | 18.2567 | 30.2001 | 12.8551 | 9.3776 | 18.0764 | 30.2353 | 12.2975 | 8.9709 | 17.928 | 30.2931 | 12.1059 | 8.8311 | 17.6823 | 30.3723 | 11.786 | 8.5977 | 17.5232 | 30.4771 | 11.4017 | 8.3174 | 17.25 | 30.6038 | 11.277 | 8.2264 | 16.9998 | 30.7494 | 11.2789 | 8.2278 | 16.6884 | 30.9113 | 11.241 | 8.2002 | 16.3884 | 31.0927 | 11.1954 | 8.1669 | 16.1156 | 31.8851 | 10.7473 | 7.84 | 14.3216 | 32.727 | 10.013 | 7.3044 | 10.5487 | 33.2913 | 10.0706 | 7.3463 | 7.6177 | 33.5919 | 9.5591 | 6.9732 | 5.6921 | 30.1502 | 13.2938 | 9.6977 | 18.2348 | 30.2016 | 13.2194 | 9.6434 | 18.0516 | 30.2314 | 13.0354 | 9.5091 | 17.9301 | 30.2795 | 12.9591 | 9.4535 | 17.7347 | 30.3507 | 12.8643 | 9.3843 | 17.6238 | 30.4489 | 12.6413 | 9.2217 | 17.4105 | 30.5765 | 12.6689 | 9.2418 | 17.2111 | 30.7229 | 12.6542 | 9.231 | 16.9578 | 30.8929 | 12.5853 | 9.1808 | 16.6069 | 31.1098 | 12.3998 | 9.0455 | 15.7115 | 31.9634 | 11.4919 | 8.3832 | 11.5182 | 32.6454 | 10.4623 | 7.6321 | 8.1558 | 33.0078 | 9.8556 | 7.1895 | 6.2359 | 33.0713 | 9.7645 | 7.1231 | 6.7896
WESLEY PLACE BACUP | ROSSENDALE | PADIHAM | 386475 | 422130 | 30.1975 | 17.6795 | 12.8969 | 17.2909 | 30.2496 | 16.0994 | 11.7443 | 17.0947 | 30.2795 | 14.5273 | 10.5974 | 16.9591 | 30.3275 | 12.8789 | 9.3949 | 16.7606 | 30.3919 | 11.2036 | 8.1729 | 16.5348 | 30.4712 | 9.4953 | 6.9267 | 16.265 | 30.5621 | 9.2571 | 6.7529 | 15.9468 | 30.6618 | 8.9651 | 6.5399 | 15.5955 | 30.7636 | 8.5154 | 6.2118 | 15.2547 | 30.8739 | 8.5775 | 6.2572 | 14.8507 | 31.3681 | 8.9406 | 6.522 | 13.3433 | 31.8495 | 10.9748 | 8.0059 | 12.484 | 32.1987 | 14.2274 | 10.3787 | 12.2209 | 32.5262 | 14.7819 | 10.7832 | 12.1809 | 30.1745 | 17.7307 | 12.9343 | 17.3634 | 30.2104 | 16.2099 | 11.8249 | 17.2224 | 30.2674 | 14.6654 | 10.6982 | 17.0174 | 30.3322 | 13.1229 | 9.573 | 16.802 | 30.4062 | 11.5741 | 8.4431 | 16.5706 | 30.4888 | 10.0093 | 7.3016 | 16.2802 | 30.5816 | 9.9279 | 7.2423 | 15.9517 | 30.6822 | 9.8482 | 7.1842 | 15.5982 | 30.7904 | 9.7922 | 7.1433 | 15.2443 | 30.9058 | 9.6979 | 7.0745 | 14.8703 | 31.1719 | 9.7405 | 7.1056 | 13.8254 | 31.4217 | 11.0798 | 8.0825 | 13.0647 | 31.6507 | 13.1766 | 9.6121 | 12.6076 | 31.8411 | 13.3662 | 9.7504 | 12.2639 | 30.1976 | 17.7315 | 12.9349 | 17.3009 | 30.2498 | 16.2176 | 11.8305 | 17.1179 | 30.28 | 14.6704 | 10.7018 | 16.9957 | 30.3284 | 13.1231 | 9.5731 | 16.8098 | 30.3929 | 11.5562 | 8.4301 | 16.5991 | 30.4721 | 9.9773 | 7.2783 | 16.3448 | 30.563 | 9.9085 | 7.2281 | 16.054 | 30.6628 | 9.8074 | 7.1544 | 15.7198 | 30.7639 | 9.7088 | 7.0824 | 15.4007 | 30.8701 | 9.5778 | 6.9869 | 15.0318 | 31.3184 | 9.4752 | 6.912 | 13.6245 | 31.6894 | 11.3809 | 8.3022 | 12.8985 | 31.9827 | 14.7702 | 10.7746 | 12.6829 | 32.2159 | 15.092 | 11.0094 | 12.6954 | 30.1947 | 17.6764 | 12.8947 | 17.2942 | 30.2474 | 16.085 | 11.7338 | 17.096 | 30.2853 | 14.4868 | 10.5679 | 16.9565 | 30.3484 | 12.8244 | 9.3552 | 16.7495 | 30.4364 | 11.1319 | 8.1205 | 16.5219 | 30.553 | 9.3958 | 6.8541 | 16.2436 | 30.6977 | 9.1097 | 6.6454 | 15.9279 | 30.863 | 8.7509 | 6.3836 | 15.5925 | 31.0349 | 8.5017 | 6.2019 | 15.2923 | 31.2273 | 8.6339 | 6.2983 | 14.9803 | 32.1559 | 8.5503 | 6.2374 | 12.8969 | 33.0471 | 9.6691 | 7.0535 | 8.2303 | 33.5989 | 12.2326 | 8.9235 | 4.5821 | 33.8894 | 12.1592 | 8.87 | 2.1513 | 30.1873 | 17.6836 | 12.8999 | 17.319 | 30.2407 | 17.5723 | 12.8187 | 17.1299 | 30.2785 | 17.4541 | 12.7325 | 17.009 | 30.3358 | 17.2317 | 12.5703 | 16.8377 | 30.4174 | 16.9417 | 12.3588 | 16.6493 | 30.5272 | 16.5261 | 12.0556 | 16.4194 | 30.6614 | 16.3586 | 11.9334 | 16.1492 | 30.816 | 16.4768 | 12.0196 | 15.8644 | 31.0085 | 16.5002 | 12.0367 | 15.4698 | 31.2829 | 16.3227 | 11.9072 | 14.3516 | 32.2767 | 15.0404 | 10.9718 | 9.2015 | 32.9891 | 13.4588 | 9.818 | 4.9832 | 33.2854 | 12.8913 | 9.404 | 2.5865 | 33.2664 | 12.3968 | 9.0433 | 3.2492
WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 31.0445 | 12.4936 | 9.1139 | 14.015 | 31.1439 | 12.3743 | 9.0269 | 13.4718 | 31.1757 | 12.2643 | 8.9466 | 13.0702 | 31.2421 | 12.223 | 8.9165 | 12.718 | 31.3335 | 12.2593 | 8.943 | 12.2614 | 31.448 | 12.1919 | 8.8938 | 11.7678 | 31.5728 | 12.0862 | 8.8167 | 11.1868 | 31.7058 | 11.9736 | 8.7346 | 10.6447 | 31.8459 | 11.8928 | 8.6756 | 10.1192 | 32.001 | 11.7399 | 8.5641 | 9.4852 | 32.6287 | 10.9791 | 8.0091 | 7.2964 | 33.0638 | 11.0651 | 8.0718 | 6.3159 | 33.3076 | 11.3994 | 8.3157 | 6.1917 | 33.4441 | 11.7475 | 8.5697 | 6.4595 | 30.9629 | 12.6022 | 9.1931 | 14.2285 | 30.9939 | 12.5114 | 9.1269 | 13.887 | 31.0622 | 12.4007 | 9.0461 | 13.4895 | 31.1457 | 12.3135 | 8.9825 | 13.2006 | 31.2392 | 12.2331 | 8.9239 | 12.8276 | 31.3433 | 12.1429 | 8.8581 | 12.4111 | 31.457 | 12.032 | 8.7772 | 11.9057 | 31.5768 | 11.9578 | 8.723 | 11.4355 | 31.7025 | 11.871 | 8.6597 | 10.9705 | 31.8332 | 11.7706 | 8.5865 | 10.4607 | 32.1677 | 11.4167 | 8.3284 | 8.7961 | 32.4143 | 11.4058 | 8.3204 | 7.721 | 32.5557 | 11.7551 | 8.5752 | 7.1631 | 32.6307 | 11.8883 | 8.6724 | 6.8335 | 31.0445 | 12.6018 | 9.1929 | 14.0312 | 31.1439 | 12.5049 | 9.1221 | 13.5081 | 31.1757 | 12.3891 | 9.0377 | 13.1272 | 31.2421 | 12.2995 | 8.9723 | 12.792 | 31.3332 | 12.2204 | 8.9146 | 12.3565 | 31.447 | 12.1198 | 8.8412 | 11.8832 | 31.5713 | 11.9944 | 8.7497 | 11.3223 | 31.7039 | 11.8815 | 8.6674 | 10.7982 | 31.8422 | 11.6984 | 8.5338 | 10.2989 | 31.99 | 11.6496 | 8.4982 | 9.7245 | 32.5838 | 11.1588 | 8.1402 | 7.7467 | 32.9901 | 11.2095 | 8.1772 | 6.8972 | 33.2182 | 11.6677 | 8.5114 | 6.8114 | 33.3493 | 11.5961 | 8.4592 | 7.0481 | 31.0381 | 12.4984 | 9.1174 | 14.0222 | 31.1367 | 12.3966 | 9.0431 | 13.4795 | 31.1796 | 12.3004 | 8.973 | 13.0826 | 31.2668 | 12.2677 | 8.9491 | 12.7301 | 31.3915 | 12.263 | 8.9457 | 12.2796 | 31.555 | 12.1658 | 8.8748 | 11.7801 | 31.7481 | 12.0233 | 8.7708 | 11.171 | 31.965 | 11.9272 | 8.7008 | 10.602 | 32.1736 | 11.7747 | 8.5895 | 10.125 | 32.4078 | 11.6072 | 8.4673 | 9.6026 | 33.1624 | 10.795 | 7.8748 | 7.0977 | 33.8213 | 10.022 | 7.3109 | 3.078 | 34.1719 | 9.9551 | 7.2621 | 0.36852 | 34.3687 | 9.7379 | 7.1036 | -1.5876 | 31.0376 | 12.4957 | 9.1155 | 13.9866 | 31.1445 | 12.4731 | 9.0989 | 13.3768 | 31.1857 | 12.4214 | 9.0612 | 12.9847 | 31.2647 | 12.4035 | 9.0482 | 12.6782 | 31.381 | 12.3451 | 9.0056 | 12.2756 | 31.5288 | 12.2441 | 8.9319 | 11.8504 | 31.7071 | 12.1108 | 8.8347 | 11.3168 | 31.877 | 11.9576 | 8.7229 | 10.8414 | 32.0563 | 11.9066 | 8.6857 | 10.4328 | 32.3172 | 11.6707 | 8.5136 | 9.3377 | 33.1818 | 11.3823 | 8.3032 | 4.2946 | 33.6864 | 10.3478 | 7.5486 | 0.77634 | 33.8495 | 10.1997 | 7.4406 | -0.97392 | 33.7101 | 10.1456 | 7.4011 | -0.18007
WESTGATE | LANCASTER | HEYSHAM | 343077 | 463204 | 15.957 | 9.9064 | 7.2266 | 5.0014 | 16.0539 | 9.8926 | 7.2165 | 4.9233 | 16.175 | 9.9903 | 7.2878 | 4.6127 | 16.3062 | 9.5667 | 6.9788 | 4.158 | 16.4718 | 9.486 | 6.9199 | 3.5149 | 16.6714 | 8.8799 | 6.4777 | 3.0412 | 16.8882 | 8.594 | 6.2692 | 2.3842 | 17.1305 | 8.3171 | 6.0672 | 1.4867 | 17.3971 | 8.1086 | 5.9151 | 0.98645 | 17.6945 | 7.8289 | 5.7111 | 0.18135 | 19.2747 | 6.7296 | 4.9092 | -2.8361 | 20.9692 | 5.9559 | 4.3447 | -4.9413 | 22.0946 | 5.5236 | 4.0294 | -6.1818 | 22.9709 | 5.4339 | 3.964 | -5.6129 | 15.9703 | 9.938 | 7.2497 | 5.0843 | 16.0605 | 9.8664 | 7.1974 | 5.074 | 16.193 | 9.6973 | 7.074 | 4.6718 | 16.3252 | 9.595 | 6.9994 | 4.2456 | 16.4794 | 9.4433 | 6.8888 | 3.6588 | 16.6601 | 9.3687 | 6.8343 | 3.2328 | 16.8713 | 9.2159 | 6.7229 | 2.6226 | 17.092 | 8.9964 | 6.5627 | 1.7684 | 17.3259 | 8.8839 | 6.4807 | 1.3001 | 17.5768 | 8.722 | 6.3626 | 0.62573 | 18.5264 | 8.2726 | 6.0347 | -1.5398 | 19.456 | 7.85 | 5.7265 | -3.2948 | 20.151 | 7.4067 | 5.4031 | -5.1392 | 20.6715 | 7.3593 | 5.3685 | -4.8071 | 15.9666 | 9.9338 | 7.2466 | 5.0327 | 16.0669 | 9.8374 | 7.1762 | 4.963 | 16.1896 | 9.7447 | 7.1086 | 4.6955 | 16.3186 | 9.5821 | 6.99 | 4.265 | 16.4842 | 9.4224 | 6.8735 | 3.6539 | 16.6787 | 9.314 | 6.7944 | 3.2077 | 16.8899 | 9.1472 | 6.6728 | 2.5809 | 17.1246 | 8.9312 | 6.5152 | 1.7187 | 17.3791 | 8.6888 | 6.3384 | 1.2561 | 17.6535 | 8.4997 | 6.2004 | 0.53456 | 19.0648 | 7.709 | 5.6236 | -2.2315 | 20.3069 | 6.9673 | 5.0826 | -3.9856 | 21.1758 | 6.2261 | 4.5418 | -4.9062 | 21.7736 | 5.9736 | 4.3577 | -4.0661 | 15.9716 | 9.9053 | 7.2258 | 5.0036 | 16.0842 | 9.8898 | 7.2145 | 4.926 | 16.225 | 9.9321 | 7.2453 | 4.621 | 16.3969 | 9.6481 | 7.0381 | 4.1731 | 16.6131 | 9.3756 | 6.8394 | 3.5558 | 16.8815 | 8.889 | 6.4844 | 3.0931 | 17.2297 | 8.4626 | 6.1733 | 2.4066 | 17.6387 | 8.1536 | 5.948 | 1.4835 | 18.1036 | 7.9311 | 5.7856 | 1.0373 | 18.6279 | 7.6632 | 5.5902 | 0.39311 | 21.2375 | 6.2024 | 4.5246 | -3.6297 | 24.0114 | 4.1806 | 3.0497 | -11.255 | 15.6145 | 2.5328 | 1.8477 | -17.8402 | 10.7751 | 1.7478 | 1.275 | -20.3149 | 15.9883 | 9.9048 | 7.2254 | 4.9812 | 16.1351 | 9.9127 | 7.2311 | 4.8738 | 16.2738 | 9.9428 | 7.2531 | 4.5613 | 16.4542 | 9.7043 | 7.0791 | 4.1453 | 16.6597 | 9.3583 | 6.8268 | 3.5349 | 16.9497 | 8.8556 | 6.46 | 3.1117 | 17.3441 | 8.3731 | 6.1081 | 2.4848 | 17.8061 | 8.067 | 5.8848 | 1.6377 | 18.3401 | 7.8237 | 5.7073 | 1.1079 | 18.9833 | 7.3436 | 5.3571 | -0.65752 | 21.6734 | 5.1129 | 3.7298 | -9.0446 | 19.3059 | 3.1316 | 2.2845 | -15.9717 | 11.676 | 1.894 | 1.3816 | -20.8369 | 12.9565 | 2.1017 | 1.5331 | -18.6204
WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 22.1148 | 11.8682 | 8.5299 | 9.2829 | 22.1937 | 9.1328 | 6.5639 | 8.6169 | 22.2469 | 6.3681 | 4.5769 | 8.2249 | 21.2158 | 3.493 | 2.5105 | 7.5622 | 5.9416 | 0.97824 | 0.70308 | 5.9416 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.1543 | 4.4179 | 0.72737 | 0.52278 | -0.28426 | 26.4143 | 7.5954 | 5.459 | -0.91771 | 27.1287 | 8.7451 | 6.2853 | -0.85646 | 22.0576 | 11.8565 | 8.5215 | 9.4838 | 22.0892 | 8.922 | 6.4124 | 9.0125 | 22.1643 | 6.148 | 4.4187 | 8.6386 | 21.237 | 3.4965 | 2.513 | 8.0356 | 5.4621 | 0.89929 | 0.64634 | 5.4621 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.0394 | 24.1086 | 3.9693 | 2.8528 | 1.0283 | 25.2392 | 5.7318 | 4.1195 | 0.47468 | 22.115 | 11.8523 | 8.5185 | 9.2936 | 22.1944 | 8.89 | 6.3894 | 8.6441 | 22.2483 | 6.1466 | 4.4177 | 8.2684 | 21.1156 | 3.4765 | 2.4986 | 7.624 | 5.0822 | 0.83674 | 0.60138 | 5.0822 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.7189 | 6.0571 | 0.99726 | 0.71675 | 0.6607 | 25.8805 | 8.2081 | 5.8993 | 0.21665 | 26.3598 | 9.2452 | 6.6447 | 0.45636 | 22.1107 | 11.8703 | 8.5314 | 9.2869 | 22.1947 | 9.1088 | 6.5467 | 8.6228 | 22.2753 | 6.3457 | 4.5608 | 8.2434 | 20.9123 | 3.4431 | 2.4746 | 7.6015 | 5.8922 | 0.9701 | 0.69723 | 5.8922 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 0.76236 | 2.6844 | 0.44197 | 0.31765 | -6.7624 | 29.9758 | 4.9353 | 3.5471 | -12.8442 | 30.6562 | 5.2942 | 3.8051 | -16.8056 | 22.1153 | 11.8759 | 8.5354 | 9.3037 | 22.227 | 11.7864 | 8.4712 | 8.6197 | 22.3126 | 11.583 | 8.3249 | 8.2594 | 22.4286 | 11.3046 | 8.1249 | 7.6824 | 22.5979 | 10.9867 | 7.8964 | 7.6681 | 22.8311 | 10.9901 | 7.8988 | 6.9647 | 23.1412 | 10.855 | 7.8017 | 6.5158 | 23.4998 | 10.7002 | 7.6905 | 5.9395 | 23.9088 | 10.534 | 7.571 | 5.3537 | 24.5295 | 10.1009 | 7.2597 | 3.4341 | 26.9788 | 8.4095 | 6.0441 | -5.0369 | 28.646 | 6.7483 | 4.8501 | -11.6817 | 29.3045 | 5.759 | 4.1391 | -15.7226 | 29.2718 | 5.7788 | 4.1534 | -14.5408
WESTLINTON | CARLISLE | HARKER / HUTTON | 339551 | 564489 | 16.1819 | 16.1819 | 16.1819 | 12.938 | 16.219 | 16.219 | 16.219 | 12.6131 | 16.2774 | 16.2774 | 16.1861 | 12.4163 | 16.3431 | 16.3431 | 16.1171 | 12.1867 | 16.4141 | 16.4141 | 16.0917 | 12.2713 | 16.4948 | 16.4948 | 16.0045 | 12.0561 | 16.5941 | 16.5941 | 15.9184 | 11.8102 | 16.7042 | 16.7042 | 15.8574 | 11.7287 | 16.8288 | 16.8288 | 15.7664 | 11.4443 | 16.9165 | 16.9165 | 15.6599 | 11.0788 | 17.6147 | 17.6147 | 15.2775 | 9.5549 | 18.7492 | 18.7492 | 14.9787 | 8.2756 | 19.5884 | 19.5884 | 14.7829 | 7.3477 | 20.2559 | 20.2242 | 14.5355 | 6.7086 | 16.185 | 16.185 | 16.185 | 13.2004 | 16.2214 | 16.2214 | 16.2214 | 13.0555 | 16.2737 | 16.2737 | 16.256 | 12.8335 | 16.3176 | 16.3176 | 16.1987 | 12.603 | 16.3663 | 16.3663 | 16.182 | 12.6642 | 16.4241 | 16.4241 | 16.1212 | 12.4829 | 16.4935 | 16.4935 | 16.0612 | 12.2394 | 16.5695 | 16.5695 | 16.0159 | 12.0854 | 16.6509 | 16.6509 | 15.9643 | 11.8782 | 16.7361 | 16.7361 | 15.9109 | 11.6477 | 17.2522 | 17.2522 | 15.7431 | 10.8464 | 17.9717 | 17.9717 | 15.5134 | 9.6289 | 18.6971 | 18.6971 | 15.371 | 8.4234 | 19.279 | 19.279 | 15.2105 | 7.5261 | 16.1822 | 16.1822 | 16.1822 | 12.9419 | 16.22 | 16.22 | 16.22 | 12.6318 | 16.2795 | 16.2795 | 16.2402 | 12.4461 | 16.3465 | 16.3465 | 16.1668 | 12.2338 | 16.4188 | 16.4188 | 16.1339 | 12.3223 | 16.5004 | 16.5004 | 16.0309 | 12.1123 | 16.6007 | 16.6007 | 15.9142 | 11.8744 | 16.7118 | 16.7118 | 15.8332 | 11.7973 | 16.8397 | 16.8397 | 15.7697 | 11.5293 | 16.926 | 16.926 | 15.6552 | 11.2075 | 17.485 | 17.485 | 15.3894 | 9.9294 | 18.1449 | 18.1449 | 15.0622 | 9.0566 | 18.88 | 18.88 | 14.5758 | 8.3717 | 19.4169 | 19.4169 | 14.0951 | 8.1343 | 16.1837 | 16.1837 | 16.1837 | 12.9493 | 16.233 | 16.233 | 16.233 | 12.6176 | 16.3135 | 16.3135 | 16.1633 | 12.407 | 16.4103 | 16.4103 | 16.0846 | 12.1616 | 16.531 | 16.531 | 16.0458 | 12.2045 | 16.6958 | 16.6958 | 15.943 | 11.9381 | 16.856 | 16.856 | 15.8311 | 11.5828 | 17.0199 | 17.0199 | 15.7404 | 11.3685 | 17.2124 | 17.2124 | 15.6318 | 11.044 | 17.4288 | 17.4288 | 15.5164 | 10.7298 | 18.9016 | 18.9016 | 14.9639 | 8.6618 | 20.2171 | 20.1601 | 14.4895 | 6.3997 | 21.0189 | 19.5385 | 14.0427 | 5.0175 | 21.3561 | 19.1215 | 13.743 | 4.5679 | 16.1999 | 16.1999 | 16.1999 | 12.9337 | 16.2758 | 16.2758 | 16.2332 | 12.561 | 16.3763 | 16.3763 | 16.1533 | 12.364 | 16.4933 | 16.4933 | 16.0664 | 12.108 | 16.6465 | 16.6465 | 16.0126 | 12.0969 | 16.8142 | 16.8142 | 15.8937 | 11.7592 | 17.0065 | 17.0065 | 15.7689 | 11.3806 | 17.248 | 17.248 | 15.6732 | 11.1649 | 17.5348 | 17.5348 | 15.5541 | 10.7702 | 17.8653 | 17.8653 | 15.4138 | 10.2606 | 19.3943 | 19.3943 | 14.8911 | 7.5868 | 20.5749 | 19.8614 | 14.2748 | 5.6064 | 21.0683 | 19.4139 | 13.9531 | 4.7686 | 21.0884 | 19.1806 | 13.7855 | 4.968
WHALLEY | PADIHAM | PADIHAM | 373376 | 436176 | 25.7762 | 12.2935 | 8.8356 | 13.5655 | 25.8933 | 12.1754 | 8.7507 | 12.961 | 25.9659 | 12.1147 | 8.7071 | 12.52 | 26.0668 | 11.9931 | 8.6197 | 12.0987 | 26.1896 | 11.9127 | 8.5619 | 11.6237 | 26.3148 | 11.763 | 8.4543 | 11.1231 | 26.4517 | 11.5287 | 8.2859 | 10.5713 | 26.5956 | 11.4207 | 8.2083 | 10.0069 | 26.7465 | 11.142 | 8.008 | 9.4519 | 26.9237 | 11.0181 | 7.9189 | 8.7447 | 27.6874 | 10.2609 | 7.3747 | 6.0691 | 28.3251 | 9.6466 | 6.9332 | 4.585 | 28.7477 | 10.4628 | 7.5198 | 4.1267 | 29.0595 | 10.5365 | 7.5728 | 4.3091 | 25.729 | 12.2676 | 8.817 | 13.7931 | 25.8084 | 12.0947 | 8.6927 | 13.4048 | 25.9217 | 12.0152 | 8.6356 | 12.955 | 26.0262 | 11.9599 | 8.5958 | 12.6041 | 26.1386 | 11.775 | 8.4629 | 12.2045 | 26.2618 | 11.6558 | 8.3772 | 11.7804 | 26.3971 | 11.5684 | 8.3144 | 11.3008 | 26.5395 | 11.4146 | 8.2039 | 10.805 | 26.6904 | 11.2558 | 8.0898 | 10.2875 | 26.848 | 11.1232 | 7.9945 | 9.7707 | 27.2457 | 10.9012 | 7.8349 | 8.1269 | 27.6091 | 10.5534 | 7.5849 | 6.7197 | 27.8776 | 11.1644 | 8.0241 | 5.7735 | 28.0759 | 11.786 | 8.4708 | 5.1134 | 25.7763 | 12.2599 | 8.8114 | 13.5726 | 25.8935 | 12.0857 | 8.6862 | 12.9845 | 25.9663 | 12.0332 | 8.6485 | 12.5624 | 26.0674 | 11.9025 | 8.5546 | 12.1649 | 26.1902 | 11.7276 | 8.4289 | 11.7152 | 26.3151 | 11.4991 | 8.2647 | 11.24 | 26.4517 | 11.4199 | 8.2077 | 10.7139 | 26.5956 | 11.3173 | 8.134 | 10.1747 | 26.7451 | 11.2173 | 8.0621 | 9.6488 | 26.9156 | 11.0699 | 7.9562 | 9.0118 | 27.6282 | 10.498 | 7.5451 | 6.649 | 28.167 | 10.0275 | 7.207 | 5.3664 | 28.5391 | 10.9016 | 7.8352 | 4.9388 | 28.7752 | 10.6015 | 7.6195 | 5.0854 | 25.7723 | 12.2959 | 8.8373 | 13.5797 | 25.894 | 12.187 | 8.759 | 12.9588 | 25.9851 | 12.1169 | 8.7087 | 12.4999 | 26.1157 | 11.9817 | 8.6115 | 12.0677 | 26.2617 | 11.8647 | 8.5274 | 11.5696 | 26.4478 | 11.6533 | 8.3755 | 11.0206 | 26.6716 | 11.4552 | 8.2331 | 10.3806 | 26.9252 | 11.1728 | 8.0301 | 9.7191 | 27.2023 | 11.0338 | 7.9302 | 9.1439 | 27.4962 | 10.8373 | 7.789 | 8.5626 | 28.629 | 9.7058 | 6.9758 | 5.956 | 29.4303 | 8.5386 | 6.1368 | 2.3142 | 29.8477 | 8.8914 | 6.3904 | 0.18833 | 30.0574 | 8.6969 | 6.2506 | -1.5326 | 25.7714 | 12.2926 | 8.8349 | 13.565 | 25.908 | 12.1717 | 8.7481 | 12.9038 | 26.0011 | 12.1309 | 8.7187 | 12.4597 | 26.1236 | 12.0078 | 8.6303 | 12.0624 | 26.262 | 11.8972 | 8.5508 | 11.5989 | 26.436 | 11.737 | 8.4356 | 11.118 | 26.6466 | 11.5157 | 8.2765 | 10.5701 | 26.8766 | 11.2439 | 8.0812 | 10.0287 | 27.1196 | 11.1893 | 8.042 | 9.5612 | 27.4441 | 10.9506 | 7.8704 | 8.6139 | 28.5655 | 10.5479 | 7.581 | 4.1839 | 29.1574 | 9.3641 | 6.7302 | 1.2151 | 29.3422 | 9.2666 | 6.6601 | -0.11986 | 29.2868 | 9.2114 | 6.6204 | 0.33934
WHALLEY RANGE | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 36.9074 | 8.8134 | 6.4293 | 11.2471 | 36.9707 | 8.6817 | 6.3332 | 10.7203 | 37.0007 | 8.5417 | 6.2311 | 10.2793 | 37.0828 | 8.4047 | 6.1311 | 9.8569 | 37.1932 | 8.2615 | 6.0266 | 9.3089 | 37.3293 | 8.0755 | 5.891 | 8.6834 | 37.4788 | 7.8733 | 5.7434 | 7.9303 | 37.6396 | 7.6748 | 5.5987 | 7.3024 | 37.8106 | 7.4466 | 5.4322 | 6.6881 | 38.0044 | 7.1946 | 5.2483 | 5.9159 | 37.441 | 6.0733 | 4.4304 | 3.0812 | 34.8418 | 5.6517 | 4.1228 | 1.6373 | 33.0272 | 5.3573 | 3.9081 | 1.2582 | 31.543 | 5.1166 | 3.7325 | 1.4503 | 36.8756 | 8.8552 | 6.4597 | 11.5457 | 36.9168 | 8.7842 | 6.4079 | 11.2706 | 36.9944 | 8.647 | 6.3079 | 10.7195 | 37.106 | 8.5359 | 6.2268 | 10.2993 | 37.2352 | 8.3746 | 6.1092 | 9.7905 | 37.3832 | 8.2406 | 6.0114 | 9.209 | 37.5465 | 8.0735 | 5.8895 | 8.4826 | 37.7233 | 7.9231 | 5.7798 | 7.8655 | 37.9135 | 7.7639 | 5.6637 | 7.2453 | 38.1171 | 7.5796 | 5.5292 | 6.5472 | 38.4812 | 7.0353 | 5.1322 | 4.5227 | 38.7404 | 6.5184 | 4.7551 | 3.1858 | 38.8959 | 6.3514 | 4.6332 | 2.4968 | 38.6604 | 6.2711 | 4.5747 | 2.1275 | 36.9074 | 8.8516 | 6.4571 | 11.2584 | 36.9707 | 8.7748 | 6.4011 | 10.7456 | 37.0007 | 8.6228 | 6.2902 | 10.3205 | 37.0828 | 8.4516 | 6.1653 | 9.9123 | 37.1928 | 8.2808 | 6.0407 | 9.3814 | 37.3281 | 8.0732 | 5.8893 | 8.7748 | 37.4769 | 7.8677 | 5.7394 | 8.0415 | 37.6373 | 7.6815 | 5.6035 | 7.4309 | 37.8061 | 7.478 | 5.4551 | 6.8438 | 37.9911 | 7.2446 | 5.2848 | 6.1384 | 38.6378 | 6.4216 | 4.6844 | 3.5027 | 37.5171 | 6.0856 | 4.4394 | 2.1786 | 35.804 | 5.8078 | 4.2367 | 1.8297 | 34.075 | 5.5273 | 4.0321 | 1.9862 | 36.9035 | 8.8164 | 6.4314 | 11.2774 | 36.9644 | 8.6803 | 6.3322 | 10.7728 | 36.9976 | 8.5323 | 6.2242 | 10.3552 | 37.0928 | 8.3823 | 6.1147 | 9.9457 | 37.2254 | 8.2271 | 6.0016 | 9.4216 | 37.3931 | 8.0368 | 5.8627 | 8.8041 | 37.5859 | 7.7957 | 5.6869 | 8.0263 | 37.8006 | 7.5576 | 5.5132 | 7.3716 | 38.0334 | 7.3072 | 5.3305 | 6.8078 | 38.2909 | 7.0396 | 5.1353 | 6.1659 | 35.4638 | 5.7526 | 4.1964 | 2.6346 | 25.6188 | 4.1556 | 3.0315 | -3.2371 | 17.8786 | 2.9001 | 2.1156 | -7.8307 | 11.6501 | 1.8898 | 1.3785 | -10.8282 | 36.8905 | 8.8174 | 6.4322 | 11.2629 | 36.9499 | 8.6842 | 6.335 | 10.6874 | 36.9778 | 8.5325 | 6.2244 | 10.257 | 37.0568 | 8.3855 | 6.1171 | 9.8844 | 37.1714 | 8.2175 | 5.9945 | 9.4025 | 37.3128 | 7.983 | 5.8235 | 8.8672 | 37.4807 | 7.7166 | 5.6292 | 8.1827 | 37.662 | 7.4688 | 5.4484 | 7.6459 | 37.8631 | 7.2153 | 5.2635 | 7.0855 | 38.1757 | 6.72 | 4.9022 | 5.5739 | 30.9298 | 5.0171 | 3.6599 | -1.7642 | 20.4921 | 3.324 | 2.4248 | -7.4583 | 15.253 | 2.4742 | 1.8049 | -10.361 | 14.2405 | 2.3099 | 1.6851 | -8.9934
WHASSET | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 350648 | 481468 | 23.4557 | 21.1185 | 15.1783 | 6.7371 | 23.5617 | 21.0457 | 15.1259 | 6.4631 | 23.6608 | 20.9659 | 15.0686 | 6.2345 | 23.7888 | 20.8477 | 14.9837 | 5.9604 | 23.9404 | 20.7593 | 14.9201 | 5.8419 | 24.1143 | 20.6112 | 14.8137 | 5.5008 | 26.922 | 20.0044 | 14.3776 | 2.4788 | 26.9867 | 19.9039 | 14.3053 | 2.374 | 29.1762 | 19.4243 | 13.9606 | 0.10904 | 29.1124 | 19.2982 | 13.87 | -0.099736 | 29.7382 | 18.6793 | 13.4252 | -1.3536 | 30.3292 | 18.2251 | 13.0987 | -2.1328 | 30.2359 | 17.9683 | 12.9142 | -2.0743 | 30.4687 | 17.7564 | 12.7619 | -1.754 | 23.4173 | 21.1654 | 15.212 | 6.9413 | 23.4913 | 21.1327 | 15.1885 | 6.833 | 23.6072 | 21.0531 | 15.1313 | 6.5239 | 23.7205 | 20.9578 | 15.0628 | 6.2404 | 23.8472 | 20.8963 | 15.0186 | 6.1187 | 23.9903 | 20.7831 | 14.9372 | 5.7893 | 24.1562 | 20.6691 | 14.8553 | 5.4159 | 24.3316 | 20.5793 | 14.7907 | 5.1459 | 24.4497 | 20.4861 | 14.7237 | 4.8716 | 24.5598 | 20.3742 | 14.6433 | 4.4918 | 25.0261 | 20.0598 | 14.4174 | 3.6138 | 25.6038 | 19.7408 | 14.1881 | 2.7415 | 26.1358 | 19.4657 | 13.9904 | 2.0417 | 26.4717 | 19.2688 | 13.8489 | 1.7211 | 23.457 | 21.1645 | 15.2114 | 6.7435 | 23.5636 | 21.1266 | 15.1841 | 6.4805 | 23.6632 | 21.0286 | 15.1137 | 6.2661 | 23.7918 | 20.9014 | 15.0223 | 6.0087 | 23.9431 | 20.8069 | 14.9543 | 5.9042 | 24.1157 | 20.6549 | 14.8451 | 5.5799 | 26.9217 | 20.5021 | 14.7352 | 2.5751 | 26.9845 | 20.373 | 14.6424 | 2.4856 | 29.1753 | 20.2393 | 14.5464 | 0.23907 | 29.1079 | 20.0876 | 14.4374 | 0.076649 | 29.6498 | 19.5698 | 14.0652 | -1.0048 | 30.0862 | 19.0854 | 13.717 | -1.6031 | 29.927 | 18.5893 | 13.3605 | -1.4599 | 30.0176 | 18.1952 | 13.0772 | -1.0823 | 23.4526 | 21.1208 | 15.1799 | 6.7559 | 23.5607 | 20.9779 | 15.0772 | 6.4873 | 23.6659 | 20.8829 | 15.0089 | 6.2672 | 23.8033 | 20.7543 | 14.9165 | 6.0026 | 23.9754 | 20.6518 | 14.8428 | 5.8761 | 24.1885 | 20.4831 | 14.7216 | 5.5134 | 26.9106 | 19.8741 | 14.2839 | 2.5925 | 27.0439 | 19.7494 | 14.1942 | 2.4435 | 29.1974 | 19.2774 | 13.855 | 0.33156 | 29.2459 | 19.1533 | 13.7659 | 0.23196 | 31.7833 | 18.1166 | 13.0207 | -2.743 | 32.4976 | 17.283 | 12.4216 | -4.7769 | 32.3504 | 16.7403 | 12.0316 | -5.4774 | 32.3329 | 16.2595 | 11.686 | -6.2887 | 23.475 | 21.1203 | 15.1796 | 6.7532 | 23.6164 | 21.0424 | 15.1236 | 6.4727 | 23.7331 | 20.9378 | 15.0484 | 6.2631 | 23.8738 | 20.7954 | 14.946 | 6.0182 | 24.0508 | 20.677 | 14.861 | 5.8996 | 26.6985 | 20.0699 | 14.4247 | 3.1061 | 29.2707 | 19.4846 | 14.004 | 0.38152 | 29.2638 | 19.3904 | 13.9362 | 0.44542 | 29.2939 | 19.2948 | 13.8675 | 0.53165 | 29.3973 | 19.1134 | 13.7372 | 0.18962 | 30.5669 | 18.0699 | 12.9872 | -2.5595 | 31.0333 | 17.2677 | 12.4107 | -4.1279 | 30.833 | 16.89 | 12.1392 | -4.5148 | 30.5808 | 16.7299 | 12.0241 | -3.9629
WHITTLE LE WOODS | LEYLAND | PENWORTHAM WEST / STANAH | 357874 | 421203 | 23.9337 | 15.0826 | 10.8401 | 9.9404 | 23.9996 | 14.8768 | 10.6923 | 9.6411 | 24.0479 | 14.5971 | 10.4912 | 9.3367 | 24.1216 | 14.3825 | 10.337 | 8.9604 | 24.217 | 14.3018 | 10.279 | 8.6085 | 24.3308 | 14.2399 | 10.2345 | 8.1065 | 24.4591 | 14.1095 | 10.1408 | 7.6305 | 24.5975 | 13.9992 | 10.0615 | 7.0894 | 24.7455 | 13.834 | 9.9428 | 6.5971 | 24.9074 | 13.6163 | 9.7863 | 5.9814 | 25.5292 | 13.0166 | 9.3553 | 3.7835 | 25.9673 | 12.4628 | 8.9573 | 2.5571 | 26.2475 | 12.2497 | 8.8041 | 2.2374 | 26.4567 | 12.0676 | 8.6732 | 2.2477 | 23.909 | 15.0905 | 10.8459 | 10.0148 | 23.9546 | 15.0006 | 10.7812 | 9.782 | 24.0237 | 14.8713 | 10.6883 | 9.4372 | 24.1041 | 14.7132 | 10.5746 | 9.084 | 24.1953 | 14.6051 | 10.497 | 8.7851 | 24.2964 | 14.447 | 10.3833 | 8.3338 | 24.4079 | 14.3814 | 10.3362 | 7.9072 | 24.5263 | 14.2683 | 10.2549 | 7.4166 | 24.6524 | 14.1638 | 10.1798 | 6.9649 | 24.7841 | 14.0213 | 10.0774 | 6.4524 | 25.0991 | 13.6657 | 9.8218 | 4.8238 | 25.3508 | 13.5304 | 9.7246 | 3.608 | 25.5349 | 13.3174 | 9.5715 | 2.9056 | 25.672 | 13.2424 | 9.5176 | 2.3567 | 23.9337 | 15.0823 | 10.8399 | 9.9474 | 23.9997 | 14.9414 | 10.7386 | 9.6607 | 24.0481 | 14.7925 | 10.6316 | 9.3692 | 24.1218 | 14.652 | 10.5307 | 9.0046 | 24.2169 | 14.6604 | 10.5367 | 8.6795 | 24.3302 | 14.5532 | 10.4596 | 8.1956 | 24.4579 | 14.4338 | 10.3738 | 7.7367 | 24.5961 | 14.2775 | 10.2615 | 7.2131 | 24.7421 | 14.1015 | 10.1351 | 6.7445 | 24.896 | 13.961 | 10.0341 | 6.1821 | 25.4815 | 13.5094 | 9.7095 | 4.1987 | 25.8674 | 13.0793 | 9.4004 | 3.1269 | 26.1202 | 12.78 | 9.1853 | 2.8207 | 26.2991 | 12.4018 | 8.9134 | 2.7998 | 23.931 | 15.0805 | 10.8386 | 9.9487 | 23.9991 | 14.8656 | 10.6842 | 9.655 | 24.0605 | 14.5005 | 10.4218 | 9.3544 | 24.1587 | 14.3911 | 10.3432 | 8.9696 | 24.2902 | 14.4036 | 10.3522 | 8.6548 | 24.455 | 14.2391 | 10.2339 | 8.185 | 24.6527 | 14.0249 | 10.0799 | 7.7296 | 24.8771 | 13.8829 | 9.9779 | 7.2142 | 25.1021 | 13.8123 | 9.9272 | 6.8057 | 25.3289 | 13.6761 | 9.8293 | 6.3382 | 26.1133 | 12.6891 | 9.1199 | 3.9625 | 26.765 | 11.4182 | 8.2065 | -0.14841 | 27.1326 | 10.5714 | 7.5978 | -3.2141 | 27.3433 | 9.9647 | 7.1618 | -5.5166 | 23.9305 | 15.0783 | 10.8371 | 9.9412 | 24.0095 | 14.8615 | 10.6813 | 9.6182 | 24.0753 | 14.6399 | 10.522 | 9.3222 | 24.1693 | 14.5042 | 10.4245 | 8.9518 | 24.2945 | 14.4972 | 10.4194 | 8.6674 | 24.4468 | 14.3493 | 10.3131 | 8.2571 | 24.6351 | 14.1432 | 10.165 | 7.8635 | 24.8382 | 14.118 | 10.1469 | 7.4249 | 25.0253 | 14.0148 | 10.0727 | 6.9993 | 25.254 | 13.7504 | 9.8827 | 5.9504 | 26.0326 | 12.1734 | 8.7493 | 1.2193 | 26.5091 | 11.2296 | 8.071 | -2.4419 | 26.6725 | 10.6006 | 7.6188 | -4.5125 | 26.6295 | 10.4035 | 7.4772 | -4.2195
WHITWORTH | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 10.0831 | 5.152 | 3.7583 | 5.6055 | 10.1105 | 5.123 | 3.7371 | 5.5446 | 10.1594 | 5.0732 | 3.7009 | 5.3866 | 10.2197 | 5.0397 | 3.6764 | 5.3886 | 10.272 | 4.9862 | 3.6373 | 5.2662 | 10.3166 | 4.9309 | 3.597 | 5.1343 | 10.3632 | 4.8634 | 3.5478 | 4.9206 | 10.415 | 4.7989 | 3.5007 | 4.7199 | 10.4659 | 4.7302 | 3.4506 | 4.5279 | 10.5208 | 4.6078 | 3.3613 | 4.2832 | 10.752 | 4.3143 | 3.1472 | 3.4779 | 10.9092 | 3.7591 | 2.7422 | 3.1273 | 10.9982 | 3.2379 | 2.362 | 3.086 | 11.0526 | 3.5878 | 2.6172 | 3.2154 | 10.0857 | 5.187 | 3.7839 | 5.689 | 10.1125 | 5.2154 | 3.8046 | 5.6944 | 10.1524 | 5.1872 | 3.784 | 5.5197 | 10.1867 | 5.2095 | 3.8003 | 5.5172 | 10.2276 | 5.1936 | 3.7886 | 5.4027 | 10.2699 | 5.1766 | 3.7763 | 5.3384 | 10.3031 | 5.1356 | 3.7463 | 5.1689 | 10.3385 | 5.0907 | 3.7136 | 5.0114 | 10.376 | 5.0504 | 3.6842 | 4.858 | 10.412 | 5.0224 | 3.6638 | 4.6866 | 10.514 | 4.8868 | 3.5648 | 4.1737 | 10.5878 | 4.734 | 3.4534 | 3.829 | 10.6368 | 4.4765 | 3.2655 | 3.6495 | 10.6686 | 4.3637 | 3.1833 | 3.5527 | 10.0831 | 5.1845 | 3.782 | 5.6075 | 10.1105 | 5.1911 | 3.7868 | 5.5501 | 10.1594 | 5.158 | 3.7627 | 5.3973 | 10.2197 | 5.1515 | 3.758 | 5.4034 | 10.2719 | 5.0956 | 3.7172 | 5.2869 | 10.3162 | 5.086 | 3.7102 | 5.1491 | 10.3626 | 5.0296 | 3.6691 | 4.9397 | 10.4142 | 4.9712 | 3.6264 | 4.7427 | 10.4645 | 4.911 | 3.5825 | 4.557 | 10.5166 | 4.8599 | 3.5452 | 4.3321 | 10.7343 | 4.5606 | 3.3269 | 3.5954 | 10.8799 | 4.2398 | 3.0929 | 3.2825 | 10.9625 | 3.9267 | 2.8644 | 3.2486 | 11.0148 | 3.6036 | 2.6288 | 3.3646 | 10.0843 | 5.1517 | 3.7581 | 5.6119 | 10.1199 | 5.0939 | 3.7159 | 5.5536 | 10.1871 | 5.037 | 3.6744 | 5.3969 | 10.2557 | 5.0049 | 3.651 | 5.3998 | 10.3093 | 4.9442 | 3.6067 | 5.2762 | 10.3708 | 4.8981 | 3.5731 | 5.201 | 10.446 | 4.8251 | 3.5198 | 5.0047 | 10.5223 | 4.7511 | 3.4659 | 4.826 | 10.6058 | 4.6835 | 3.4165 | 4.6781 | 10.6993 | 4.5592 | 3.3258 | 4.5132 | 10.9994 | 4.2033 | 3.0663 | 3.7135 | 11.1944 | 3.4455 | 2.5135 | 2.6459 | 11.2881 | 2.8658 | 2.0906 | 2.0179 | 11.3379 | 2.9513 | 2.1529 | 1.6283 | 10.0882 | 5.1504 | 3.7572 | 5.6102 | 10.1387 | 5.0781 | 3.7044 | 5.543 | 10.2184 | 4.9774 | 3.631 | 5.3826 | 10.273 | 4.8814 | 3.5609 | 5.3869 | 10.3232 | 4.7456 | 3.4619 | 5.2634 | 10.3827 | 4.5938 | 3.3511 | 5.1643 | 10.4493 | 4.4698 | 3.2607 | 4.9888 | 10.5157 | 4.374 | 3.1908 | 4.8421 | 10.5887 | 4.3381 | 3.1646 | 4.7041 | 10.6765 | 4.2377 | 3.0913 | 4.4026 | 10.9506 | 3.6286 | 2.647 | 3.0985 | 11.0844 | 3.0956 | 2.2582 | 2.2686 | 11.1128 | 2.7578 | 2.0118 | 1.9539 | 11.0856 | 2.9808 | 2.1744 | 2.2257
WIGTON | CARLISLE | HARKER / HUTTON | 325814 | 549933 | 14.7486 | 14.7486 | 14.7486 | 2.8903 | 14.9894 | 14.9894 | 14.9894 | 2.1194 | 15.0347 | 15.0347 | 15.0347 | 2.2353 | 15.1574 | 15.1574 | 15.1574 | 1.8659 | 15.334 | 15.334 | 15.334 | 1.547 | 15.5702 | 15.5702 | 15.5702 | 1.0281 | 15.8435 | 15.8435 | 15.8435 | 0.50906 | 16.141 | 16.141 | 16.141 | 0.25918 | 16.4569 | 16.4569 | 16.4569 | -0.33664 | 18.8533 | 18.8533 | 18.8533 | -3.3152 | 19.6027 | 19.6027 | 19.6027 | -5.6552 | 21.1978 | 21.1978 | 19.9297 | -8.1634 | 21.5239 | 21.5239 | 21.5239 | -8.9801 | 21.5769 | 21.5769 | 21.5769 | -8.4244 | 14.5137 | 14.5137 | 14.5137 | 3.2545 | 14.5638 | 14.5638 | 14.5638 | 2.796 | 14.7053 | 14.7053 | 14.7053 | 2.7567 | 14.8835 | 14.8835 | 14.8835 | 2.3854 | 15.0844 | 15.0844 | 15.0844 | 2.0644 | 15.3066 | 15.3066 | 15.3066 | 1.561 | 15.5589 | 15.5589 | 15.5589 | 1.04 | 15.8295 | 15.8295 | 15.8295 | 0.76895 | 16.115 | 16.115 | 16.115 | 0.1695 | 16.412 | 16.412 | 16.412 | -0.49466 | 17.1245 | 17.1245 | 17.1245 | -1.7176 | 17.6194 | 17.6194 | 17.6194 | -3.4995 | 17.9011 | 17.9011 | 17.9011 | -5.0304 | 17.9656 | 17.9656 | 17.9656 | -5.8273 | 14.7552 | 14.7552 | 14.7552 | 2.8981 | 14.9981 | 14.9981 | 14.9981 | 2.1579 | 15.0448 | 15.0448 | 15.0448 | 2.3025 | 15.1682 | 15.1682 | 15.1682 | 1.9638 | 15.344 | 15.344 | 15.344 | 1.6702 | 15.5752 | 15.5752 | 15.5752 | 1.1768 | 15.8406 | 15.8406 | 15.8406 | 0.68242 | 16.1275 | 16.1275 | 16.1275 | 0.45193 | 16.4274 | 16.4274 | 16.4274 | -0.10293 | 18.7948 | 18.7948 | 18.7948 | -2.9865 | 19.523 | 19.523 | 19.523 | -4.9814 | 20.9764 | 20.9764 | 20.1281 | -7.1952 | 21.1841 | 21.1841 | 21.1841 | -7.7943 | 21.1336 | 21.1336 | 21.1336 | -7.1998 | 14.7373 | 14.7373 | 14.7373 | 2.918 | 14.9684 | 14.9684 | 14.9684 | 2.1334 | 15.0198 | 15.0198 | 15.0198 | 2.2331 | 15.1654 | 15.1654 | 15.1654 | 1.8488 | 15.3896 | 15.3896 | 15.3896 | 1.4655 | 15.7091 | 15.7091 | 15.7091 | 0.84575 | 16.1115 | 16.1115 | 16.1115 | 0.16177 | 16.5761 | 16.5761 | 16.5761 | -0.24694 | 16.9062 | 16.9062 | 16.9062 | -0.90683 | 19.1008 | 19.1008 | 19.1008 | -3.6142 | 19.9139 | 19.9139 | 19.9139 | -5.6627 | 21.6732 | 21.6732 | 19.6769 | -9.3964 | 22.0103 | 22.0103 | 21.6018 | -10.8426 | 22.0091 | 22.0091 | 22.0091 | -11.6048 | 14.7351 | 14.7351 | 14.7351 | 2.9422 | 14.9865 | 14.9865 | 14.9865 | 2.1532 | 15.0569 | 15.0569 | 15.0569 | 2.2589 | 15.2107 | 15.2107 | 15.2107 | 1.887 | 15.4445 | 15.4445 | 15.4445 | 1.4696 | 15.7814 | 15.7814 | 15.7814 | 0.85737 | 16.2132 | 16.2132 | 16.2132 | 0.24374 | 18.8533 | 18.8533 | 18.8533 | -2.2364 | 18.9831 | 18.9831 | 18.9831 | -2.7165 | 20.1975 | 20.1975 | 20.154 | -4.6943 | 20.9763 | 20.9763 | 19.8123 | -8.023 | 21.5461 | 21.5461 | 19.9297 | -10.2391 | 21.6566 | 21.6566 | 21.6566 | -11.0721 | 21.3997 | 21.3997 | 21.3997 | -10.2224
WILLOW HEY | SKELMERSDALE | WASHWAY FARM / KIRKBY | 347779 | 406066 | 30.1682 | 9.3863 | 6.7461 | 16.5637 | 30.2488 | 9.1151 | 6.5512 | 16.2737 | 30.2559 | 8.8802 | 6.3824 | 16.1814 | 30.2947 | 8.5984 | 6.1798 | 16.0402 | 30.3558 | 8.3575 | 6.0067 | 15.8403 | 30.433 | 8.1838 | 5.8819 | 15.6161 | 30.5193 | 8.032 | 5.7727 | 15.3665 | 30.6115 | 7.9073 | 5.6831 | 15.0188 | 30.7091 | 7.8366 | 5.6323 | 14.6718 | 30.8172 | 7.6992 | 5.5336 | 14.265 | 31.4238 | 7.2251 | 5.1928 | 12.7775 | 32.1937 | 7.3144 | 5.257 | 11.8798 | 32.8006 | 9.0852 | 6.5297 | 11.5121 | 33.4327 | 9.6646 | 6.9461 | 11.1622 | 30.1182 | 9.5206 | 6.8426 | 16.8031 | 30.1288 | 9.413 | 6.7653 | 16.7049 | 30.1734 | 9.2664 | 6.6599 | 16.5342 | 30.2464 | 9.0806 | 6.5264 | 16.3309 | 30.3268 | 8.9783 | 6.4529 | 16.0932 | 30.4166 | 8.8945 | 6.3926 | 15.8478 | 30.518 | 8.8109 | 6.3326 | 15.5156 | 30.6268 | 8.7334 | 6.2769 | 15.1625 | 30.74 | 8.6538 | 6.2197 | 14.7871 | 30.8441 | 8.5608 | 6.1528 | 14.3892 | 31.2332 | 8.3193 | 5.9792 | 13.569 | 31.6464 | 8.3819 | 6.0243 | 12.7966 | 32.0734 | 9.5032 | 6.8301 | 12.2602 | 32.4314 | 10.3005 | 7.4032 | 11.9011 | 30.1692 | 9.5163 | 6.8396 | 16.5719 | 30.2504 | 9.4014 | 6.757 | 16.29 | 30.2579 | 9.1426 | 6.571 | 16.2062 | 30.2976 | 9.0865 | 6.5307 | 16.0737 | 30.3595 | 8.963 | 6.4419 | 15.8841 | 30.4371 | 8.8268 | 6.344 | 15.6708 | 30.5238 | 8.69 | 6.2457 | 15.4054 | 30.6161 | 8.5769 | 6.1644 | 15.0784 | 30.7128 | 8.4715 | 6.0886 | 14.7503 | 30.8164 | 8.3415 | 5.9952 | 14.384 | 31.33 | 7.9731 | 5.7304 | 13.0769 | 31.8165 | 8.091 | 5.8151 | 12.4299 | 32.2737 | 9.9276 | 7.1352 | 12.0455 | 32.6437 | 10.4676 | 7.5232 | 11.888 | 30.166 | 9.3859 | 6.7458 | 16.5777 | 30.2452 | 9.1098 | 6.5474 | 16.3032 | 30.2434 | 8.8387 | 6.3525 | 16.2259 | 30.2912 | 8.5569 | 6.15 | 16.0938 | 30.3696 | 8.2589 | 5.9359 | 15.8796 | 30.4861 | 8.0035 | 5.7523 | 15.5976 | 30.6318 | 7.9427 | 5.7086 | 15.2688 | 30.8027 | 7.823 | 5.6225 | 14.9211 | 30.9918 | 7.6779 | 5.5182 | 14.5817 | 31.2041 | 7.4991 | 5.3897 | 14.237 | 32.4462 | 6.756 | 4.8556 | 12.1529 | 33.7028 | 6.1554 | 4.424 | 8.4321 | 34.3958 | 7.3905 | 5.3117 | 5.6852 | 34.6311 | 7.5976 | 5.4605 | 3.7642 | 30.1715 | 9.3879 | 6.7473 | 16.5751 | 30.2458 | 9.1906 | 6.6055 | 16.279 | 30.2501 | 8.9681 | 6.4455 | 16.1971 | 30.3001 | 8.7339 | 6.2772 | 16.0651 | 30.3804 | 8.3995 | 6.0369 | 15.8414 | 30.5066 | 8.3376 | 5.9924 | 15.5691 | 30.6786 | 8.2227 | 5.9098 | 15.2316 | 30.8833 | 8.0975 | 5.8198 | 14.8822 | 31.1222 | 7.9947 | 5.746 | 14.5087 | 31.444 | 7.8494 | 5.6415 | 13.7254 | 32.8032 | 8.7421 | 6.2831 | 9.6844 | 33.8841 | 7.7479 | 5.5685 | 6.2847 | 34.2434 | 8.0941 | 5.8174 | 4.3096 | 34.1728 | 7.9499 | 5.7138 | 4.6562
WILLOWBANK | GREENHILL | WHITEGATE | 391885 | 406064 | 26.1482 | 13.4149 | 9.786 | 6.5218 | 26.2693 | 13.0899 | 9.5489 | 6.0684 | 26.2816 | 12.7507 | 9.3015 | 5.9796 | 26.3263 | 12.3419 | 9.0033 | 5.7984 | 26.3943 | 11.9696 | 8.7317 | 5.6013 | 26.4855 | 11.7904 | 8.6009 | 5.3722 | 26.5825 | 11.7631 | 8.581 | 5.1243 | 26.6842 | 11.718 | 8.5481 | 4.8541 | 26.7901 | 11.6512 | 8.4994 | 4.5471 | 26.9053 | 11.5725 | 8.442 | 4.2021 | 27.6048 | 11.198 | 8.1688 | 2.6262 | 28.5325 | 11.0549 | 8.0644 | 1.3001 | 29.2835 | 11.6854 | 8.5243 | 0.45704 | 30.0742 | 11.6265 | 8.4814 | -0.155 | 26.034 | 13.5473 | 9.8826 | 6.8678 | 26.062 | 13.3207 | 9.7173 | 6.7106 | 26.1286 | 13.0426 | 9.5144 | 6.5042 | 26.2105 | 12.7148 | 9.2753 | 6.2307 | 26.3031 | 12.4225 | 9.0621 | 6.0088 | 26.4035 | 12.1754 | 8.8818 | 5.761 | 26.5131 | 12.1101 | 8.8341 | 5.4782 | 26.6288 | 12.0352 | 8.7795 | 5.1649 | 26.7503 | 11.9467 | 8.7149 | 4.7965 | 26.8763 | 11.8578 | 8.6501 | 4.4462 | 27.3439 | 11.622 | 8.4781 | 3.3683 | 27.8873 | 11.484 | 8.3774 | 2.4049 | 28.4428 | 11.9243 | 8.6986 | 1.6735 | 28.9107 | 12.276 | 8.9551 | 1.1668 | 26.1489 | 13.5393 | 9.8768 | 6.5143 | 26.2705 | 13.3518 | 9.74 | 6.0704 | 26.2838 | 13.0519 | 9.5212 | 5.9885 | 26.3296 | 12.7118 | 9.2731 | 5.7854 | 26.3986 | 12.3834 | 9.0335 | 5.6305 | 26.4905 | 12.0671 | 8.8028 | 5.3883 | 26.5879 | 11.9828 | 8.7413 | 5.145 | 26.6899 | 11.881 | 8.667 | 4.8662 | 26.7952 | 11.7905 | 8.601 | 4.5681 | 26.9063 | 11.6951 | 8.5314 | 4.2579 | 27.5029 | 11.3519 | 8.281 | 2.8761 | 28.1025 | 11.3079 | 8.249 | 1.8881 | 28.6796 | 12.2024 | 8.9015 | 1.2152 | 29.1624 | 12.1616 | 8.8717 | 0.84053 | 26.1389 | 13.4118 | 9.7837 | 6.5389 | 26.2528 | 13.0993 | 9.5557 | 6.1004 | 26.2639 | 12.7422 | 9.2953 | 6.0232 | 26.3131 | 12.3045 | 8.9759 | 5.8463 | 26.3921 | 12.0024 | 8.7556 | 5.657 | 26.5158 | 11.7946 | 8.604 | 5.4141 | 26.6689 | 11.7475 | 8.5696 | 5.1115 | 26.8463 | 11.6734 | 8.5156 | 4.7533 | 27.0422 | 11.5929 | 8.4568 | 4.3691 | 27.2588 | 11.4902 | 8.382 | 3.9777 | 28.6256 | 10.889 | 7.9434 | 1.424 | 30.1495 | 10.0145 | 7.3054 | -3.0927 | 31.1403 | 9.9784 | 7.2791 | -6.7673 | 31.5272 | 9.531 | 6.9527 | -9.2711 | 26.1324 | 13.4149 | 9.786 | 6.5531 | 26.2469 | 13.4285 | 9.7959 | 6.1079 | 26.263 | 13.3512 | 9.7395 | 6.0308 | 26.3148 | 13.1003 | 9.5565 | 5.843 | 26.3998 | 13.1982 | 9.6279 | 5.6755 | 26.5414 | 13.1707 | 9.6078 | 5.4053 | 26.7274 | 13.0814 | 9.5427 | 5.0977 | 26.9483 | 12.9769 | 9.4665 | 4.7327 | 27.2117 | 12.8451 | 9.3704 | 4.2504 | 27.54 | 12.5793 | 9.1764 | 3.208 | 29.0963 | 11.4696 | 8.3669 | -1.7482 | 30.4439 | 10.2641 | 7.4875 | -6.0698 | 31.05 | 9.6773 | 7.0594 | -8.6898 | 31.0715 | 9.6438 | 7.035 | -8.2882
WILLOWHOLME | CARLISLE | HARKER / HUTTON | 338653 | 556688 | 28.1556 | 7.7372 | 5.5609 | 16.0123 | 28.2259 | 7.5399 | 5.4191 | 15.5811 | 28.3001 | 7.3504 | 5.2829 | 15.3448 | 28.3845 | 7.1043 | 5.106 | 15.0613 | 28.5014 | 6.9118 | 4.9677 | 14.9269 | 28.6379 | 6.5044 | 4.6748 | 14.5336 | 28.793 | 6.2282 | 4.4763 | 14.1034 | 28.9621 | 5.9702 | 4.2909 | 13.7115 | 29.149 | 5.7978 | 4.167 | 13.3284 | 29.38 | 5.6083 | 4.0308 | 12.8187 | 30.4408 | 5.2475 | 3.7715 | 11.1356 | 31.0241 | 5.1658 | 3.7128 | 10.3021 | 31.3345 | 6.359 | 4.5703 | 10.133 | 31.5315 | 7.1069 | 5.1079 | 10.3815 | 28.1521 | 7.8234 | 5.6229 | 16.3854 | 28.2148 | 7.6753 | 5.5164 | 16.2695 | 28.3004 | 7.5069 | 5.3954 | 15.9943 | 28.3717 | 7.3229 | 5.2631 | 15.6858 | 28.4686 | 7.174 | 5.1561 | 15.5553 | 28.582 | 6.8757 | 4.9417 | 15.1976 | 28.7092 | 6.68 | 4.8011 | 14.8022 | 28.8456 | 6.4989 | 4.6709 | 14.4421 | 28.9901 | 6.3216 | 4.5435 | 14.0888 | 29.141 | 6.1401 | 4.413 | 13.6695 | 29.7756 | 5.8848 | 4.2296 | 12.4292 | 30.3749 | 5.7685 | 4.1459 | 11.5841 | 30.6061 | 6.5685 | 4.7209 | 11.1396 | 30.7055 | 7.3385 | 5.2743 | 10.9954 | 28.157 | 7.8214 | 5.6214 | 16.0163 | 28.2279 | 7.6701 | 5.5127 | 15.5952 | 28.3024 | 7.4827 | 5.378 | 15.3696 | 28.3872 | 7.2841 | 5.2352 | 15.0945 | 28.5039 | 7.1271 | 5.1224 | 14.9697 | 28.6391 | 6.8067 | 4.8921 | 14.5892 | 28.7924 | 6.5863 | 4.7337 | 14.1719 | 28.9592 | 6.381 | 4.5862 | 13.7926 | 29.1418 | 6.1793 | 4.4412 | 13.4292 | 29.3623 | 5.9742 | 4.2938 | 12.9655 | 30.3622 | 5.6094 | 4.0316 | 11.4539 | 30.8207 | 5.4267 | 3.9003 | 10.7985 | 31.0372 | 6.3748 | 4.5817 | 10.727 | 31.146 | 7.068 | 5.0799 | 11.03 | 28.1617 | 7.7378 | 5.5613 | 16.0327 | 28.2422 | 7.5328 | 5.414 | 15.6266 | 28.3355 | 7.3819 | 5.3055 | 15.4194 | 28.4514 | 7.1295 | 5.1241 | 15.1623 | 28.5997 | 6.9343 | 4.9838 | 15.0767 | 28.7848 | 6.5455 | 4.7044 | 14.741 | 29.0175 | 6.3728 | 4.5802 | 14.3601 | 29.2808 | 6.1566 | 4.4249 | 14.0254 | 29.5592 | 5.947 | 4.2742 | 13.743 | 29.8671 | 5.7218 | 4.1123 | 13.3942 | 30.9698 | 5.1215 | 3.6809 | 11.4063 | 26.2984 | 4.3298 | 3.1119 | 7.7512 | 28.9959 | 4.7739 | 3.4311 | 4.9405 | 30.6722 | 5.0499 | 3.6295 | 3.1991 | 28.1602 | 7.7389 | 5.5621 | 16.0265 | 28.2483 | 7.6057 | 5.4664 | 15.5859 | 28.3493 | 7.408 | 5.3243 | 15.3657 | 28.4748 | 7.2067 | 5.1796 | 15.1164 | 28.6377 | 7.1938 | 5.1703 | 15.0369 | 28.8336 | 7.1222 | 5.1188 | 14.7263 | 29.0737 | 6.9684 | 5.0084 | 14.3752 | 29.3432 | 6.8444 | 4.9192 | 14.0816 | 29.7006 | 6.7025 | 4.8173 | 13.7322 | 30.1362 | 6.4464 | 4.6331 | 12.7777 | 31.1065 | 5.3767 | 3.8643 | 8.5471 | 27.6039 | 4.5448 | 3.2664 | 5.3042 | 32.2246 | 5.4904 | 3.9461 | 3.5001 | 32.2014 | 5.3886 | 3.8729 | 4.1828
WILMSLOW | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 25.0428 | 11.2 | 8.0496 | 8.173 | 25.1337 | 11.1203 | 7.9923 | 7.7547 | 25.1551 | 11.0749 | 7.9597 | 7.702 | 25.2112 | 10.9772 | 7.8895 | 7.5471 | 25.2864 | 10.8426 | 7.7928 | 7.3081 | 25.3813 | 10.7035 | 7.6928 | 6.971 | 25.4825 | 10.5379 | 7.5738 | 6.6073 | 25.5879 | 10.384 | 7.4632 | 6.3504 | 25.6975 | 10.21 | 7.3381 | 6.1012 | 25.8132 | 10.0677 | 7.2359 | 5.7709 | 26.2524 | 9.2936 | 6.6795 | 4.6798 | 26.5696 | 9.1204 | 6.555 | 4.0535 | 26.763 | 9.2311 | 6.6346 | 3.8469 | 26.8801 | 8.9489 | 6.4318 | 3.8223 | 24.9711 | 11.2212 | 8.0649 | 8.322 | 25.0029 | 11.177 | 8.0332 | 8.0641 | 25.0623 | 11.1158 | 7.9891 | 7.8829 | 25.143 | 11.026 | 7.9246 | 7.6905 | 25.2324 | 10.9234 | 7.8509 | 7.4112 | 25.3301 | 10.824 | 7.7794 | 7.0538 | 25.4359 | 10.7052 | 7.6941 | 6.6434 | 25.5471 | 10.6086 | 7.6246 | 6.3175 | 25.6643 | 10.5077 | 7.5521 | 6.0102 | 25.7858 | 10.4011 | 7.4755 | 5.6369 | 26.016 | 10.1119 | 7.2676 | 4.7116 | 26.1925 | 9.8264 | 7.0624 | 4.0076 | 26.3024 | 9.7198 | 6.9858 | 3.594 | 26.3587 | 9.8566 | 7.0841 | 3.2961 | 25.0428 | 11.2165 | 8.0615 | 8.1823 | 25.1337 | 11.1481 | 8.0124 | 7.7906 | 25.1551 | 11.0564 | 7.9465 | 7.7537 | 25.2112 | 10.9268 | 7.8533 | 7.6177 | 25.286 | 10.7762 | 7.745 | 7.3981 | 25.3804 | 10.6532 | 7.6567 | 7.0816 | 25.4813 | 10.5227 | 7.5628 | 6.739 | 25.5864 | 10.3896 | 7.4672 | 6.4977 | 25.6946 | 10.2889 | 7.3948 | 6.2747 | 25.8046 | 10.156 | 7.2993 | 5.982 | 26.2178 | 9.5029 | 6.8299 | 4.9989 | 26.5123 | 9.457 | 6.7969 | 4.4466 | 26.6928 | 9.4842 | 6.8165 | 4.258 | 26.8046 | 9.4711 | 6.807 | 4.2393 | 25.0372 | 11.1985 | 8.0486 | 8.1904 | 25.1261 | 11.1219 | 7.9935 | 7.7907 | 25.1539 | 11.0571 | 7.947 | 7.7682 | 25.2254 | 10.9603 | 7.8774 | 7.6122 | 25.3236 | 10.8058 | 7.7663 | 7.3935 | 25.4513 | 10.6488 | 7.6535 | 7.0736 | 25.596 | 10.4659 | 7.522 | 6.7213 | 25.7545 | 10.2929 | 7.3977 | 6.4784 | 25.9265 | 10.129 | 7.2799 | 6.2603 | 26.1128 | 9.9865 | 7.1775 | 5.9985 | 26.6737 | 9.1082 | 6.5462 | 4.6016 | 27.1026 | 8.2924 | 5.9599 | 1.7217 | 27.2752 | 8.0368 | 5.7762 | -0.47683 | 27.3073 | 7.6177 | 5.475 | -2.008 | 25.0422 | 11.1953 | 8.0463 | 8.1768 | 25.1425 | 11.1183 | 7.9909 | 7.7743 | 25.1673 | 11.0421 | 7.9362 | 7.779 | 25.2278 | 10.9308 | 7.8562 | 7.6752 | 25.3135 | 10.7166 | 7.7022 | 7.5076 | 25.4237 | 10.4874 | 7.5375 | 7.248 | 25.5531 | 10.3279 | 7.4229 | 6.9539 | 25.6895 | 10.1787 | 7.3156 | 6.7738 | 25.8389 | 10.0019 | 7.1886 | 6.5338 | 26.0175 | 9.7119 | 6.9802 | 5.8009 | 26.5456 | 8.7726 | 6.305 | 2.5017 | 26.8286 | 7.9869 | 5.7404 | -0.12216 | 26.8687 | 7.6898 | 5.5268 | -1.5804 | 26.7571 | 7.5755 | 5.4446 | -1.1416
WINDERMERE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 341657 | 498418 | 29.3796 | 22.4639 | 16.1452 | 13.4644 | 29.4186 | 22.3765 | 16.0824 | 13.1251 | 29.4792 | 22.2581 | 15.9974 | 12.818 | 29.55 | 22.0923 | 15.8782 | 12.398 | 29.632 | 21.941 | 15.7695 | 12.0936 | 29.7289 | 21.7355 | 15.6217 | 11.6134 | 29.8446 | 21.5099 | 15.4596 | 11.0667 | 29.9714 | 21.3066 | 15.3135 | 10.574 | 30.1072 | 21.0858 | 15.1548 | 10.0738 | 30.2619 | 20.808 | 14.9551 | 9.3929 | 30.7956 | 19.7381 | 14.1862 | 7.0466 | 31.1732 | 19.132 | 13.7505 | 5.8811 | 31.3748 | 18.5987 | 13.3673 | 5.6195 | 31.4691 | 18.1208 | 13.0238 | 5.9977 | 29.4165 | 22.4918 | 16.1653 | 13.5474 | 29.4902 | 22.4277 | 16.1193 | 13.298 | 29.581 | 22.3318 | 16.0503 | 12.9266 | 29.6775 | 22.2074 | 15.9609 | 12.5488 | 29.7854 | 22.1022 | 15.8853 | 12.2873 | 29.9127 | 21.9489 | 15.7751 | 11.8467 | 30.0594 | 21.793 | 15.663 | 11.3379 | 30.2208 | 21.6497 | 15.5601 | 10.87 | 30.3982 | 21.4986 | 15.4515 | 10.3553 | 30.5919 | 21.2469 | 15.2706 | 9.2471 | 30.8679 | 20.8766 | 15.0044 | 8.425 | 31.0779 | 20.446 | 14.6949 | 7.4125 | 31.2112 | 20.1054 | 14.4502 | 6.7743 | 31.2991 | 19.7472 | 14.1927 | 6.3939 | 29.38 | 22.4904 | 16.1643 | 13.4683 | 29.4191 | 22.4204 | 16.114 | 13.1455 | 29.4799 | 22.2921 | 16.0218 | 12.8579 | 29.551 | 22.1171 | 15.896 | 12.4627 | 29.6327 | 21.9583 | 15.7819 | 12.1815 | 29.7286 | 21.7406 | 15.6254 | 11.7287 | 29.8431 | 21.5157 | 15.4638 | 11.2101 | 29.9687 | 21.2831 | 15.2966 | 10.744 | 30.1017 | 21.0762 | 15.1479 | 10.2753 | 30.248 | 20.7485 | 14.9123 | 9.6641 | 30.7475 | 19.898 | 14.3011 | 7.5288 | 31.0822 | 18.9808 | 13.6418 | 6.5002 | 31.2481 | 18.6033 | 13.3706 | 6.2888 | 31.326 | 18.5442 | 13.3281 | 6.638 | 29.3845 | 22.4624 | 16.1441 | 13.468 | 29.4285 | 22.2871 | 16.0181 | 13.1144 | 29.4869 | 22.1429 | 15.9145 | 12.7999 | 29.566 | 21.9564 | 15.7805 | 12.3831 | 29.6662 | 21.7816 | 15.6549 | 12.064 | 29.7904 | 21.5451 | 15.4849 | 11.5572 | 29.9463 | 21.2713 | 15.2881 | 10.9581 | 30.1236 | 20.9922 | 15.0875 | 10.4083 | 30.3194 | 20.7704 | 14.9281 | 9.9189 | 30.5409 | 20.5204 | 14.7484 | 9.3945 | 31.2176 | 19.2886 | 13.8631 | 6.9515 | 31.7739 | 17.7424 | 12.7518 | 2.7141 | 32.0763 | 16.4928 | 11.8537 | -0.17496 | 32.2536 | 15.3952 | 11.0648 | -2.4042 | 29.3804 | 22.4532 | 16.1376 | 13.4109 | 29.4192 | 22.3518 | 16.0647 | 13.0115 | 29.4623 | 22.1908 | 15.9489 | 12.7236 | 29.5232 | 21.982 | 15.7989 | 12.3452 | 29.6044 | 21.7857 | 15.6578 | 12.0613 | 29.7051 | 21.526 | 15.4712 | 11.6222 | 29.8393 | 21.2582 | 15.2787 | 11.1124 | 29.9877 | 21.017 | 15.1053 | 10.6844 | 30.1509 | 20.7613 | 14.9216 | 10.2892 | 30.3576 | 20.3579 | 14.6316 | 9.2031 | 31.014 | 18.7062 | 13.4445 | 4.247 | 31.4052 | 17.1248 | 12.3079 | 0.68074 | 31.5569 | 16.2271 | 11.6627 | -1.2401 | 31.5467 | 15.5446 | 11.1722 | -0.63353
WINIFRED RD | ADSWOOD | BREDBURY | 389971 | 388470 | 12.6827 | 12.6827 | 10.2061 | 8.8237 | 12.7206 | 12.7206 | 10.0842 | 8.1619 | 12.7629 | 12.7629 | 10.0329 | 8.2858 | 12.8252 | 12.8252 | 9.8948 | 7.7969 | 12.9053 | 12.9053 | 9.7909 | 7.8406 | 12.9991 | 12.9991 | 9.752 | 7.4901 | 13.1058 | 13.1058 | 9.6485 | 7.06 | 13.2224 | 13.1024 | 9.558 | 6.6558 | 13.349 | 12.9528 | 9.4489 | 6.249 | 13.4895 | 12.8018 | 9.3387 | 5.6997 | 14.0344 | 12.1079 | 8.8325 | 4.0355 | 14.4393 | 11.5131 | 8.3986 | 3.2957 | 14.6848 | 11.387 | 8.3067 | 3.1765 | 14.8307 | 11.2482 | 8.2054 | 3.4795 | 12.689 | 12.689 | 10.1829 | 9.0248 | 12.7393 | 12.7393 | 9.9587 | 8.5355 | 12.8077 | 12.8077 | 9.9224 | 8.5754 | 12.8858 | 12.8858 | 9.8461 | 8.0535 | 12.9766 | 12.9766 | 9.8225 | 8.0809 | 13.0815 | 13.0815 | 9.7485 | 7.7257 | 13.2001 | 13.2001 | 9.7478 | 7.3157 | 13.3293 | 13.2959 | 9.6992 | 6.9097 | 13.4702 | 13.2103 | 9.6367 | 6.4434 | 13.6213 | 13.1168 | 9.5685 | 6.0521 | 13.9102 | 12.8612 | 9.3821 | 4.8779 | 14.1253 | 12.588 | 9.1828 | 4.1139 | 14.2641 | 12.406 | 9.05 | 3.6914 | 14.3625 | 12.2934 | 8.9678 | 3.5581 | 12.683 | 12.683 | 10.1746 | 8.8331 | 12.7211 | 12.7211 | 10.0473 | 8.1848 | 12.7637 | 12.7637 | 9.9307 | 8.3141 | 12.8262 | 12.8262 | 9.8962 | 7.8394 | 12.9059 | 12.9059 | 9.8969 | 7.8904 | 12.9991 | 12.9991 | 9.8202 | 7.5542 | 13.1046 | 13.1046 | 9.7355 | 7.1294 | 13.22 | 13.22 | 9.6512 | 6.7399 | 13.3438 | 13.1143 | 9.5667 | 6.355 | 13.4766 | 12.9961 | 9.4805 | 5.8571 | 13.9851 | 12.4913 | 9.1122 | 4.3444 | 14.3386 | 12.0991 | 8.8261 | 3.7096 | 14.5462 | 11.6584 | 8.5046 | 3.6292 | 14.6657 | 11.5752 | 8.4439 | 3.9244 | 12.6833 | 12.6833 | 10.2073 | 8.8382 | 12.7242 | 12.7242 | 10.0807 | 8.1957 | 12.7732 | 12.7732 | 9.99 | 8.3463 | 12.8523 | 12.8523 | 9.8163 | 7.8902 | 12.9575 | 12.9575 | 9.8155 | 7.9737 | 13.089 | 13.089 | 9.7349 | 7.6748 | 13.248 | 13.1942 | 9.625 | 7.2696 | 13.4306 | 13.0781 | 9.5403 | 6.9172 | 13.6238 | 12.9386 | 9.4386 | 6.6185 | 13.84 | 12.7673 | 9.3136 | 6.2293 | 14.5443 | 11.7832 | 8.5957 | 3.9973 | 15.2128 | 10.4147 | 7.5974 | -0.85731 | 15.615 | 9.3858 | 6.8468 | -4.8017 | 15.8334 | 8.704 | 6.3494 | -7.1593 | 12.6716 | 12.6716 | 10.2102 | 8.8486 | 12.7083 | 12.7083 | 10.096 | 8.1878 | 12.75 | 12.75 | 9.935 | 8.3529 | 12.8145 | 12.8145 | 9.9108 | 7.9491 | 12.9032 | 12.9032 | 9.8834 | 8.0915 | 13.0141 | 13.0141 | 9.7784 | 7.8693 | 13.156 | 13.156 | 9.6662 | 7.4851 | 13.3161 | 13.109 | 9.5628 | 7.2131 | 13.5033 | 12.9392 | 9.439 | 6.8553 | 13.7274 | 12.6027 | 9.1935 | 5.6114 | 14.4837 | 10.8914 | 7.9451 | 0.068592 | 14.9859 | 9.7337 | 7.1006 | -4.2839 | 15.1927 | 9.0251 | 6.5837 | -6.8859 | 15.1427 | 8.99 | 6.5581 | -5.7496
WITHINGTON | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 24.765 | 10.1858 | 7.4304 | 6.0461 | 24.8341 | 10.1013 | 7.3688 | 5.6652 | 24.8782 | 10.001 | 7.2956 | 5.3645 | 24.9452 | 9.8952 | 7.2184 | 5.0241 | 25.036 | 9.798 | 7.1475 | 4.5625 | 25.1452 | 9.6906 | 7.0691 | 4.0588 | 25.2628 | 9.542 | 6.9608 | 3.4923 | 25.3885 | 9.4047 | 6.8606 | 2.95 | 25.5217 | 9.2518 | 6.7491 | 2.462 | 25.6699 | 9.0635 | 6.6117 | 1.8492 | 26.2294 | 8.1283 | 5.9295 | -0.33932 | 26.6099 | 7.678 | 5.601 | -1.4842 | 26.797 | 7.6216 | 5.5599 | -1.8421 | 26.9048 | 7.5976 | 5.5423 | -1.8002 | 24.7322 | 10.17 | 7.4188 | 6.1961 | 24.7837 | 10.1189 | 7.3816 | 5.9417 | 24.8649 | 10.0099 | 7.3021 | 5.5593 | 24.9563 | 9.9265 | 7.2413 | 5.2252 | 25.0653 | 9.8122 | 7.1579 | 4.7922 | 25.1879 | 9.6821 | 7.0629 | 4.3125 | 25.3223 | 9.5628 | 6.9759 | 3.7557 | 25.4673 | 9.4397 | 6.8861 | 3.2067 | 25.6232 | 9.3274 | 6.8042 | 2.695 | 25.7898 | 9.2 | 6.7113 | 2.1199 | 26.0893 | 8.7514 | 6.384 | 0.44639 | 26.3181 | 8.3934 | 6.1228 | -0.71716 | 26.458 | 8.1967 | 5.9793 | -1.3513 | 26.5493 | 8.1388 | 5.9371 | -1.7563 | 24.765 | 10.1699 | 7.4188 | 6.0808 | 24.8341 | 10.1141 | 7.3781 | 5.7237 | 24.8782 | 9.9959 | 7.2919 | 5.405 | 24.9452 | 9.8918 | 7.2159 | 5.0836 | 25.0357 | 9.7406 | 7.1056 | 4.645 | 25.1443 | 9.6025 | 7.0049 | 4.1586 | 25.2615 | 9.432 | 6.8805 | 3.5999 | 25.3868 | 9.2712 | 6.7632 | 3.0962 | 25.5185 | 9.0894 | 6.6306 | 2.6226 | 25.6604 | 8.9341 | 6.5173 | 2.0642 | 26.191 | 8.1736 | 5.9625 | 0.024824 | 26.5475 | 7.7838 | 5.6782 | -1.0688 | 26.7229 | 7.7498 | 5.6533 | -1.4038 | 26.8273 | 7.7008 | 5.6176 | -1.3867 | 24.7614 | 10.1883 | 7.4322 | 6.0595 | 24.8346 | 10.1074 | 7.3732 | 5.682 | 24.8874 | 9.9962 | 7.2921 | 5.3813 | 24.9765 | 9.881 | 7.208 | 5.0285 | 25.1001 | 9.7719 | 7.1285 | 4.5634 | 25.2566 | 9.6368 | 7.0299 | 4.0382 | 25.4386 | 9.472 | 6.9097 | 3.4167 | 25.6279 | 9.2941 | 6.7799 | 2.8103 | 25.8227 | 9.113 | 6.6478 | 2.3291 | 26.0393 | 8.9061 | 6.4969 | 1.7853 | 26.6946 | 7.4968 | 5.4688 | -1.1303 | 27.2646 | 6.3167 | 4.6079 | -6.4995 | 27.5781 | 5.4112 | 3.9474 | -10.4151 | 27.761 | 4.7534 | 3.4675 | -13.1935 | 24.7478 | 10.1913 | 7.4344 | 6.0594 | 24.8137 | 10.1374 | 7.3951 | 5.6442 | 24.8642 | 10.0297 | 7.3166 | 5.3484 | 24.943 | 9.9167 | 7.2341 | 5.0401 | 25.0526 | 9.8228 | 7.1656 | 4.6243 | 25.1878 | 9.6681 | 7.0527 | 4.1781 | 25.3261 | 9.4775 | 6.9137 | 3.6407 | 25.4729 | 9.2853 | 6.7735 | 3.14 | 25.6353 | 9.0813 | 6.6247 | 2.676 | 25.8561 | 8.666 | 6.3217 | 1.3124 | 26.5754 | 6.9817 | 5.093 | -5.1423 | 26.9918 | 5.5794 | 4.0701 | -9.9613 | 27.1237 | 5.204 | 3.7963 | -12.5428 | 27.0262 | 5.0574 | 3.6893 | -11.6592
WITHYFOLD DRIVE | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.5645 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
WOODBINE ST | CASTLETON | ROCHDALE | 390519 | 412388 | 23.1501 | 14.9337 | 10.8939 | 9.5775 | 23.2258 | 13.7133 | 10.0036 | 9.2218 | 23.3624 | 12.2881 | 8.964 | 9.0053 | 23.5214 | 10.6041 | 7.7356 | 8.8936 | 23.7174 | 9.5844 | 6.9917 | 8.6958 | 23.9283 | 8.2508 | 6.0189 | 8.2607 | 24.0629 | 8.1667 | 5.9575 | 7.8379 | 24.1858 | 8.1127 | 5.9181 | 7.6684 | 24.3182 | 8.0128 | 5.8452 | 7.2842 | 24.4729 | 7.8803 | 5.7486 | 6.8037 | 25.2777 | 7.6773 | 5.6005 | 5.5693 | 26.0156 | 9.1856 | 6.7008 | 4.7363 | 26.4972 | 12.3921 | 9.0399 | 4.3957 | 26.979 | 12.882 | 9.3973 | 4.1898 | 23.1622 | 14.9377 | 10.8969 | 9.7381 | 23.2453 | 13.4925 | 9.8426 | 9.5442 | 23.3732 | 11.8795 | 8.666 | 9.2539 | 23.4927 | 10.6315 | 7.7556 | 9.1144 | 23.6331 | 9.4443 | 6.8895 | 8.9142 | 23.7868 | 8.0877 | 5.8999 | 8.4964 | 23.9549 | 7.9908 | 5.8292 | 8.084 | 24.1113 | 7.9215 | 5.7786 | 7.8982 | 24.2193 | 7.8385 | 5.7181 | 7.5287 | 24.3315 | 7.7289 | 5.6382 | 7.0773 | 24.8095 | 7.7406 | 5.6466 | 6.1494 | 25.2837 | 8.8646 | 6.4666 | 5.3591 | 25.7082 | 10.7859 | 7.8681 | 4.846 | 26.0284 | 11.0958 | 8.0943 | 4.4286 | 23.1502 | 14.9362 | 10.8958 | 9.5773 | 23.2261 | 13.4391 | 9.8036 | 9.2484 | 23.3631 | 11.8526 | 8.6463 | 9.0447 | 23.5226 | 10.7059 | 7.8098 | 8.9422 | 23.7181 | 9.4124 | 6.8662 | 8.7568 | 23.928 | 7.9864 | 5.826 | 8.3376 | 24.0651 | 7.87 | 5.7411 | 7.9302 | 24.1883 | 7.7963 | 5.6873 | 7.7363 | 24.3199 | 7.7021 | 5.6186 | 7.4062 | 24.4697 | 7.5832 | 5.5318 | 6.9624 | 25.2081 | 7.4903 | 5.4641 | 5.8267 | 25.7701 | 9.2474 | 6.7459 | 5.1682 | 26.1626 | 12.2368 | 8.9266 | 4.8785 | 26.4878 | 12.7187 | 9.2781 | 4.7677 | 23.1525 | 14.9363 | 10.8958 | 9.5845 | 23.2354 | 13.8066 | 10.0717 | 9.2363 | 23.3885 | 12.233 | 8.9238 | 9.0251 | 23.5743 | 10.9813 | 8.0107 | 8.915 | 23.8034 | 9.7332 | 7.1002 | 8.7285 | 24.0664 | 8.3588 | 6.0976 | 8.2996 | 24.3592 | 8.244 | 6.0139 | 7.871 | 24.614 | 8.1399 | 5.9379 | 7.6789 | 24.8769 | 8.0087 | 5.8422 | 7.3277 | 25.1703 | 7.8712 | 5.742 | 6.9048 | 26.2489 | 7.2853 | 5.3145 | 5.1292 | 27.3721 | 8.6583 | 6.3161 | 1.4399 | 28.0009 | 10.9773 | 8.0078 | -1.4553 | 28.3076 | 11.0251 | 8.0426 | -3.5546 | 23.1629 | 14.9433 | 10.9009 | 9.6022 | 23.2819 | 14.995 | 10.9387 | 9.244 | 23.4602 | 14.8135 | 10.8062 | 9.0354 | 23.6526 | 14.5451 | 10.6105 | 8.9494 | 23.8823 | 14.6477 | 10.6853 | 8.7936 | 24.137 | 14.4811 | 10.5637 | 8.4068 | 24.3736 | 14.3115 | 10.44 | 8.0138 | 24.6395 | 14.2104 | 10.3663 | 7.8746 | 24.9781 | 14.0474 | 10.2474 | 7.4615 | 25.3136 | 13.7621 | 10.0393 | 6.4368 | 26.5137 | 12.7424 | 9.2954 | 2.3271 | 27.3549 | 11.9066 | 8.6857 | -1.0331 | 27.7082 | 11.3731 | 8.2965 | -2.9688 | 27.7177 | 11.2765 | 8.2261 | -2.6097
WOODFIELD RD | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 358258 | 418014 | 32.8217 | 15.8494 | 11.3913 | 10.5779 | 32.9387 | 15.1522 | 10.8902 | 9.6045 | 32.9837 | 14.9734 | 10.7617 | 9.0342 | 33.0678 | 14.5461 | 10.4546 | 8.6703 | 33.1802 | 14.146 | 10.167 | 8.3545 | 33.3194 | 13.7634 | 9.892 | 7.889 | 33.4734 | 13.4265 | 9.6499 | 7.2658 | 33.6371 | 13.092 | 9.4095 | 6.6391 | 33.8103 | 12.7786 | 9.1842 | 6.0048 | 33.9978 | 12.3956 | 8.909 | 5.27 | 34.8958 | 10.8606 | 7.8057 | 2.5348 | 35.8615 | 9.8761 | 7.0982 | 0.70151 | 36.5964 | 9.8212 | 7.0587 | -0.15476 | 37.327 | 9.803 | 7.0456 | -0.62281 | 32.7699 | 16.1923 | 11.6377 | 11.0978 | 32.8334 | 15.9258 | 11.4462 | 10.6111 | 32.9327 | 15.5424 | 11.1706 | 10.0636 | 33.0548 | 15.1985 | 10.9235 | 9.6339 | 33.1928 | 14.8566 | 10.6778 | 9.1804 | 33.3456 | 14.5914 | 10.4871 | 8.6444 | 33.5139 | 14.3552 | 10.3174 | 8.0204 | 33.6929 | 14.1029 | 10.136 | 7.3875 | 33.884 | 13.8622 | 9.9631 | 6.7357 | 34.0845 | 13.5984 | 9.7735 | 6.0522 | 34.6018 | 12.7647 | 9.1743 | 3.8951 | 35.1259 | 12.1214 | 8.7119 | 2.1591 | 35.6301 | 11.9325 | 8.5761 | 1.0116 | 36.0604 | 11.7191 | 8.4227 | 0.095925 | 32.8219 | 16.1919 | 11.6375 | 10.597 | 32.9394 | 15.8687 | 11.4052 | 9.6478 | 32.9849 | 15.326 | 11.0151 | 9.1022 | 33.0699 | 14.8349 | 10.6621 | 8.7591 | 33.1828 | 14.4231 | 10.3662 | 8.4715 | 33.3224 | 14.0019 | 10.0634 | 8.0659 | 33.4767 | 13.7817 | 9.9052 | 7.4797 | 33.6408 | 13.513 | 9.712 | 6.89 | 33.8129 | 13.2007 | 9.4876 | 6.3021 | 33.9932 | 12.9504 | 9.3077 | 5.6459 | 34.7916 | 11.8732 | 8.5335 | 3.2311 | 35.4928 | 11.1101 | 7.985 | 1.7276 | 36.0935 | 10.8447 | 7.7943 | 1.0279 | 36.5883 | 10.5394 | 7.5749 | 0.71852 | 32.816 | 15.8482 | 11.3904 | 10.5957 | 32.9287 | 15.1729 | 10.905 | 9.6375 | 32.9815 | 14.9395 | 10.7373 | 9.0718 | 33.0854 | 14.4813 | 10.408 | 8.6903 | 33.2276 | 14.047 | 10.0959 | 8.3793 | 33.4197 | 13.6231 | 9.7912 | 7.9942 | 33.6529 | 13.289 | 9.551 | 7.421 | 33.9191 | 12.9187 | 9.2849 | 6.8265 | 34.2159 | 12.5785 | 9.0404 | 6.2844 | 34.5451 | 12.2146 | 8.7788 | 5.7174 | 36.0835 | 10.2744 | 7.3844 | 2.1466 | 37.6517 | 8.0679 | 5.7986 | -4.1657 | 38.6196 | 6.8059 | 4.8916 | -9.0424 | 35.4292 | 5.8332 | 4.1924 | -12.3591 | 32.8073 | 15.848 | 11.3903 | 10.6086 | 32.9254 | 15.1781 | 10.9088 | 9.6445 | 32.9784 | 15.0257 | 10.7992 | 9.0909 | 33.0744 | 14.5984 | 10.4921 | 8.7364 | 33.2084 | 14.182 | 10.1929 | 8.4555 | 33.3972 | 13.8099 | 9.9254 | 8.1105 | 33.6412 | 13.4702 | 9.6813 | 7.6397 | 33.92 | 13.1165 | 9.4271 | 7.1358 | 34.2422 | 12.8035 | 9.2021 | 6.4997 | 34.6357 | 12.2444 | 8.8003 | 4.9666 | 36.3331 | 9.909 | 7.1218 | -2.0556 | 37.6442 | 7.7204 | 5.5488 | -7.8145 | 38.1842 | 6.9209 | 4.9742 | -11.1059 | 38.1898 | 6.7108 | 4.8232 | -10.6453
WOODHILL LANE | LANCASTER | HEYSHAM | 343294 | 463785 | 12.1119 | 9.483 | 6.9177 | 1.1827 | 12.157 | 9.4729 | 6.9104 | 1.0932 | 12.1888 | 9.3683 | 6.834 | 1.0324 | 12.2394 | 9.1227 | 6.6549 | 0.91032 | 12.304 | 8.9112 | 6.5006 | 0.69484 | 12.3803 | 8.7441 | 6.3787 | 0.53983 | 12.4515 | 8.6228 | 6.2902 | 0.3513 | 12.5154 | 8.5337 | 6.2252 | 0.078074 | 12.5819 | 8.4678 | 6.1771 | -0.045167 | 12.6529 | 8.3809 | 6.1138 | -0.27312 | 12.8437 | 8.0186 | 5.8495 | -1.0244 | 12.9661 | 7.8079 | 5.6957 | -1.4911 | 13.0312 | 7.6983 | 5.6158 | -1.6661 | 13.0626 | 7.6558 | 5.5848 | -1.4855 | 12.1144 | 9.4474 | 6.8917 | 1.2967 | 12.1696 | 9.4322 | 6.8807 | 1.293 | 12.2452 | 9.3749 | 6.8389 | 1.139 | 12.3357 | 9.2903 | 6.7771 | 0.96621 | 12.4393 | 9.2144 | 6.7218 | 0.70487 | 12.5103 | 9.1321 | 6.6618 | 0.50802 | 12.5816 | 9.0611 | 6.6099 | 0.26313 | 12.6574 | 8.9788 | 6.5499 | -0.080006 | 12.7382 | 8.9121 | 6.5012 | -0.28309 | 12.824 | 8.8259 | 6.4384 | -0.57967 | 12.9404 | 8.6459 | 6.307 | -1.1459 | 13.0214 | 8.4876 | 6.1916 | -1.6123 | 13.0649 | 8.3596 | 6.0982 | -1.8995 | 13.0798 | 8.2947 | 6.0509 | -1.8394 | 12.1119 | 9.4419 | 6.8877 | 1.1941 | 12.157 | 9.413 | 6.8666 | 1.1178 | 12.1888 | 9.3168 | 6.7964 | 1.0726 | 12.2394 | 9.2247 | 6.7293 | 0.96521 | 12.3038 | 9.1098 | 6.6455 | 0.76646 | 12.3798 | 8.9999 | 6.5653 | 0.62537 | 12.451 | 8.9112 | 6.5006 | 0.45143 | 12.5148 | 8.8079 | 6.4252 | 0.19548 | 12.5807 | 8.7326 | 6.3703 | 0.08787 | 12.6495 | 8.6381 | 6.3014 | -0.11337 | 12.8294 | 8.3225 | 6.0711 | -0.81017 | 12.9427 | 8.1094 | 5.9157 | -1.2336 | 13.003 | 7.9607 | 5.8072 | -1.3907 | 13.0328 | 7.8659 | 5.7381 | -1.2043 | 12.1098 | 9.4833 | 6.918 | 1.1886 | 12.1547 | 9.4634 | 6.9034 | 1.0976 | 12.1919 | 9.3836 | 6.8452 | 1.0333 | 12.254 | 9.0882 | 6.6297 | 0.90258 | 12.338 | 8.8853 | 6.4817 | 0.6696 | 12.4091 | 8.7129 | 6.3559 | 0.48728 | 12.4867 | 8.5784 | 6.2578 | 0.25604 | 12.5714 | 8.4743 | 6.1819 | -0.065094 | 12.6621 | 8.3986 | 6.1267 | -0.2156 | 12.7603 | 8.3043 | 6.0579 | -0.44721 | 13.0103 | 7.8062 | 5.6945 | -1.596 | 13.2057 | 7.2114 | 5.2606 | -3.9893 | 13.2952 | 6.7447 | 4.9202 | -5.7897 | 13.3302 | 6.4541 | 4.7082 | -6.7417 | 12.0943 | 9.4888 | 6.922 | 1.2147 | 12.1295 | 9.4716 | 6.9094 | 1.1403 | 12.1574 | 9.3792 | 6.842 | 1.0935 | 12.2048 | 9.0515 | 6.6029 | 0.9886 | 12.268 | 8.8595 | 6.4629 | 0.77959 | 12.3191 | 8.6768 | 6.3296 | 0.63016 | 12.377 | 8.5242 | 6.2183 | 0.43911 | 12.4388 | 8.4112 | 6.1359 | 0.16532 | 12.5059 | 8.3065 | 6.0595 | 0.026358 | 12.5915 | 8.1323 | 5.9324 | -0.59551 | 12.8539 | 7.3725 | 5.3782 | -3.405 | 12.9877 | 6.6556 | 4.8552 | -5.6004 | 13.0076 | 6.3229 | 4.6125 | -6.8268 | 12.9442 | 6.3569 | 4.6372 | -6.135
WOODHOUSE PARK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 25.2653 | 11.3326 | 8.1449 | 9.0304 | 25.3501 | 11.198 | 8.0483 | 8.556 | 25.3636 | 11.1566 | 8.0184 | 8.4558 | 25.4092 | 11.0549 | 7.9454 | 8.3221 | 25.4784 | 10.8545 | 7.8013 | 8.1064 | 25.5698 | 10.6778 | 7.6743 | 7.8011 | 25.67 | 10.3693 | 7.4527 | 7.4709 | 25.7725 | 10.2329 | 7.3546 | 7.2175 | 25.8606 | 10.4185 | 7.488 | 6.9852 | 25.9563 | 10.4405 | 7.5038 | 6.6596 | 26.3495 | 10.1703 | 7.3096 | 5.4074 | 26.6315 | 9.6775 | 6.9554 | 4.6324 | 26.7862 | 9.4314 | 6.7785 | 4.3253 | 26.8623 | 9.2019 | 6.6136 | 4.217 | 25.1911 | 11.2521 | 8.0871 | 9.2587 | 25.2156 | 11.2079 | 8.0553 | 8.9924 | 25.2725 | 11.1688 | 8.0272 | 8.8465 | 25.3463 | 11.0757 | 7.9603 | 8.6971 | 25.4317 | 10.9443 | 7.8659 | 8.4804 | 25.5218 | 10.932 | 7.857 | 8.1886 | 25.6098 | 10.9807 | 7.8921 | 7.8648 | 25.6965 | 11.013 | 7.9152 | 7.6133 | 25.7869 | 11.0281 | 7.9261 | 7.3752 | 25.8806 | 11.0218 | 7.9216 | 7.0845 | 26.1313 | 10.9905 | 7.8991 | 6.1134 | 26.317 | 10.842 | 7.7923 | 5.3961 | 26.4108 | 10.8855 | 7.8236 | 5.0052 | 26.4452 | 10.8579 | 7.8038 | 4.7068 | 25.2659 | 11.2348 | 8.0747 | 9.0574 | 25.3509 | 11.1167 | 7.9898 | 8.5987 | 25.3645 | 11.0463 | 7.9392 | 8.512 | 25.4101 | 11.0923 | 7.9723 | 8.3903 | 25.4791 | 11.1235 | 7.9947 | 8.1907 | 25.5697 | 11.1089 | 7.9842 | 7.9017 | 25.6689 | 11.1003 | 7.978 | 7.588 | 25.7709 | 11.0985 | 7.9767 | 7.3494 | 25.8573 | 11.0717 | 7.9574 | 7.1347 | 25.9485 | 11.0255 | 7.9242 | 6.8385 | 26.3209 | 10.7296 | 7.7116 | 5.6944 | 26.5757 | 10.3579 | 7.4444 | 4.9951 | 26.7063 | 10.2183 | 7.3441 | 4.7168 | 26.7705 | 9.857 | 7.0844 | 4.6175 | 25.2596 | 11.3296 | 8.1428 | 9.0305 | 25.3405 | 11.1883 | 8.0412 | 8.5481 | 25.3572 | 11.1291 | 7.9987 | 8.4245 | 25.413 | 11.0195 | 7.92 | 8.25 | 25.5004 | 10.8082 | 7.7681 | 7.9963 | 25.6199 | 10.537 | 7.5732 | 7.6317 | 25.7367 | 10.1462 | 7.2923 | 7.2102 | 25.8576 | 10.2515 | 7.368 | 6.8441 | 25.9866 | 10.3443 | 7.4347 | 6.5457 | 26.1281 | 10.3048 | 7.4062 | 6.183 | 26.6187 | 9.6974 | 6.9697 | 4.3904 | 27.0558 | 8.5255 | 6.1274 | 0.69861 | 27.2979 | 7.7973 | 5.6041 | -2.2133 | 27.4236 | 7.303 | 5.2488 | -4.6004 | 25.2477 | 11.3336 | 8.1457 | 9.0665 | 25.3236 | 11.1564 | 8.0183 | 8.6077 | 25.3366 | 11.0274 | 7.9256 | 8.5029 | 25.3828 | 10.8372 | 7.7889 | 8.3603 | 25.4592 | 10.4243 | 7.4921 | 8.1506 | 25.5641 | 10.6353 | 7.6438 | 7.8387 | 25.6794 | 10.6805 | 7.6763 | 7.4657 | 25.7883 | 10.6622 | 7.6631 | 7.152 | 25.9055 | 10.6044 | 7.6216 | 6.8658 | 26.0612 | 10.4048 | 7.4782 | 5.9436 | 26.5998 | 9.3036 | 6.6867 | 1.6852 | 26.9276 | 8.111 | 5.8295 | -1.6893 | 27.0469 | 7.8184 | 5.6192 | -3.7612 | 26.9761 | 7.713 | 5.5435 | -3.5544
WOODLEY | VERNON PARK | BREDBURY | 393116 | 392019 | 23.2835 | 8.3269 | 5.9847 | 14.1641 | 23.3929 | 8.0465 | 5.7832 | 13.6624 | 23.413 | 7.8078 | 5.6116 | 13.5315 | 23.4776 | 7.5437 | 5.4218 | 13.4694 | 23.5713 | 7.2669 | 5.2229 | 13.1921 | 23.6951 | 6.962 | 5.0038 | 12.9694 | 23.8375 | 6.9399 | 4.9878 | 12.702 | 23.9934 | 6.8611 | 4.9312 | 12.5179 | 24.1612 | 6.7781 | 4.8715 | 12.2215 | 24.3536 | 6.6681 | 4.7925 | 11.9471 | 25.4433 | 6.1917 | 4.4501 | 10.7594 | 26.9043 | 5.7763 | 4.1516 | 9.2772 | 28.0678 | 6.8406 | 4.9165 | 8.3527 | 29.2851 | 6.6637 | 4.7893 | 7.2817 | 23.177 | 8.3842 | 6.0259 | 14.4698 | 23.1959 | 8.0946 | 5.8178 | 14.2297 | 23.2623 | 7.8997 | 5.6777 | 14.0393 | 23.357 | 7.7131 | 5.5435 | 13.9123 | 23.4561 | 7.4781 | 5.3747 | 13.6017 | 23.5689 | 7.3704 | 5.2972 | 13.3622 | 23.6976 | 7.2707 | 5.2256 | 13.0707 | 23.8358 | 7.2058 | 5.1789 | 12.852 | 23.9838 | 7.11 | 5.1101 | 12.5106 | 24.138 | 6.9827 | 5.0186 | 12.0797 | 24.9211 | 6.8023 | 4.8889 | 11.3576 | 25.8194 | 6.7194 | 4.8294 | 10.4413 | 26.6767 | 7.277 | 5.2301 | 9.6678 | 27.3947 | 7.6768 | 5.5175 | 8.9401 | 23.2859 | 8.382 | 6.0243 | 14.1703 | 23.3969 | 8.1269 | 5.841 | 13.676 | 23.4181 | 7.8812 | 5.6644 | 13.5514 | 23.4849 | 7.6796 | 5.5195 | 13.4947 | 23.5809 | 7.4346 | 5.3434 | 13.2259 | 23.7057 | 7.2854 | 5.2362 | 13.0114 | 23.8485 | 7.1366 | 5.1292 | 12.7529 | 24.0042 | 7.0472 | 5.0649 | 12.5764 | 24.1698 | 6.9838 | 5.0194 | 12.2929 | 24.3539 | 6.8341 | 4.9118 | 12.0426 | 25.2621 | 6.5663 | 4.7194 | 11.0333 | 26.1587 | 6.5919 | 4.7377 | 10.0518 | 27.0188 | 7.5586 | 5.4325 | 9.3637 | 27.764 | 7.2761 | 5.2294 | 8.7479 | 23.2784 | 8.3286 | 5.9859 | 14.1771 | 23.3888 | 8.0515 | 5.7868 | 13.6895 | 23.4197 | 7.7895 | 5.5985 | 13.5721 | 23.4971 | 7.4716 | 5.37 | 13.5201 | 23.6209 | 7.2344 | 5.1995 | 13.2502 | 23.8195 | 7.0354 | 5.0565 | 13.0151 | 24.0829 | 6.9037 | 4.9618 | 12.7136 | 24.4007 | 6.8072 | 4.8924 | 12.4771 | 24.7054 | 6.6897 | 4.8081 | 12.1205 | 25.0894 | 6.5502 | 4.7077 | 11.7073 | 27.152 | 5.6939 | 4.0923 | 9.3176 | 28.6027 | 4.7092 | 3.3846 | 4.389 | 30.1292 | 4.9605 | 3.5652 | 0.58352 | 26.852 | 4.421 | 3.1774 | -1.913 | 23.2776 | 8.3295 | 5.9866 | 14.1755 | 23.4003 | 8.0878 | 5.8128 | 13.6667 | 23.4508 | 7.8563 | 5.6465 | 13.5394 | 23.5534 | 7.5988 | 5.4614 | 13.4934 | 23.6965 | 7.2688 | 5.2242 | 13.2303 | 24.0432 | 7.1354 | 5.1284 | 12.8854 | 24.3801 | 6.9901 | 5.0239 | 12.5568 | 24.7916 | 6.9072 | 4.9643 | 12.2828 | 25.2119 | 6.7919 | 4.8815 | 11.8634 | 25.6845 | 6.6105 | 4.7511 | 11.2237 | 28.1885 | 6.4992 | 4.6711 | 6.1398 | 30.1219 | 5.4075 | 3.8865 | 1.5906 | 29.0327 | 4.78 | 3.4355 | -1.2376 | 28.3883 | 4.6739 | 3.3592 | -1.0096
WOOLFOLD | BURY | KEARSLEY | 378874 | 411666 | 29.0545 | 14.0752 | 10.1161 | 14.5191 | 29.1238 | 14.0092 | 10.0687 | 13.9999 | 29.1895 | 13.9674 | 10.0386 | 13.727 | 29.2769 | 13.8821 | 9.9774 | 13.252 | 29.39 | 13.79 | 9.9111 | 12.8848 | 29.5237 | 13.6299 | 9.796 | 12.3212 | 29.6757 | 13.5461 | 9.7359 | 11.7248 | 29.8424 | 13.4089 | 9.6373 | 11.145 | 30.0228 | 13.2883 | 9.5506 | 10.5477 | 30.2048 | 13.1304 | 9.4371 | 9.9397 | 30.8723 | 12.5865 | 9.0462 | 7.6902 | 31.3516 | 12.4568 | 8.9529 | 6.7248 | 31.6462 | 12.7661 | 9.1752 | 6.5961 | 31.841 | 12.7401 | 9.1565 | 7.0369 | 29.0246 | 14.1281 | 10.1542 | 14.786 | 29.0677 | 14.0651 | 10.1089 | 14.4912 | 29.1395 | 13.9589 | 10.0325 | 14.153 | 29.2147 | 13.8295 | 9.9396 | 13.7134 | 29.2995 | 13.7401 | 9.8753 | 13.4262 | 29.3939 | 13.6011 | 9.7754 | 12.9634 | 29.4978 | 13.4869 | 9.6933 | 12.4642 | 29.6089 | 13.3997 | 9.6306 | 11.9763 | 29.7272 | 13.2973 | 9.557 | 11.4631 | 29.85 | 13.2065 | 9.4918 | 10.991 | 30.1676 | 12.9203 | 9.2861 | 9.4434 | 30.3981 | 12.901 | 9.2722 | 8.539 | 30.5492 | 13.1178 | 9.428 | 8.0566 | 30.6377 | 13.1515 | 9.4522 | 8.0129 | 29.0545 | 14.1312 | 10.1564 | 14.5267 | 29.1238 | 14.0665 | 10.1099 | 14.0216 | 29.1895 | 13.9503 | 10.0264 | 13.7616 | 29.2769 | 13.8405 | 9.9475 | 13.2989 | 29.3894 | 13.7115 | 9.8547 | 12.9475 | 29.5221 | 13.6035 | 9.7771 | 12.4021 | 29.6732 | 13.4854 | 9.6922 | 11.8229 | 29.8394 | 13.3586 | 9.6011 | 11.2587 | 30.0168 | 13.2108 | 9.4949 | 10.6873 | 30.1903 | 13.0853 | 9.4046 | 10.1018 | 30.8129 | 12.7303 | 9.1495 | 8.0205 | 31.2537 | 12.7958 | 9.1966 | 7.1742 | 31.5268 | 13.1844 | 9.4759 | 7.0739 | 31.7136 | 13.2474 | 9.5212 | 7.4796 | 29.0536 | 14.0806 | 10.12 | 14.5462 | 29.1294 | 14.0321 | 10.0851 | 14.0631 | 29.2179 | 13.9932 | 10.0572 | 13.8432 | 29.3433 | 13.9016 | 9.9914 | 13.4353 | 29.5134 | 13.811 | 9.9262 | 13.1652 | 29.7241 | 13.6828 | 9.8341 | 12.7214 | 29.9694 | 13.5978 | 9.773 | 12.2559 | 30.2022 | 13.4841 | 9.6913 | 11.8253 | 30.4604 | 13.3511 | 9.5957 | 11.4419 | 30.7476 | 13.2309 | 9.5093 | 11.0694 | 31.7077 | 12.4743 | 8.9656 | 8.2021 | 32.4315 | 11.5209 | 8.2803 | 3.2347 | 32.8583 | 11.0099 | 7.913 | -0.65282 | 33.1047 | 10.4868 | 7.5371 | -2.946 | 29.0656 | 14.0729 | 10.1145 | 14.4628 | 29.1696 | 14.0444 | 10.094 | 13.8619 | 29.2737 | 14.0187 | 10.0755 | 13.6171 | 29.4037 | 13.9431 | 10.0212 | 13.2292 | 29.5754 | 13.855 | 9.9578 | 12.9924 | 29.7762 | 13.759 | 9.8888 | 12.6102 | 29.985 | 13.6103 | 9.782 | 12.2005 | 30.1966 | 13.5478 | 9.7371 | 11.8491 | 30.4351 | 13.4394 | 9.6592 | 11.3519 | 30.7361 | 13.1802 | 9.4729 | 10.0707 | 31.695 | 12.6169 | 9.068 | 4.0812 | 32.2201 | 11.4624 | 8.2382 | -0.41935 | 32.3991 | 10.7358 | 7.7161 | -2.9969 | 32.3105 | 10.7709 | 7.7413 | -1.6713
WORDSWORTH ST | BOLTON | KEARSLEY | 370709 | 410873 | 31.3645 | 9.3219 | 6.8002 | 13.465 | 31.4133 | 9.194 | 6.7069 | 13.1785 | 31.4309 | 9.0736 | 6.6191 | 13.0468 | 31.4827 | 8.9015 | 6.4936 | 12.8238 | 31.5573 | 8.7135 | 6.3564 | 12.4113 | 31.6511 | 8.4238 | 6.1451 | 11.8315 | 31.757 | 8.3461 | 6.0884 | 11.5758 | 31.8721 | 8.3507 | 6.0917 | 11.2215 | 31.9952 | 8.279 | 6.0394 | 10.729 | 32.1321 | 8.143 | 5.9402 | 10.045 | 32.6514 | 7.6206 | 5.5591 | 8.1985 | 32.9929 | 7.3666 | 5.3738 | 7.3943 | 33.1753 | 7.6621 | 5.5894 | 7.2594 | 33.2679 | 7.3743 | 5.3794 | 7.5823 | 31.3285 | 9.3388 | 6.8125 | 13.688 | 31.3526 | 9.2024 | 6.713 | 13.5013 | 31.4057 | 9.0615 | 6.6102 | 13.2326 | 31.4783 | 8.8784 | 6.4767 | 12.9563 | 31.5626 | 8.7246 | 6.3644 | 12.5271 | 31.6575 | 8.5469 | 6.2349 | 11.9429 | 31.7637 | 8.5437 | 6.2325 | 11.6694 | 31.8782 | 8.5143 | 6.2111 | 11.3275 | 32.0012 | 8.4421 | 6.1584 | 10.7863 | 32.1317 | 8.3673 | 6.1038 | 10.2991 | 32.3563 | 8.2153 | 5.9929 | 9.3382 | 32.5199 | 8.0544 | 5.8756 | 8.5297 | 32.6191 | 8.2525 | 6.0201 | 8.0407 | 32.672 | 8.4992 | 6.2 | 7.8419 | 31.3645 | 9.3333 | 6.8085 | 13.4741 | 31.4134 | 9.1341 | 6.6632 | 13.1977 | 31.4309 | 8.9508 | 6.5295 | 13.1081 | 31.4827 | 8.9627 | 6.5382 | 12.8966 | 31.557 | 8.87 | 6.4705 | 12.4999 | 31.6502 | 8.7402 | 6.3759 | 11.94 | 31.7555 | 8.6907 | 6.3397 | 11.6407 | 31.8702 | 8.602 | 6.2751 | 11.2554 | 31.9916 | 8.4806 | 6.1865 | 10.7841 | 32.1215 | 8.3512 | 6.0921 | 10.156 | 32.6076 | 8.0161 | 5.8476 | 8.4872 | 32.9231 | 7.8414 | 5.7202 | 7.7882 | 33.0921 | 8.1385 | 5.9369 | 7.6519 | 33.1809 | 7.9743 | 5.8171 | 7.9394 | 31.3595 | 9.3236 | 6.8014 | 13.4854 | 31.4056 | 9.1906 | 6.7044 | 13.2207 | 31.4286 | 9.0472 | 6.5998 | 13.1323 | 31.496 | 8.8798 | 6.4777 | 12.9566 | 31.5972 | 8.675 | 6.3283 | 12.6121 | 31.7223 | 8.3511 | 6.092 | 12.1201 | 31.8708 | 8.3998 | 6.1275 | 11.7861 | 32.0404 | 8.3597 | 6.0983 | 11.4269 | 32.2281 | 8.2809 | 6.0408 | 11.0467 | 32.4394 | 8.165 | 5.9562 | 10.5515 | 33.1217 | 7.3468 | 5.3594 | 7.8448 | 33.7684 | 5.757 | 4.1996 | 1.4718 | 31.1099 | 5.0463 | 3.6812 | -3.696 | 25.7579 | 4.1782 | 3.0479 | -7.0835 | 31.3458 | 9.3294 | 6.8057 | 13.5037 | 31.3888 | 9.2157 | 6.7228 | 13.2319 | 31.4107 | 9.0549 | 6.6054 | 13.1238 | 31.4682 | 8.7672 | 6.3956 | 12.9841 | 31.5523 | 8.8706 | 6.471 | 12.6843 | 31.6564 | 8.8293 | 6.4409 | 12.2631 | 31.7869 | 8.7523 | 6.3847 | 11.9783 | 31.9312 | 8.6936 | 6.3419 | 11.7057 | 32.1007 | 8.5583 | 6.2431 | 11.1972 | 32.3406 | 8.1908 | 5.9751 | 9.5186 | 33.1244 | 6.9095 | 5.0404 | 2.3458 | 33.5805 | 5.5085 | 4.0184 | -3.3149 | 28.0187 | 4.5449 | 3.3154 | -6.7428 | 27.3604 | 4.4381 | 3.2376 | -5.4863
WORSLEY MESNES | WIGAN | WASHWAY FARM / KIRKBY | 357435 | 403977 | 29.169 | 13.9216 | 10.1556 | 17.5866 | 29.1925 | 13.1917 | 9.6232 | 17.3496 | 29.2232 | 12.5935 | 9.1868 | 17.1673 | 29.2679 | 11.914 | 8.6911 | 16.1323 | 29.3259 | 11.2546 | 8.21 | 15.0256 | 29.3946 | 10.5527 | 7.6981 | 12.6474 | 29.4751 | 10.1541 | 7.4073 | 10.2426 | 29.564 | 9.8574 | 7.1908 | 8.6385 | 29.6613 | 9.5808 | 6.9891 | 7.0309 | 29.7722 | 9.3599 | 6.828 | 5.7642 | 30.2498 | 9.0054 | 6.5693 | 4.1837 | 30.6403 | 9.3113 | 6.7925 | 3.3974 | 30.8949 | 10.57 | 7.7107 | 3.2136 | 31.0688 | 10.8897 | 7.9439 | 3.3465 | 29.1712 | 13.9766 | 10.1957 | 17.6837 | 29.1986 | 13.4008 | 9.7757 | 17.5268 | 29.2404 | 12.7963 | 9.3347 | 17.3181 | 29.2885 | 12.0758 | 8.8091 | 16.916 | 29.3434 | 11.5158 | 8.4006 | 16.4662 | 29.4048 | 10.9954 | 8.021 | 15.6683 | 29.4745 | 10.8401 | 7.9077 | 14.846 | 29.5501 | 10.7174 | 7.8182 | 14.2133 | 29.6313 | 10.5972 | 7.7305 | 13.5748 | 29.717 | 10.4857 | 7.6491 | 13.0302 | 29.942 | 10.2824 | 7.5009 | 11.9203 | 30.1367 | 10.5407 | 7.6893 | 11.1563 | 30.2868 | 11.2688 | 8.2204 | 10.7297 | 30.4014 | 11.3683 | 8.293 | 10.4707 | 29.169 | 13.9721 | 10.1924 | 17.5937 | 29.1926 | 13.4016 | 9.7763 | 17.363 | 29.2234 | 12.7656 | 9.3123 | 17.1818 | 29.2682 | 11.9165 | 8.6929 | 16.1526 | 29.3261 | 11.4922 | 8.3834 | 15.0544 | 29.3945 | 10.9469 | 7.9856 | 12.6842 | 29.4747 | 10.7718 | 7.8579 | 10.2872 | 29.5635 | 10.6363 | 7.759 | 8.6912 | 29.6595 | 10.4898 | 7.6521 | 7.0981 | 29.7653 | 10.3581 | 7.5561 | 5.8703 | 30.2094 | 10.0736 | 7.3485 | 4.4369 | 30.5468 | 10.5439 | 7.6916 | 3.7586 | 30.7743 | 11.9889 | 8.7457 | 3.6105 | 30.9218 | 12.3005 | 8.9731 | 3.7438 | 29.1687 | 13.9205 | 10.1548 | 17.5926 | 29.1947 | 13.192 | 9.6234 | 17.3626 | 29.2353 | 12.5786 | 9.1759 | 17.193 | 29.2964 | 11.8683 | 8.6578 | 16.169 | 29.3772 | 11.2408 | 8.2 | 15.0934 | 29.4793 | 10.5585 | 7.7023 | 12.7482 | 29.6087 | 10.1238 | 7.3852 | 10.3655 | 29.7589 | 9.8484 | 7.1842 | 8.7871 | 29.9234 | 9.5742 | 6.9843 | 7.2576 | 30.11 | 9.3472 | 6.8186 | 6.1259 | 30.9132 | 8.7392 | 6.3751 | 4.0472 | 31.7448 | 8.1795 | 5.9668 | -0.29896 | 32.1441 | 8.7288 | 6.3675 | -3.7851 | 32.3414 | 8.4678 | 6.1771 | -6.2048 | 29.1629 | 14.006 | 10.2172 | 17.608 | 29.1881 | 13.947 | 10.1742 | 17.3638 | 29.2286 | 13.8664 | 10.1154 | 17.1838 | 29.2837 | 13.5881 | 9.9123 | 16.1824 | 29.3605 | 13.4559 | 9.8159 | 15.1268 | 29.4548 | 13.0592 | 9.5265 | 12.8217 | 29.5774 | 12.6586 | 9.2342 | 10.4834 | 29.7167 | 12.3919 | 9.0397 | 8.961 | 29.8931 | 12.0957 | 8.8237 | 7.3462 | 30.1903 | 11.7254 | 8.5535 | 5.4865 | 31.0532 | 10.7697 | 7.8564 | 0.62215 | 31.6088 | 9.6307 | 7.0254 | -3.2735 | 31.8392 | 8.9626 | 6.5381 | -5.5669 | 31.7989 | 8.8964 | 6.4898 | -5.0181
WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 353466 | 413290 | 30.5466 | 15.8494 | 11.3913 | 15.6348 | 30.6289 | 15.1522 | 10.8902 | 15.225 | 30.7057 | 14.9734 | 10.7617 | 14.7714 | 30.8119 | 14.5461 | 10.4546 | 14.1786 | 30.9459 | 14.146 | 10.167 | 13.6715 | 31.1048 | 13.7634 | 9.892 | 12.9797 | 31.2759 | 13.4265 | 9.6499 | 12.2863 | 31.4518 | 13.092 | 9.4095 | 11.5089 | 31.6373 | 12.7786 | 9.1842 | 10.8135 | 31.8503 | 12.3956 | 8.909 | 9.8404 | 32.7086 | 10.8606 | 7.8057 | 6.4401 | 33.3416 | 9.8761 | 7.0982 | 4.7211 | 33.7204 | 9.8212 | 7.0587 | 4.438 | 33.9684 | 9.803 | 7.0456 | 4.8405 | 30.5253 | 16.1923 | 11.6377 | 15.7395 | 30.5901 | 15.9258 | 11.4462 | 15.4331 | 30.6857 | 15.5424 | 11.1706 | 14.9725 | 30.7877 | 15.1985 | 10.9235 | 14.5147 | 30.9033 | 14.8566 | 10.6778 | 14.1533 | 31.033 | 14.5914 | 10.4871 | 13.6092 | 31.1705 | 14.3552 | 10.3174 | 13.068 | 31.3048 | 14.1029 | 10.136 | 12.4469 | 31.4469 | 13.8622 | 9.9631 | 11.8701 | 31.5945 | 13.5984 | 9.7735 | 11.2205 | 32.0039 | 12.7647 | 9.1743 | 9.2003 | 32.3541 | 12.1214 | 8.7119 | 7.5561 | 32.5998 | 11.9325 | 8.5761 | 6.5081 | 32.7438 | 11.7191 | 8.4227 | 5.7587 | 30.5467 | 16.1919 | 11.6375 | 15.6403 | 30.629 | 15.8687 | 11.4052 | 15.2463 | 30.7059 | 15.326 | 11.0151 | 14.812 | 30.8122 | 14.8349 | 10.6621 | 14.2584 | 30.9456 | 14.4231 | 10.3662 | 13.7791 | 31.1036 | 14.0019 | 10.0634 | 13.1184 | 31.2743 | 13.7817 | 9.9052 | 12.4549 | 31.4497 | 13.513 | 9.712 | 11.7079 | 31.6329 | 13.2007 | 9.4876 | 11.047 | 31.8356 | 12.9504 | 9.3077 | 10.1671 | 32.639 | 11.8732 | 8.5335 | 7.0533 | 33.2072 | 11.1101 | 7.985 | 5.5351 | 33.5519 | 10.8447 | 7.7943 | 5.3161 | 33.7696 | 10.5394 | 7.5749 | 5.7617 | 30.5445 | 15.8482 | 11.3904 | 15.6449 | 30.6334 | 15.1729 | 10.905 | 15.2154 | 30.7326 | 14.9395 | 10.7373 | 14.7444 | 30.8747 | 14.4813 | 10.408 | 14.1598 | 31.0585 | 14.047 | 10.0959 | 13.6622 | 31.2593 | 13.6231 | 9.7912 | 12.96 | 31.5054 | 13.289 | 9.551 | 12.2232 | 31.7867 | 12.9187 | 9.2849 | 11.4037 | 32.0966 | 12.5785 | 9.0404 | 10.7591 | 32.4428 | 12.2146 | 8.7788 | 10.0365 | 33.5987 | 10.2744 | 7.3844 | 7.1223 | 34.3856 | 8.0679 | 5.7986 | 3.4086 | 34.7857 | 6.8059 | 4.8916 | 1.4107 | 34.997 | 5.8332 | 4.1924 | -0.24713 | 30.5466 | 15.848 | 11.3903 | 15.6213 | 30.6558 | 15.1781 | 10.9088 | 15.1214 | 30.7659 | 15.0257 | 10.7992 | 14.6321 | 30.9091 | 14.5984 | 10.4921 | 14.0459 | 31.0645 | 14.182 | 10.1929 | 13.5667 | 31.2502 | 13.8099 | 9.9254 | 12.9332 | 31.4834 | 13.4702 | 9.6813 | 12.3002 | 31.7396 | 13.1165 | 9.4271 | 11.6293 | 32.0149 | 12.8035 | 9.2021 | 11.1154 | 32.3402 | 12.2444 | 8.8003 | 10.0572 | 33.3973 | 9.909 | 7.1218 | 5.4491 | 33.9654 | 7.7204 | 5.5488 | 2.5769 | 34.1157 | 6.9209 | 4.9742 | 1.4117 | 34.0447 | 6.7108 | 4.8232 | 1.9494
YEALAND | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351537 | 475934 | 12.6243 | 12.6243 | 12.6243 | 8.5747 | 12.6625 | 12.6625 | 12.6625 | 8.4708 | 12.7228 | 12.7228 | 12.7228 | 8.4426 | 12.7761 | 12.7761 | 12.7761 | 8.2982 | 12.8042 | 12.8042 | 12.8042 | 8.1296 | 12.8382 | 12.8382 | 12.8382 | 7.9762 | 12.8787 | 12.8787 | 12.8787 | 7.7717 | 12.9231 | 12.9231 | 12.9231 | 7.6705 | 12.9655 | 12.9655 | 12.9655 | 7.483 | 13.0137 | 13.0137 | 13.0137 | 7.3612 | 13.2192 | 13.2192 | 13.2192 | 6.7215 | 13.3772 | 13.3772 | 13.3772 | 6.4326 | 13.468 | 13.468 | 13.468 | 6.3511 | 13.5349 | 13.5349 | 13.5349 | 6.5161 | 12.6209 | 12.6209 | 12.6209 | 8.6618 | 12.6541 | 12.6541 | 12.6541 | 8.5939 | 12.7047 | 12.7047 | 12.7047 | 8.5375 | 12.7481 | 12.7481 | 12.7481 | 8.4154 | 12.7864 | 12.7864 | 12.7864 | 8.2769 | 12.814 | 12.814 | 12.814 | 8.1547 | 12.8455 | 12.8455 | 12.8455 | 7.9855 | 12.8793 | 12.8793 | 12.8793 | 7.9128 | 12.9152 | 12.9152 | 12.9152 | 7.7547 | 12.9513 | 12.9513 | 12.9513 | 7.6774 | 13.0405 | 13.0405 | 13.0405 | 7.318 | 13.1184 | 13.1184 | 13.1184 | 7.0067 | 13.1794 | 13.1794 | 13.1794 | 6.7648 | 13.2217 | 13.2217 | 13.2217 | 6.6813 | 12.6243 | 12.6243 | 12.6243 | 8.576 | 12.6626 | 12.6626 | 12.6626 | 8.4727 | 12.7229 | 12.7229 | 12.7229 | 8.4537 | 12.7762 | 12.7762 | 12.7762 | 8.3331 | 12.8043 | 12.8043 | 12.8043 | 8.1545 | 12.8381 | 12.8381 | 12.8381 | 8.0205 | 12.8785 | 12.8785 | 12.8785 | 7.8207 | 12.9228 | 12.9228 | 12.9228 | 7.703 | 12.9648 | 12.9648 | 12.9648 | 7.5206 | 13.0106 | 13.0106 | 13.0106 | 7.4119 | 13.2007 | 13.2007 | 13.2007 | 6.8651 | 13.3337 | 13.3337 | 13.3337 | 6.6249 | 13.412 | 13.412 | 13.412 | 6.5657 | 13.4623 | 13.4623 | 13.4623 | 6.7307 | 12.624 | 12.624 | 12.624 | 8.5793 | 12.6643 | 12.6643 | 12.6643 | 8.4764 | 12.7278 | 12.7278 | 12.7278 | 8.4365 | 12.787 | 12.787 | 12.787 | 8.306 | 12.8267 | 12.8267 | 12.8267 | 8.1929 | 12.8777 | 12.8777 | 12.8777 | 7.9891 | 12.9425 | 12.9425 | 12.9425 | 7.7841 | 13.0094 | 13.0094 | 13.0094 | 7.7553 | 13.0817 | 13.0817 | 13.0817 | 7.5394 | 13.1625 | 13.1625 | 13.1625 | 7.4631 | 13.4412 | 13.4412 | 13.4412 | 6.7615 | 13.6435 | 13.6435 | 13.6435 | 5.8986 | 13.7407 | 13.7407 | 13.7407 | 5.3816 | 13.7838 | 13.7838 | 13.7838 | 5.0189 | 12.6384 | 12.6384 | 12.6384 | 8.5757 | 12.7011 | 12.7011 | 12.7011 | 8.4564 | 12.7676 | 12.7676 | 12.7676 | 8.4026 | 12.7972 | 12.7972 | 12.7972 | 8.2655 | 12.8376 | 12.8376 | 12.8376 | 8.1456 | 12.8876 | 12.8876 | 12.8876 | 7.9616 | 12.9496 | 12.9496 | 12.9496 | 7.7736 | 13.0126 | 13.0126 | 13.0126 | 7.7707 | 13.0775 | 13.0775 | 13.0775 | 7.5818 | 13.1522 | 13.1522 | 13.1522 | 7.3809 | 13.4054 | 13.4054 | 13.4054 | 6.3143 | 13.5468 | 13.5468 | 13.5468 | 5.6225 | 13.5791 | 13.5791 | 13.5791 | 5.3211 | 13.5589 | 13.5589 | 13.5589 | 5.4643

## Gen BSP Headroom
Click the scenario name to move directly to the associated results | Best View
Steady Progression
System Transformation
Consumer Transformation
Leading the Way
|  |  |  | Central Outlook | [41 empty] | Steady Progression | [41 empty] | Steady Transformation | [41 empty] | Consumer Transformation | [41 empty] | Leading the Way
BSP Headroom |  |  |  | 2022 |  |  | 2023 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2036 |  |  | 2041 |  |  | 2046 |  |  | 2051 |  |  | 2022 |  |  | 2023 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2036 |  |  | 2041 |  |  | 2046 |  |  | 2051 |  |  | 2022 |  |  | 2023 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2036 |  |  | 2041 |  |  | 2046 |  |  | 2051 |  |  | 2022 |  |  | 2023 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2036 |  |  | 2041 |  |  | 2046 |  |  | 2051 |  |  | 2022 |  |  | 2023 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2036 |  |  | 2041 |  |  | 2046 |  |  | 2051
BSP | GSP Group | BSP Coordinates |  | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW)
| GSP Group | Easting | Northing | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.)
ADSWOOD | BREDBURY | 389188 | 388310 | 136.9441 | 54.901 | 72.6641 | 137.2249 | 54.0787 | 63.5345 | 137.3611 | 53.4353 | 62.8965 | 137.6521 | 52.6404 | 62.0559 | 138.0489 | 52.0564 | 60.8721 | 138.5408 | 50.9697 | 59.5098 | 138.9732 | 50.0693 | 57.8999 | 139.4436 | 49.6423 | 56.3439 | 139.9538 | 49.2193 | 54.7654 | 140.5095 | 48.6125 | 52.9981 | 142.9569 | 46.0165 | 46.6677 | 145.0881 | 44.7065 | 43.4915 | 146.478 | 44.0997 | 42.8542 | 147.4112 | 43.4498 | 43.5513 | 136.7773 | 55.1446 | 77.4247 | 136.9332 | 54.1719 | 72.8911 | 137.2187 | 53.6246 | 71.9733 | 137.5974 | 53.0591 | 71.0448 | 138.0306 | 52.694 | 69.9491 | 138.4641 | 52.196 | 68.686 | 138.8931 | 51.6085 | 67.1692 | 139.3547 | 51.2545 | 65.6804 | 139.852 | 50.8453 | 64.1227 | 140.3757 | 50.35 | 62.5389 | 141.8687 | 49.2879 | 57.8896 | 143.1442 | 48.6049 | 54.7517 | 143.9846 | 48.1389 | 53.0036 | 144.5272 | 48.3532 | 51.9783 | 136.9545 | 55.126 | 72.7176 | 137.239 | 54.5519 | 63.6662 | 137.3777 | 53.8819 | 63.084 | 137.6702 | 53.1713 | 62.2124 | 138.0655 | 52.65 | 61.0836 | 138.5449 | 52.0272 | 59.7851 | 138.9709 | 51.3065 | 58.2399 | 139.4333 | 50.9278 | 56.7464 | 139.9289 | 50.5488 | 55.2585 | 140.4428 | 50.078 | 53.6802 | 142.6958 | 48.3782 | 47.8935 | 144.4129 | 47.3538 | 45.3114 | 145.479 | 47.0934 | 44.9819 | 146.1195 | 46.4744 | 45.8367 | 136.9372 | 54.9087 | 72.7183 | 137.2178 | 54.0776 | 63.6608 | 137.3977 | 53.3998 | 63.129 | 137.7805 | 52.5917 | 62.4041 | 138.2555 | 51.971 | 61.4121 | 138.7619 | 50.9536 | 60.2554 | 139.3748 | 50.2492 | 58.8369 | 140.0774 | 49.8553 | 57.4934 | 140.8502 | 49.4079 | 56.3155 | 141.715 | 48.8449 | 55.1311 | 145.5731 | 45.5688 | 46.8948 | 150.5183 | 40.9852 | 29.4004 | 152.8699 | 37.4702 | 15.9343 | 153.6818 | 34.9899 | 7.2143 | 136.9172 | 54.9183 | 72.7368 | 137.232 | 54.1909 | 63.5852 | 137.4324 | 53.5298 | 63.0855 | 137.7996 | 52.6842 | 62.4816 | 138.1599 | 52.2984 | 61.6516 | 138.6329 | 51.7412 | 60.7417 | 139.2345 | 51.0482 | 59.5453 | 139.9191 | 50.5612 | 58.4652 | 140.7686 | 49.8816 | 57.0215 | 142.1176 | 48.8041 | 52.8503 | 147.0254 | 43.9256 | 33.2455 | 150.3572 | 39.0102 | 17.6208 | 151.4143 | 36.2161 | 8.9215 | 151.2021 | 35.5643 | 12.0522
AGECROFT | KEARSLEY | 380345 | 401831 | 92.1847 | 39.6643 | 30.7305 | 92.5571 | 33.846 | 29.9301 | 93.1602 | 28.3397 | 29.1479 | 93.6765 | 22.6855 | 27.9861 | 94.0714 | 17.336 | 26.3636 | 85.1616 | 15.4497 | 24.6759 | 81.5434 | 14.7933 | 22.7172 | 77.7959 | 14.1134 | 20.7664 | 73.7994 | 13.3884 | 18.7005 | 69.2311 | 12.5596 | 16.4524 | 62.337 | 11.3089 | 7.9827 | 98.2398 | 17.8223 | 2.9709 | 104.5419 | 29.9346 | 0.94311 | 106.1041 | 31.9779 | 0.48973 | 92.2585 | 39.262 | 30.876 | 92.6723 | 33.0327 | 30.2027 | 93.0068 | 27.0213 | 29.2264 | 93.467 | 20.9649 | 28.049 | 83.9898 | 15.2371 | 26.5641 | 74.7277 | 13.5568 | 24.9752 | 72.2572 | 13.1086 | 23.2073 | 69.6936 | 12.6435 | 21.369 | 66.9466 | 12.1452 | 19.4417 | 64.0642 | 11.6223 | 17.3492 | 59.7203 | 10.8342 | 11.0165 | 86.1122 | 15.6221 | 6.0801 | 101.7964 | 24.3476 | 2.817 | 102.8596 | 26.2258 | 0.49254 | 92.1872 | 39.249 | 30.7603 | 92.5611 | 32.941 | 29.9805 | 93.1658 | 26.7916 | 29.343 | 93.6839 | 20.5953 | 28.1653 | 81.1699 | 14.7255 | 26.6767 | 71.3524 | 12.9445 | 25.0326 | 69.0998 | 12.5358 | 23.1954 | 66.7796 | 12.1149 | 21.3296 | 64.2294 | 11.6522 | 19.3804 | 61.4857 | 11.1545 | 17.3609 | 59.229 | 10.7451 | 9.7805 | 101.7532 | 18.5224 | 5.626 | 103.4206 | 32.4221 | 3.9783 | 104.5062 | 34.9802 | 3.6127 | 92.1717 | 39.6677 | 30.7691 | 92.5208 | 33.8453 | 30.0193 | 93.095 | 28.3028 | 29.3028 | 93.7165 | 22.6501 | 28.1631 | 94.2081 | 17.2986 | 26.6609 | 84.881 | 15.3988 | 25.0622 | 80.961 | 14.6876 | 23.215 | 76.9007 | 13.951 | 21.3003 | 72.6947 | 13.188 | 19.5092 | 69.6551 | 12.6365 | 17.7861 | 58.9368 | 10.6921 | 7.1435 | 77.2231 | 14.0095 | -12.0705 | 110.3507 | 22.9336 | -26.5064 | 111.5903 | 23.0642 | -36.3428 | 92.2145 | 39.6848 | 30.8631 | 92.7256 | 35.5527 | 30.0133 | 93.3445 | 31.4565 | 29.3088 | 93.6599 | 27.0356 | 28.3079 | 94.1232 | 22.8639 | 26.9194 | 94.8431 | 22.397 | 25.4272 | 95.6235 | 21.8371 | 23.734 | 96.5057 | 21.5855 | 22.1007 | 97.506 | 21.3587 | 20.2329 | 98.7339 | 20.698 | 15.668 | 103.5957 | 32.3357 | -6.3256 | 107.1965 | 27.0432 | -23.6959 | 108.5745 | 24.108 | -33.3098 | 108.4138 | 23.3907 | -30.9981
ALTRINCHAM | CARRINGTON | 376380 | 389012 | 150.2907 | 48.2837 | 78.0792 | 150.6441 | 47.6955 | 76.7094 | 150.8003 | 47.1501 | 75.5046 | 151.0915 | 46.5344 | 74.1038 | 151.4736 | 46.0146 | 72.4189 | 151.9388 | 45.4359 | 70.5458 | 152.4006 | 44.8757 | 68.5648 | 152.8949 | 44.3831 | 66.5226 | 153.4187 | 43.7631 | 64.4656 | 153.9919 | 43.1516 | 62.1865 | 156.3426 | 40.8749 | 54.6853 | 158.2914 | 39.3977 | 51.2332 | 159.6 | 39.6975 | 50.7605 | 160.6008 | 39.968 | 51.7863 | 150.0618 | 48.3626 | 78.5794 | 150.2367 | 47.8568 | 77.6176 | 150.5387 | 47.2693 | 76.23 | 150.9117 | 46.7263 | 74.9587 | 151.3275 | 46.3517 | 73.4751 | 151.7933 | 45.9286 | 71.7981 | 152.2668 | 45.5234 | 69.9807 | 152.7697 | 45.1989 | 68.0801 | 153.3061 | 44.7168 | 65.9129 | 153.8688 | 44.3023 | 63.662 | 155.0518 | 43.34 | 58.36 | 156.0744 | 42.6547 | 54.6466 | 156.8695 | 42.8566 | 52.4929 | 157.4269 | 43.1096 | 51.3102 | 150.2909 | 48.3561 | 78.1246 | 150.6446 | 47.8241 | 76.8133 | 150.8014 | 47.1582 | 75.6451 | 151.0932 | 46.549 | 74.3021 | 151.4742 | 46.0973 | 72.6923 | 151.9379 | 45.6077 | 70.8966 | 152.3983 | 45.158 | 68.9894 | 152.8919 | 44.7652 | 67.0175 | 153.4093 | 44.2168 | 65.0661 | 153.954 | 43.733 | 63.0202 | 156.1219 | 42.2255 | 56.2912 | 157.7689 | 41.3214 | 53.4026 | 158.9205 | 42.1708 | 53.106 | 159.7117 | 42.5221 | 54.1908 | 150.2711 | 48.2946 | 78.1418 | 150.6287 | 47.7233 | 76.8613 | 150.8387 | 47.1722 | 75.8264 | 151.2294 | 46.5776 | 74.6 | 151.7285 | 46.0927 | 73.1637 | 152.3318 | 45.5597 | 71.5708 | 153.0404 | 45.0124 | 69.8594 | 153.8418 | 44.5176 | 68.1332 | 154.7143 | 43.9904 | 66.6249 | 155.6759 | 43.4968 | 65.137 | 159.3663 | 40.6667 | 55.9514 | 162.4826 | 36.5302 | 37.7008 | 164.1563 | 34.2798 | 23.7421 | 164.9646 | 32.5551 | 14.4575 | 150.2877 | 48.2643 | 77.9221 | 150.716 | 47.7731 | 76.2628 | 150.9322 | 47.2899 | 75.2538 | 151.2771 | 46.7366 | 74.286 | 151.6947 | 46.2689 | 73.1022 | 152.2377 | 45.75 | 71.8426 | 152.9017 | 45.1168 | 70.434 | 153.6346 | 44.5864 | 69.0714 | 154.4896 | 43.9398 | 67.4081 | 155.7165 | 42.8579 | 62.9162 | 159.3449 | 38.3826 | 41.9371 | 161.5535 | 33.8337 | 25.4771 | 162.2527 | 32.1785 | 16.3553 | 161.8438 | 31.8991 | 19.8828
ATHERTON | KEARSLEY | 366150 | 402088 | 151.1034 | 34.1696 | 46.0128 | 151.5653 | 32.3473 | 44.4247 | 151.768 | 30.8282 | 37.0664 | 152.1896 | 28.8723 | 28.7937 | 150.1363 | 27.2371 | 25.5488 | 139.2109 | 25.2551 | 21.1956 | 133.1019 | 24.1468 | 16.5388 | 127.4569 | 23.1227 | 12.2843 | 121.2153 | 21.9904 | 7.8708 | 114.9088 | 20.8463 | 3.1781 | 91.4311 | 16.5871 | -11.2364 | 76.8707 | 13.9456 | -19.0284 | 88.0758 | 15.9783 | -20.4988 | 82.5068 | 14.968 | -19.3221 | 150.737 | 34.3997 | 46.4753 | 150.9176 | 33.1012 | 45.2705 | 151.3017 | 31.9766 | 43.2593 | 151.7807 | 30.6023 | 41.1971 | 152.3318 | 29.5408 | 38.7717 | 152.9501 | 28.1933 | 35.875 | 151.299 | 27.4481 | 32.6963 | 147.3704 | 26.7353 | 29.514 | 142.845 | 25.9144 | 26.2237 | 137.9562 | 25.0275 | 22.6817 | 125.9027 | 22.8407 | 12.8635 | 117.495 | 21.3155 | 5.9068 | 123.3932 | 22.3855 | 1.9113 | 132.6281 | 24.0609 | -0.50468 | 151.1064 | 34.3899 | 46.0905 | 151.5697 | 32.4856 | 44.6011 | 151.7748 | 30.5884 | 37.3448 | 152.1991 | 28.4716 | 29.1587 | 146.7274 | 26.6187 | 26.0333 | 135.3147 | 24.5482 | 21.8039 | 130.2435 | 23.6283 | 17.2694 | 125.3486 | 22.7402 | 13.0093 | 119.7147 | 21.7182 | 8.7016 | 113.6223 | 20.6129 | 4.3977 | 94.1584 | 17.0818 | -8.5184 | 80.4503 | 14.595 | -14.9761 | 91.4674 | 16.5936 | -15.9446 | 85.9421 | 15.5913 | -14.4104 | 151.0745 | 34.1715 | 46.0379 | 151.5316 | 32.3499 | 44.4815 | 151.8062 | 30.7152 | 37.2098 | 152.3781 | 28.7449 | 29.064 | 149.1972 | 27.0668 | 26.1046 | 137.8683 | 25.0115 | 22.0585 | 131.2537 | 23.8115 | 17.6306 | 124.9756 | 22.6726 | 13.6454 | 118.4913 | 21.4962 | 10.0413 | 111.9138 | 20.3029 | 6.7005 | 79.4329 | 14.4104 | -10.7535 | 37.1783 | 6.7447 | -45.733 | 22.7659 | 4.1301 | -71.9279 | 1.6775 | 0.30432 | -89.2869 | 151.039 | 34.1988 | 46.1264 | 151.5498 | 33.039 | 44.3827 | 151.8858 | 32.0563 | 37.0692 | 152.4666 | 30.5953 | 29.1287 | 153.3181 | 29.3234 | 26.379 | 152.3493 | 27.6386 | 22.7167 | 145.5999 | 26.4141 | 18.6924 | 139.5257 | 25.3122 | 15.2158 | 132.1953 | 23.9823 | 11.1308 | 120.0194 | 21.7734 | 2.2302 | 79.1627 | 14.3614 | -37.2714 | 36.1458 | 6.5574 | -67.8401 | 15.6604 | 2.841 | -84.768 | 9.0993 | 1.6508 | -79.5335
BARROW & SANDGATE | HARKER / HUTTON | 319709 | 470489 | 167.5236 | 30.641 | 93.5475 | 166.1714 | 30.171 | 88.358 | 164.1346 | 29.7766 | 84.1075 | 159.8793 | 29.0047 | 80.9383 | 155.8796 | 28.279 | 80.0379 | 132.666 | 24.0677 | 79.1959 | 111.0806 | 20.1518 | 78.2255 | 90.1414 | 16.3531 | 77.1703 | 68.9801 | 12.5141 | 68.9801 | 47.3321 | 8.5868 | 47.3321 | 30.4338 | 5.5212 | 30.4338 | 17.0465 | 3.0925 | 17.0465 | 13.646 | 2.4756 | 13.646 | 6.3202 | 1.1466 | 6.3202 | 168.2471 | 30.9536 | 95.9951 | 168.132 | 30.9346 | 93.6738 | 167.5689 | 30.7013 | 90.8146 | 166.5053 | 30.2636 | 88.4828 | 164.9475 | 29.9241 | 87.3862 | 161.6348 | 29.3231 | 86.1587 | 158.7971 | 28.8083 | 84.714 | 156.57 | 28.4043 | 83.1181 | 154.2195 | 27.9779 | 80.8509 | 151.4635 | 27.4779 | 78.3838 | 143.1426 | 25.9684 | 76.5047 | 137.1614 | 24.8833 | 75.5519 | 136.6359 | 24.7879 | 75.4136 | 137.5343 | 24.9509 | 76.04 | 168.2276 | 30.9448 | 93.6584 | 167.4332 | 30.6889 | 88.5582 | 166.0924 | 30.1664 | 84.3988 | 161.6052 | 29.3178 | 81.3148 | 157.394 | 28.5538 | 80.4962 | 130.9427 | 23.7551 | 79.743 | 106.0046 | 19.2309 | 78.867 | 81.6877 | 14.8194 | 77.9093 | 57.4318 | 10.419 | 57.4318 | 32.8891 | 5.9666 | 32.8891 | 18.3217 | 3.3238 | 18.3217 | 6.6998 | 1.2154 | 6.6998 | 1.6408 | 0.29767 | 1.6408 | 10.6707 | 1.9358 | 10.6707 | 167.5471 | 30.6509 | 93.6322 | 165.9262 | 30.1017 | 88.5309 | 163.2965 | 29.6246 | 84.3733 | 159.0301 | 28.8506 | 81.3054 | 155.0444 | 28.1275 | 80.5197 | 131.7847 | 23.9078 | 79.6819 | 110.1615 | 19.985 | 78.824 | 89.058 | 16.1565 | 77.9822 | 67.8852 | 12.3155 | 67.8852 | 46.247 | 8.3899 | 46.247 | 16.108 | 2.9222 | 16.108 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 167.6109 | 30.6792 | 93.7246 | 166.3843 | 30.2361 | 88.6368 | 164.0218 | 29.7562 | 84.5543 | 159.3955 | 28.9169 | 81.6434 | 154.5571 | 28.0391 | 80.4687 | 131.0219 | 23.7695 | 79.984 | 102.9628 | 18.6791 | 70.859 | 82.276 | 14.9262 | 70.7889 | 61.012 | 11.0686 | 61.012 | 36.7978 | 6.6757 | 36.7978 | 8.9999 | 1.6327 | 8.9999 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707
BARTON | CARRINGTON | 376758 | 397174 | 10.6707 | 1.9358 | 10.6707 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 7.0624 | 1.9358 | 7.0624 | 10.6707 | 1.9358 | 10.6707 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 10.6707 | 1.9358 | 10.6707 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 4.4757 | 1.8384 | 4.4757 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -3.1874 | 6.7308 | 1.9358 | -13.9747 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 4.2334 | 1.7388 | 4.2334 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 2.3412 | 6.7308 | 1.9358 | 4.7305
BELFIELD | ROCHDALE | 391033 | 413945 | 103.2084 | 32.7689 | 74.0059 | 103.4538 | 30.702 | 72.6442 | 103.7042 | 28.7842 | 72.1141 | 104.0518 | 27.0818 | 71.4266 | 104.4913 | 25.3864 | 70.4569 | 105.0019 | 24.4779 | 69.3192 | 105.5753 | 24.0253 | 68.1361 | 106.1883 | 23.6553 | 66.9331 | 106.8328 | 23.2703 | 65.7481 | 107.5408 | 22.8215 | 64.5058 | 110.2674 | 21.1093 | 60.6654 | 112.2688 | 21.6838 | 58.0417 | 113.4133 | 24.4629 | 56.9506 | 114.3245 | 24.748 | 56.7964 | 103.1425 | 33.019 | 75.0403 | 103.3307 | 31.2359 | 74.5324 | 103.6384 | 29.4808 | 73.5903 | 103.976 | 27.9439 | 72.6191 | 104.3615 | 26.4847 | 71.4966 | 104.7967 | 25.8648 | 70.2901 | 105.2821 | 25.5384 | 68.9946 | 105.7982 | 25.3081 | 67.6416 | 106.3417 | 25.0083 | 66.2415 | 106.9017 | 24.6928 | 64.818 | 108.6057 | 23.994 | 61.4706 | 109.9203 | 24.4855 | 59.2152 | 110.9282 | 26.4912 | 57.9422 | 111.7062 | 27.1157 | 56.9581 | 103.2087 | 33.0163 | 74.0354 | 103.4547 | 31.1452 | 72.7045 | 103.7059 | 29.3248 | 72.2062 | 104.0547 | 27.7891 | 71.5502 | 104.4934 | 26.2772 | 70.6186 | 105.0018 | 25.5261 | 69.5237 | 105.5735 | 25.1441 | 68.3841 | 106.1857 | 24.8504 | 67.2247 | 106.8219 | 24.4714 | 66.1001 | 107.4923 | 24.0717 | 64.9745 | 109.9798 | 23.0092 | 61.4515 | 111.5633 | 23.8974 | 59.3883 | 112.5194 | 27.3429 | 58.4983 | 113.1278 | 27.6007 | 58.5561 | 103.203 | 32.7735 | 74.1088 | 103.4439 | 30.8887 | 72.8806 | 103.6909 | 28.9387 | 72.5225 | 104.0418 | 27.2333 | 72.0402 | 104.4838 | 25.5014 | 71.3324 | 105.0178 | 24.6128 | 70.5217 | 105.641 | 24.1157 | 69.7046 | 106.3253 | 23.7334 | 68.915 | 107.0526 | 23.3384 | 68.2228 | 107.8463 | 22.9032 | 67.4814 | 111.4986 | 20.5625 | 60.8916 | 102.0013 | 18.5047 | 47.421 | 105.2195 | 19.0885 | 37.1209 | 97.9645 | 17.7723 | 30.5171 | 103.1995 | 33.8489 | 74.1273 | 103.48 | 33.4185 | 72.8248 | 103.74 | 32.943 | 72.4598 | 104.0608 | 32.5262 | 72.07 | 104.4699 | 32.1048 | 71.4736 | 104.9586 | 31.4373 | 70.8185 | 105.5606 | 30.8792 | 70.133 | 106.2128 | 30.4426 | 69.5056 | 106.9642 | 29.9505 | 68.9046 | 108.1204 | 29.0537 | 65.6847 | 113.0016 | 25.0242 | 50.5002 | 115.0241 | 20.8672 | 38.3684 | 104.1009 | 18.8856 | 31.6619 | 101.3259 | 18.3821 | 33.862
BISPHAM | PENWORTHAM WEST / STANAH | 332328 | 439711 | 75.0084 | 19.6193 | 61.4398 | 47.0675 | 8.5388 | 47.0675 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 48.7248 | 8.8395 | 20.5651 | 71.8792 | 13.04 | 22.1483 | 74.9974 | 18.8646 | 62.0918 | 40.6526 | 7.375 | 40.6526 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 55.3394 | 10.0395 | 29.0329 | 75.0099 | 18.8568 | 61.5042 | 41.2433 | 7.4822 | 41.2433 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 94.1379 | 17.1081 | 24.0081 | 95.3035 | 20.3908 | 25.7775 | 74.9996 | 19.6284 | 61.5087 | 47.2813 | 8.5776 | 47.2813 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -1.9 | 10.6707 | 1.9358 | -22.0574 | 5.1038 | 0.9259 | -35.506 | 74.9677 | 19.656 | 61.5516 | 71.7981 | 13.0253 | 59.9 | 34.7218 | 6.2991 | 34.7218 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 57.2423 | 10.3847 | 5.0268 | 21.6968 | 3.9361 | -18.5858 | 12.52 | 2.2713 | -31.7585 | 9.4249 | 1.7098 | -27.1617
BLACKBURN | PENWORTHAM EAST / ROCHDALE | 370584 | 429294 | 62.5117 | 61.3564 | 62.5117 | 62.8985 | 52.5114 | 62.8985 | 63.0123 | 42.8819 | 60.1379 | 63.2668 | 33.2475 | 57.3818 | 63.6346 | 23.9097 | 56.4829 | 64.0813 | 14.3433 | 55.4332 | 64.5522 | 12.6838 | 54.239 | 65.0632 | 12.0876 | 53.1308 | 62.8415 | 11.4004 | 52.0202 | 58.7895 | 10.6654 | 50.5513 | 47.4098 | 8.6009 | 45.4066 | 60.7481 | 11.0207 | 42.8047 | 72.1955 | 39.4806 | 42.2436 | 73.1635 | 37.8882 | 42.227 | 62.1993 | 61.6009 | 62.1993 | 62.3435 | 52.7311 | 62.3435 | 62.6527 | 43.9346 | 62.6527 | 63.0312 | 35.1482 | 63.0312 | 63.4232 | 26.6859 | 63.3336 | 63.8504 | 18.1991 | 62.293 | 64.3322 | 17.718 | 61.0755 | 64.8523 | 17.294 | 59.8248 | 65.414 | 16.7914 | 58.4 | 65.9322 | 16.2764 | 56.9365 | 67.329 | 14.9398 | 53.3305 | 68.6113 | 15.7813 | 50.8655 | 69.4826 | 31.8097 | 49.5378 | 69.9864 | 46.0147 | 48.9573 | 62.5207 | 61.5853 | 62.5207 | 62.9109 | 52.0156 | 62.9109 | 63.0273 | 42.3365 | 60.2678 | 63.2835 | 32.673 | 57.558 | 63.6507 | 23.344 | 56.7161 | 64.0896 | 13.9904 | 55.7252 | 64.5522 | 13.2767 | 54.5911 | 65.0523 | 12.6188 | 53.5419 | 65.3021 | 11.8468 | 52.507 | 60.9786 | 11.0625 | 51.2601 | 50.0218 | 9.0748 | 46.6541 | 65.4891 | 11.8808 | 44.5522 | 71.0654 | 42.4558 | 44.1938 | 71.6416 | 41.6616 | 44.5315 | 62.4972 | 61.3549 | 62.4972 | 62.8789 | 52.471 | 62.8789 | 63.0306 | 42.6825 | 60.2594 | 63.3632 | 32.9275 | 57.5213 | 63.8013 | 23.4723 | 56.6274 | 64.3755 | 13.832 | 55.553 | 65.0806 | 12.0391 | 54.2785 | 62.161 | 11.277 | 53.0543 | 57.5235 | 10.4357 | 51.8912 | 52.5922 | 9.5411 | 50.7082 | 33.2148 | 6.0257 | 33.2148 | 31.819 | 5.7725 | 27.945 | 77.3615 | 31.6706 | 15.5894 | 78.2889 | 29.5406 | 7.5763 | 62.4839 | 61.3625 | 62.4839 | 62.8953 | 60.5739 | 62.8953 | 63.0639 | 58.6417 | 60.2072 | 63.3853 | 56.4681 | 57.5455 | 63.7984 | 54.4299 | 56.7504 | 64.3656 | 51.9193 | 55.82 | 65.1014 | 50.025 | 54.6718 | 65.8486 | 49.1449 | 53.6119 | 66.7244 | 48.073 | 52.3054 | 67.8605 | 46.5937 | 48.9591 | 71.6312 | 41.3707 | 30.8697 | 74.5079 | 35.6303 | 16.5438 | 75.816 | 31.9136 | 8.5463 | 75.7426 | 30.3 | 11.7881
BLACKPOOL | PENWORTHAM WEST / STANAH | 330835 | 435308 | 143.4149 | 41.509 | 56.0499 | 143.7956 | 40.9538 | 54.6122 | 144.0515 | 40.5572 | 53.5537 | 144.5427 | 39.9702 | 52.2952 | 145.0025 | 39.3772 | 50.6411 | 145.4356 | 38.7211 | 48.817 | 145.9284 | 38.025 | 46.883 | 146.4674 | 37.3225 | 44.8106 | 147.054 | 36.5667 | 42.6957 | 147.7149 | 35.723 | 40.2537 | 150.5502 | 32.7522 | 31.968 | 153.1073 | 32.2538 | 27.7967 | 154.7343 | 34.9566 | 26.9746 | 155.7628 | 35.6477 | 28.2883 | 143.2908 | 41.7472 | 56.7308 | 143.5994 | 41.4504 | 55.8368 | 144.1362 | 41.0169 | 54.3441 | 144.5428 | 40.4376 | 52.9688 | 144.983 | 39.907 | 51.3021 | 145.492 | 39.3034 | 49.44 | 146.0731 | 38.642 | 47.0243 | 146.7108 | 37.9248 | 43.0424 | 147.4085 | 37.1386 | 38.6178 | 148.1575 | 36.1803 | 33.7262 | 149.6994 | 35.3719 | 31.035 | 151.1228 | 35.6198 | 29.4196 | 152.0245 | 37.2656 | 28.9397 | 152.5037 | 37.2593 | 28.3284 | 143.4307 | 41.7431 | 56.0993 | 143.8167 | 41.4601 | 54.7294 | 144.0762 | 40.8558 | 53.7475 | 144.5693 | 39.9904 | 52.5657 | 145.014 | 39.0952 | 51.0018 | 145.4416 | 38.1152 | 49.2759 | 145.9262 | 37.2173 | 47.4412 | 146.4546 | 36.3313 | 45.4705 | 147.0223 | 35.3861 | 43.4961 | 147.6393 | 34.2645 | 41.3308 | 150.2109 | 32.0927 | 33.8128 | 152.2038 | 33.2489 | 30.37 | 153.3877 | 35.8561 | 29.9325 | 154.0078 | 37.2704 | 31.4198 | 143.414 | 41.5179 | 56.1054 | 143.8122 | 40.9603 | 54.7301 | 144.1624 | 41.2625 | 53.7829 | 144.7157 | 40.5099 | 52.6503 | 145.1374 | 39.802 | 51.1212 | 145.7541 | 38.9786 | 49.3933 | 146.5232 | 38.2136 | 47.4372 | 147.4089 | 37.4764 | 45.3557 | 148.3873 | 36.7142 | 43.4908 | 149.4771 | 35.924 | 41.6057 | 154.1243 | 31.6688 | 29.6687 | 155.529 | 28.2154 | 5.0637 | 147.3407 | 26.73 | -15.0222 | 138.3721 | 25.1029 | -28.997 | 143.3944 | 41.5275 | 56.0608 | 143.863 | 40.9615 | 54.5071 | 144.2201 | 40.6776 | 53.659 | 144.6075 | 40.0844 | 52.8072 | 144.9891 | 39.4159 | 51.4807 | 145.5607 | 38.572 | 50.073 | 146.3062 | 37.7604 | 48.4719 | 147.1579 | 37.037 | 46.8123 | 148.1789 | 36.2423 | 44.7712 | 149.6997 | 34.8029 | 38.8471 | 153.8798 | 32.3931 | 11.0939 | 142.4566 | 25.8439 | -13.5232 | 128.8104 | 23.3683 | -27.5753 | 126.5988 | 22.967 | -22.3548
BLOOM ST | SOUTH MANCHESTER | 384221 | 397717 | 158.3263 | 43.6957 | 53.4185 | 158.9352 | 42.8799 | 50.0727 | 150.2944 | 42.6151 | 60.6252 | 150.5552 | 42.2595 | 66.064 | 150.8804 | 41.6165 | 65.4947 | 151.2763 | 41.0794 | 64.6811 | 151.6799 | 40.5783 | 63.919 | 152.0864 | 40.1976 | 63.2111 | 152.4914 | 39.7811 | 62.5489 | 152.9117 | 39.3422 | 61.8521 | 153.9945 | 37.3183 | 59.4206 | 154.5781 | 36.0816 | 58.1227 | 154.797 | 38.5503 | 57.7716 | 154.7874 | 39.8585 | 58.2161 | 157.6552 | 44.266 | 56.3019 | 157.7153 | 43.8889 | 55.4577 | 150.2875 | 43.5794 | 64.5323 | 150.8138 | 43.2525 | 69.623 | 151.3998 | 42.8635 | 68.7188 | 152.0556 | 42.4492 | 67.7454 | 152.7738 | 42.0587 | 66.735 | 153.5516 | 41.773 | 65.7185 | 154.3832 | 41.4545 | 64.6604 | 154.8126 | 41.1059 | 63.5767 | 155.515 | 40.3253 | 61.3162 | 155.9912 | 39.7808 | 59.7338 | 156.1843 | 41.5225 | 59.0362 | 156.1326 | 43.3795 | 59.1421 | 158.3263 | 44.2629 | 53.4463 | 158.9352 | 43.9 | 50.1494 | 150.2944 | 43.5249 | 60.9035 | 150.5552 | 43.0947 | 65.9984 | 150.8794 | 42.6747 | 65.4662 | 151.2737 | 42.2443 | 64.6883 | 151.6761 | 41.7897 | 63.9615 | 152.082 | 41.4299 | 63.2893 | 152.4833 | 41.0204 | 62.669 | 152.8888 | 40.5714 | 62.035 | 153.9149 | 39.2308 | 59.7289 | 154.4636 | 38.4719 | 58.5221 | 154.673 | 41.0132 | 58.2146 | 154.6684 | 42.7858 | 58.6638 | 158.2685 | 43.7245 | 53.5723 | 158.8206 | 42.9285 | 50.3762 | 150.2147 | 42.6556 | 61.0571 | 150.4531 | 42.342 | 66.5021 | 150.7586 | 41.7799 | 65.9965 | 151.1348 | 41.2595 | 65.228 | 151.5179 | 40.787 | 64.4799 | 151.9019 | 40.4379 | 63.7734 | 152.2796 | 40.0532 | 63.1452 | 152.653 | 39.648 | 62.5544 | 153.6513 | 37.5449 | 60.0301 | 154.903 | 35.1796 | 55.1292 | 155.6204 | 36.9781 | 51.6851 | 155.3406 | 37.448 | 49.6804 | 158.2669 | 43.7335 | 53.609 | 158.8104 | 43.0325 | 50.4428 | 150.063 | 42.7733 | 61.1848 | 150.201 | 42.443 | 66.6395 | 150.3998 | 41.8546 | 66.1938 | 150.6535 | 41.321 | 65.5072 | 150.9154 | 40.7543 | 64.8496 | 151.1633 | 40.3247 | 64.2491 | 151.3973 | 39.8654 | 63.7227 | 151.8069 | 39.1206 | 62.3191 | 153.3912 | 36.812 | 56.16 | 154.4734 | 34.4199 | 51.6511 | 154.7888 | 36.2004 | 49.4441 | 154.2158 | 35.9143 | 51.3503
BOLTON | KEARSLEY | 372255 | 410566 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 4.8232 | 10.6707 | 1.9358 | -2.9873 | 10.6707 | 1.9358 | -4.2801 | 10.6707 | 1.9358 | -2.4237 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 5.6772 | 10.6707 | 1.9358 | 1.6643 | 10.6707 | 1.9358 | -0.33931 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.1599 | 10.6707 | 1.9358 | 1.6662 | 10.6707 | 1.9358 | 1.0209 | 10.6707 | 1.9358 | 3.4258 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 1.7348 | 2.9602 | 1.2159 | -39.5939 | -6.7399 | -2.7684 | -70.9501 | -19.4031 | -7.9697 | -91.0737 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -32.126 | 1.3554 | 0.55671 | -69.0474 | -13.2751 | -5.4526 | -89.2121 | -14.3421 | -5.8909 | -81.2031
BURNLEY | ROCHDALE | 385569 | 434469 | 93.8796 | 48.4974 | 86.5096 | 94.2164 | 40.2059 | 84.9078 | 94.3315 | 32.0926 | 83.9425 | 94.5622 | 24.0745 | 83.0678 | 89.0674 | 16.1583 | 81.9325 | 45.5051 | 8.2554 | 45.5051 | 42.8109 | 7.7666 | 42.8109 | 41.4033 | 7.5112 | 41.4033 | 39.2269 | 7.1164 | 39.2269 | 36.9695 | 6.7069 | 36.9695 | 38.7077 | 7.0222 | 38.7077 | 94.9751 | 17.23 | 65.7716 | 102.7625 | 52.669 | 65.1657 | 103.5482 | 55.594 | 65.8496 | 93.65 | 48.68 | 87.2858 | 93.8078 | 42.0233 | 86.3825 | 94.0984 | 35.3524 | 85.2581 | 94.4499 | 28.8135 | 84.2972 | 94.8232 | 22.2611 | 83.1696 | 86.7904 | 15.7452 | 81.8974 | 84.9205 | 15.4059 | 80.5063 | 83.4967 | 15.1476 | 79.0421 | 81.8225 | 14.8439 | 77.5223 | 79.9512 | 14.5044 | 75.9604 | 81.7925 | 14.8385 | 71.8301 | 99.9282 | 20.9244 | 68.9406 | 100.6493 | 44.4453 | 67.4113 | 101.04 | 60.1043 | 66.6212 | 93.8888 | 48.6735 | 86.5405 | 94.2272 | 41.4789 | 84.9991 | 94.3441 | 34.2238 | 84.057 | 94.5757 | 27.1328 | 83.2255 | 94.8872 | 20.0341 | 82.1429 | 71.8696 | 13.0383 | 71.8696 | 69.8832 | 12.6779 | 69.8832 | 68.2252 | 12.3771 | 68.2252 | 66.2429 | 12.0175 | 66.2429 | 63.7714 | 11.5691 | 63.7714 | 69.1427 | 12.5436 | 69.1427 | 100.866 | 24.2076 | 67.3429 | 101.8051 | 64.3176 | 66.9659 | 102.3384 | 67.7909 | 67.7019 | 93.868 | 48.5025 | 86.5377 | 94.1947 | 40.3069 | 84.9706 | 94.3311 | 32.2265 | 84.0521 | 94.6133 | 24.2318 | 83.2377 | 89.6955 | 16.2722 | 82.2202 | 45.9482 | 8.3357 | 45.9482 | 43.7136 | 7.9303 | 43.7136 | 41.7296 | 7.5704 | 41.7296 | 39.5868 | 7.1817 | 39.5868 | 37.7167 | 6.8424 | 37.7167 | 36.4135 | 6.606 | 36.4135 | 79.5546 | 14.4325 | 51.2109 | 106.6598 | 47.5724 | 38.317 | 107.3573 | 49.1772 | 30.5121 | 93.83 | 48.5341 | 86.6305 | 94.1573 | 46.3183 | 85.043 | 94.2955 | 44.0813 | 84.1599 | 94.5393 | 41.9016 | 83.4866 | 94.8812 | 39.5677 | 82.6137 | 95.3515 | 37.1347 | 81.654 | 95.9395 | 36.6034 | 80.5701 | 96.6048 | 36.6428 | 79.4835 | 97.4167 | 36.7193 | 78.0018 | 98.6574 | 36.6175 | 73.8212 | 101.9265 | 54.8743 | 54.7123 | 104.2322 | 51.3412 | 39.5945 | 105.1522 | 49.8653 | 31.4135 | 104.9836 | 49.4127 | 34.8993
BURY | KEARSLEY | 380272 | 411184 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 93.4667 | 21.7709 | 40.6884 | 95.2976 | 26.498 | 40.2234 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 78.147 | 14.1771 | 43.6098 | 90.2168 | 18.2756 | 42.8293 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 21.7666 | 3.9488 | 21.7666 | 91.8533 | 30.2242 | 43.6364 | 93.0343 | 36.0501 | 43.7815 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 74.8444 | 13.578 | 12.9286 | 90.0905 | 16.3438 | 0.7508 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 94.6418 | 26.4087 | 34.9891 | 99.8777 | 20.5092 | 16.3872 | 94.3498 | 17.1166 | 4.3867 | 92.832 | 16.8412 | 6.9103
BUXTON | STALYBRIDGE | 407769 | 375476 | 57.4386 | 39.664 | 57.4386 | 57.8188 | 25.3183 | 57.8188 | 57.9428 | 11.056 | 57.9428 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 78.4564 | 68.0146 | 44.8177 | 79.2316 | 67.2323 | 44.9533 | 57.1038 | 39.7241 | 57.1038 | 57.2081 | 23.7976 | 57.2081 | 43.7291 | 7.9332 | 43.7291 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 63.1632 | 17.0839 | 57.7208 | 63.833 | 63.833 | 57.2374 | 57.439 | 39.7205 | 57.439 | 57.8198 | 23.803 | 57.8198 | 43.3481 | 7.864 | 43.3481 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 77.5898 | 75.2105 | 45.8475 | 77.9998 | 74.1958 | 46.2857 | 57.4115 | 39.6721 | 57.4115 | 57.7754 | 25.3435 | 57.7754 | 57.8981 | 11.0821 | 52.3328 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 78.4955 | 65.0667 | 15.8279 | 78.5834 | 63.9611 | 13.5101 | 57.4372 | 39.6824 | 57.4372 | 57.8484 | 39.565 | 57.8484 | 57.9914 | 39.3988 | 52.3488 | 58.2379 | 38.9678 | 39.3672 | 58.5836 | 38.4627 | 39.1608 | 59.0357 | 37.5382 | 38.8743 | 59.6666 | 37.0389 | 38.4636 | 60.2416 | 37.3933 | 38.103 | 60.8982 | 38.033 | 37.6268 | 63.866 | 38.7516 | 34.7742 | 76.8441 | 68.9316 | 20.599 | 78.0913 | 66.338 | 15.4511 | 78.4048 | 64.443 | 12.938 | 77.8787 | 63.6826 | 14.8305
CARLISLE | HARKER / HUTTON | 338655 | 556583 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.2427 | 6.7308 | 1.9358 | -12.9147 | 6.7308 | 1.9358 | -25.4476 | 6.7308 | 1.9358 | -29.5104 | 6.7308 | 1.9358 | -28.3894 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 5.737 | 6.7308 | 1.9358 | -1.1294 | 6.7308 | 1.9358 | -5.2996 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -11.0331 | 6.7308 | 1.9358 | -20.8677 | 6.7308 | 1.9358 | -23.1315 | 6.7308 | 1.9358 | -20.7604 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 5.8653 | 6.7308 | 1.9358 | -20.7519 | 6.7308 | 1.9358 | -57.0538 | 6.7308 | 1.9358 | -80.2847 | 6.7308 | 1.9358 | -95.3895 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.4655 | 6.7308 | 1.9358 | -4.7707 | 6.7308 | 1.9358 | -46.2302 | 6.7308 | 1.9358 | -76.2676 | 6.7308 | 1.9358 | -91.0766 | 6.7308 | 1.9358 | -84.9115
CARRINGTON BSP | CARRINGTON | 373110 | 393020 | 18.2081 | 10.1907 | 18.2081 | 0.69824 | 0.12667 | 0.69824 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 33.0548 | 33.0548 | 31.9439 | 35.4289 | 35.4289 | 29.806 | 18.1048 | 9.2535 | 18.1048 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 24.6972 | 18.2452 | 24.6972 | 26.3049 | 26.3049 | 26.3049 | 18.2093 | 9.2482 | 18.2093 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 31.1816 | 31.1816 | 31.1816 | 32.5634 | 32.5634 | 32.5634 | 18.2099 | 10.1885 | 18.2099 | 0.6502 | 0.11796 | 0.6502 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 44.3036 | 44.3036 | 8.8625 | 45.3591 | 45.3591 | 2.6405 | 18.2118 | 10.1943 | 18.2118 | 1.1037 | 0.20023 | 1.1037 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 38.3014 | 38.3014 | 22.7222 | 40.8585 | 40.8585 | 12.9788 | 42.1345 | 42.1345 | 6.639 | 41.7708 | 41.7708 | 6.5129
CASTLETON | ROCHDALE | 388461 | 411290 | 126.0205 | 52.4966 | 77.5426 | 126.3122 | 42.775 | 74.9743 | 126.4739 | 33.0495 | 72.1596 | 126.7361 | 23.3663 | 66.7944 | 76.1959 | 13.8231 | 61.1587 | 24.768 | 4.4933 | 24.768 | 20.5479 | 3.7277 | 20.5479 | 17.8695 | 3.2418 | 17.8695 | 15.5134 | 2.8144 | 15.5134 | 12.6243 | 2.2902 | 12.6243 | 10.5226 | 1.909 | 10.5226 | 67.1272 | 12.1779 | 28.5323 | 144.1093 | 30.2415 | 25.1235 | 148.1229 | 33.8407 | 21.8546 | 125.8616 | 53.5286 | 79.1643 | 126.0582 | 44.238 | 78.0442 | 126.3646 | 34.77 | 75.4858 | 126.6915 | 25.4015 | 71.0471 | 89.4356 | 16.225 | 66.4547 | 36.8704 | 6.6889 | 36.8704 | 33.594 | 6.0945 | 33.594 | 31.8112 | 5.7711 | 31.8112 | 30.3621 | 5.5082 | 30.3621 | 28.2047 | 5.1168 | 28.2047 | 29.4352 | 5.34 | 29.4352 | 71.1498 | 12.9077 | 40.6691 | 138.055 | 25.9265 | 37.2098 | 140.7191 | 28.9432 | 34.5395 | 126.0228 | 53.5234 | 77.5903 | 126.3174 | 44.0693 | 75.07 | 126.4834 | 34.3957 | 72.3013 | 126.751 | 24.8209 | 66.9716 | 85.084 | 15.4356 | 61.3852 | 31.4012 | 5.6967 | 31.4012 | 27.752 | 5.0347 | 27.752 | 25.4205 | 4.6117 | 25.4205 | 23.3211 | 4.2308 | 23.3211 | 20.7026 | 3.7558 | 20.7026 | 22.7826 | 4.1331 | 22.7826 | 90.1265 | 16.3504 | 31.412 | 141.3382 | 37.07 | 28.887 | 143.9354 | 41.5412 | 26.7045 | 126.0152 | 52.5002 | 77.5969 | 126.322 | 46.8615 | 75.07 | 126.5414 | 37.7404 | 72.2665 | 126.9081 | 28.0518 | 66.8714 | 102.0522 | 18.5139 | 61.2083 | 50.6593 | 9.1904 | 50.6542 | 46.275 | 8.395 | 46.275 | 43.5055 | 7.8926 | 43.5055 | 41.0987 | 7.456 | 41.0987 | 38.2239 | 6.9344 | 38.2239 | 31.7884 | 5.7669 | 29.026 | 73.3644 | 13.3095 | 5.3028 | 144.2394 | 26.1673 | -12.9065 | 138.69 | 25.1606 | -25.0537 | 125.9926 | 52.547 | 77.5949 | 126.3009 | 51.127 | 75.029 | 126.5344 | 49.3935 | 72.2368 | 126.9115 | 47.48 | 66.8971 | 127.4408 | 45.4004 | 61.2755 | 128.811 | 42.922 | 50.1817 | 130.4151 | 41.8263 | 46.2195 | 132.0968 | 41.0856 | 43.1833 | 133.5894 | 40.5741 | 41.2246 | 136.1328 | 39.3838 | 36.711 | 145.8492 | 34.2964 | 11.1886 | 153.1219 | 29.4595 | -10.2193 | 148.0091 | 26.8512 | -22.5621 | 144.4989 | 26.2144 | -20.6385
CHADDERTON | WHITEGATE | 389137 | 403821 | 88.8113 | 19.4921 | 42.5812 | 74.2321 | 13.4669 | 39.6036 | 44.8655 | 8.1393 | 37.6927 | 16.3525 | 2.9666 | 16.3525 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 2.7993 | 10.6707 | 1.9358 | -6.2736 | 107.0554 | 21.048 | -10.1795 | 109.4233 | 25.5861 | -11.3993 | 88.4026 | 20.5824 | 44.154 | 86.3956 | 15.6735 | 42.5482 | 61.7476 | 11.202 | 40.3419 | 38.7134 | 7.0232 | 38.346 | 17.4717 | 3.1697 | 17.4717 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 24.2735 | 4.4036 | 3.7748 | 101.542 | 18.5919 | -1.1837 | 103.1826 | 21.761 | -4.5447 | 88.8198 | 20.5651 | 42.6707 | 85.4092 | 15.4946 | 39.7839 | 59.6553 | 10.8224 | 37.9643 | 35.5346 | 6.4466 | 35.5346 | 13.7975 | 2.5031 | 13.7975 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 5.6094 | 48.4337 | 8.7866 | -1.8314 | 105.0648 | 31.678 | -4.8915 | 106.7623 | 36.0638 | -5.4192 | 88.7983 | 19.493 | 42.6717 | 74.1298 | 13.4483 | 39.7856 | 44.4583 | 8.0654 | 37.9598 | 16.0536 | 2.9124 | 16.0536 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -1.1444 | 10.6707 | 1.9358 | -34.5831 | 56.8495 | 10.3134 | -60.9546 | 62.8669 | 11.4051 | -79.4177 | 88.7879 | 19.5275 | 42.6204 | 88.5288 | 16.0605 | 39.4762 | 71.6544 | 12.9993 | 37.5661 | 54.7633 | 9.9349 | 35.7156 | 38.4963 | 6.9838 | 33.3282 | 26.0894 | 4.733 | 26.0894 | 21.4021 | 3.8827 | 21.4021 | 19.1666 | 3.4771 | 19.1666 | 17.0777 | 3.0982 | 17.0777 | 13.8167 | 2.5066 | 13.6426 | 105.3895 | 25.019 | -24.6513 | 95.7413 | 17.369 | -56.2328 | 72.9204 | 13.2289 | -74.3269 | 70.4224 | 12.7757 | -70.2711
DROYLSDEN | STALYBRIDGE | 390140 | 398146 | 107.2263 | 19.4526 | 66.2208 | 74.1925 | 13.4597 | 64.7594 | 42.2679 | 7.6681 | 42.2679 | 9.5451 | 1.7316 | 9.5451 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 31.5714 | 5.7276 | 31.5714 | 24.7401 | 4.4882 | 24.7401 | 108.546 | 19.692 | 66.8165 | 72.248 | 13.1069 | 65.9443 | 36.5852 | 6.6371 | 36.5852 | 0.34645 | 0.062851 | 0.34645 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 56.7571 | 10.2966 | 34.0366 | 108.4139 | 19.668 | 66.3226 | 72.3801 | 13.1309 | 64.9774 | 36.2049 | 6.5681 | 36.2049 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 48.4126 | 8.7828 | 34.9209 | 42.8925 | 7.7814 | 35.5441 | 107.2162 | 19.4507 | 66.2534 | 74.126 | 13.4476 | 64.8264 | 41.8329 | 7.5892 | 41.8329 | 8.7421 | 1.586 | 8.7421 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.248 | 10.6707 | 1.9358 | -11.1241 | 10.6707 | 1.9358 | -25.6068 | 107.3836 | 19.4811 | 66.3661 | 103.8932 | 18.8479 | 64.9005 | 100.9063 | 18.306 | 63.9265 | 96.0984 | 17.4338 | 62.8439 | 91.3314 | 16.569 | 61.4307 | 86.4187 | 15.6777 | 59.8906 | 80.7616 | 14.6514 | 57.8175 | 76.0487 | 13.7965 | 56.0062 | 70.4736 | 12.785 | 53.6472 | 60.4389 | 10.9646 | 47.0754 | 28.0455 | 5.0879 | 16.3382 | 10.6707 | 1.9358 | -8.4062 | 10.6707 | 1.9358 | -22.5801 | 10.6707 | 1.9358 | -18.611
EGREMONT | HARKER / HUTTON | 301070 | 513074 | 73.1439 | 63.7679 | 73.1439 | 73.3816 | 63.5862 | 73.3816 | 73.5221 | 63.3718 | 73.5221 | 73.786 | 62.9276 | 73.786 | 74.1473 | 62.577 | 74.1473 | 74.6038 | 60.8805 | 74.6038 | 75.1375 | 59.1756 | 74.542 | 75.7314 | 57.5078 | 72.9568 | 76.3686 | 55.8172 | 71.4077 | 77.0948 | 54.049 | 69.4012 | 80.0579 | 52.0096 | 62.5617 | 81.4503 | 50.8668 | 59.5904 | 82.1998 | 53.5514 | 59.6648 | 82.5198 | 52.7953 | 61.9582 | 72.9994 | 63.8292 | 72.9994 | 73.1288 | 63.7282 | 73.1288 | 73.3941 | 63.5134 | 73.3941 | 73.7078 | 63.2066 | 73.7078 | 74.07 | 63.0227 | 74.07 | 74.4874 | 62.6981 | 74.4874 | 74.9633 | 62.3756 | 74.9633 | 75.4868 | 62.0904 | 75.4868 | 76.0531 | 61.7912 | 76.0531 | 76.6597 | 61.468 | 76.6597 | 78.0306 | 60.6279 | 78.0306 | 79.1639 | 59.8053 | 79.1639 | 79.7797 | 61.2349 | 79.7797 | 80.0431 | 63.0826 | 80.0431 | 73.1499 | 63.8273 | 73.1499 | 73.3896 | 63.7137 | 73.3896 | 73.5314 | 63.4482 | 73.5314 | 73.7959 | 63.0457 | 73.7959 | 74.1555 | 62.7611 | 74.1555 | 74.6056 | 59.8902 | 74.6056 | 75.1303 | 57.0051 | 74.9777 | 75.7134 | 54.1399 | 73.4637 | 76.3305 | 51.2252 | 72.0124 | 77.0072 | 48.2895 | 70.2339 | 79.8625 | 46.8341 | 64.2088 | 81.0161 | 45.889 | 61.837 | 81.5695 | 48.5962 | 62.1986 | 81.7507 | 47.4432 | 64.4915 | 73.1387 | 63.765 | 73.1387 | 73.3854 | 63.559 | 73.3854 | 73.58 | 63.2902 | 73.58 | 73.943 | 62.8214 | 73.943 | 74.468 | 62.4396 | 74.468 | 75.1639 | 60.6859 | 75.1639 | 76.0315 | 58.8924 | 74.6375 | 77.0408 | 57.1228 | 72.9314 | 78.1634 | 55.3997 | 71.5123 | 79.3987 | 53.6676 | 70.0587 | 81.9399 | 51.1743 | 62.6766 | 84.1393 | 48.0928 | 49.5493 | 85.1203 | 48.8681 | 41.2093 | 85.4883 | 46.8406 | 35.7137 | 73.1229 | 63.7745 | 73.1229 | 73.4052 | 63.5977 | 73.4052 | 73.6318 | 63.3234 | 73.6318 | 74.0014 | 62.8178 | 74.0014 | 74.5294 | 62.3892 | 74.5294 | 75.2051 | 60.6212 | 75.2051 | 76.0677 | 58.8242 | 74.7491 | 77.0376 | 57.1573 | 73.3609 | 78.1054 | 55.5314 | 72.0555 | 79.2302 | 53.6207 | 68.6437 | 81.7989 | 53.7034 | 52.9961 | 83.381 | 49.9983 | 42.1342 | 83.7428 | 47.8075 | 37.2893 | 83.3142 | 47.0599 | 40.9017
FREDERICK RD | KEARSLEY | 381795 | 399250 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -9.2061 | 6.7308 | 1.9358 | -20.9446 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -5.3194 | 6.7308 | 1.9358 | -17.0345 | 6.7308 | 1.9358 | -15.9123
GOLBORNE | BOLD | 360607 | 397690 | 79.0905 | 39.1458 | 67.368 | 76.4131 | 31.9329 | 65.4212 | 76.6518 | 25.015 | 63.6767 | 77.0848 | 18.1043 | 62.021 | 62.686 | 11.3722 | 59.9125 | 51.1249 | 9.2749 | 51.1249 | 47.8126 | 8.674 | 47.8126 | 45.0049 | 8.1646 | 45.0049 | 41.8768 | 7.5971 | 41.8768 | 38.3623 | 6.9595 | 38.3623 | 39.8443 | 7.2284 | 35.1011 | 95.5572 | 24.4056 | 28.5751 | 100.5525 | 55.7399 | 26.2612 | 104.7947 | 61.7305 | 24.7769 | 78.6481 | 38.8178 | 68.7164 | 75.6986 | 31.4441 | 68.2939 | 76.1201 | 24.1126 | 66.5482 | 76.6219 | 16.8382 | 65.1054 | 53.8919 | 9.7768 | 53.8919 | 44.3648 | 8.0485 | 44.3648 | 41.9073 | 7.6026 | 41.9073 | 39.8267 | 7.2252 | 39.8267 | 37.6198 | 6.8248 | 37.6198 | 35.15 | 6.3768 | 35.15 | 38.1828 | 6.927 | 38.1828 | 87.5735 | 19.1309 | 39.4984 | 90.897 | 40.4684 | 35.9857 | 93.722 | 46.1072 | 33.5706 | 79.0947 | 38.8098 | 67.7678 | 76.4217 | 31.2812 | 65.4625 | 76.6657 | 23.7565 | 63.7883 | 77.105 | 16.2007 | 62.1673 | 48.8322 | 8.8589 | 48.8322 | 38.087 | 6.9096 | 38.087 | 34.9392 | 6.3385 | 34.9392 | 32.1173 | 5.8266 | 32.1173 | 29.0412 | 5.2685 | 29.0412 | 25.6329 | 4.6502 | 25.6329 | 29.999 | 5.4423 | 29.999 | 92.6679 | 24.6306 | 32.28 | 96.8301 | 58.7224 | 30.7175 | 99.7026 | 65.1359 | 30.8327 | 79.0693 | 39.1515 | 67.4491 | 76.3903 | 31.935 | 65.5326 | 76.7123 | 24.9996 | 63.874 | 77.3093 | 18.0556 | 62.3227 | 62.2647 | 11.2958 | 60.4516 | 50.8388 | 9.223 | 50.8388 | 47.1797 | 8.5591 | 47.1797 | 43.9737 | 7.9775 | 43.9737 | 40.5792 | 7.3617 | 40.5792 | 36.7922 | 6.6747 | 36.7922 | 33.8769 | 6.1458 | 33.8769 | 105.7834 | 20.7393 | 9.0442 | 111.1704 | 48.9403 | -9.9461 | 113.4863 | 53.0307 | -22.4463 | 79.0696 | 39.1563 | 67.3702 | 76.5093 | 33.7357 | 65.366 | 76.9297 | 28.4139 | 63.6771 | 77.5819 | 22.9594 | 62.2217 | 78.4983 | 17.5865 | 60.4671 | 79.7982 | 16.6757 | 58.1481 | 81.5249 | 15.9829 | 55.5192 | 83.5422 | 16.2623 | 53.0836 | 85.8554 | 16.738 | 50.2781 | 88.5888 | 17.3671 | 44.2355 | 99.5716 | 62.9796 | 16.2264 | 107.0071 | 57.8249 | -6.1927 | 110.1396 | 54.7692 | -18.6186 | 110.1774 | 53.6302 | -15.6076
GREENHILL | WHITEGATE | 393262 | 404755 | 127.1152 | 54.7043 | 62.6056 | 127.7958 | 44.0013 | 60.7381 | 127.9357 | 33.8776 | 59.8844 | 128.2722 | 24.0478 | 58.7304 | 80.2369 | 14.5563 | 57.2277 | 30.9231 | 5.61 | 30.9231 | 28.277 | 5.1299 | 28.277 | 25.3068 | 4.5911 | 25.3068 | 22.0853 | 4.0066 | 22.0853 | 18.7317 | 3.3982 | 18.7317 | 11.6169 | 2.1075 | 11.6169 | 47.3228 | 8.5851 | 33.9546 | 142.9611 | 39.8949 | 31.5216 | 144.8785 | 41.4686 | 31.0846 | 126.5507 | 54.9954 | 63.778 | 126.7689 | 44.0025 | 62.8851 | 127.2164 | 33.2877 | 61.4905 | 126.493 | 22.9479 | 60.0938 | 71.6401 | 12.9967 | 58.4877 | 19.7215 | 3.5778 | 19.7215 | 17.8394 | 3.2364 | 17.8394 | 15.614 | 2.8326 | 15.614 | 13.0807 | 2.3731 | 13.0807 | 10.6892 | 1.9392 | 10.6892 | 6.6915 | 1.214 | 6.6915 | 23.8782 | 4.3319 | 23.8782 | 134.6845 | 24.4339 | 34.0263 | 140.5774 | 39.6697 | 31.8165 | 127.128 | 54.9813 | 62.6827 | 127.8136 | 43.7278 | 60.8879 | 127.9575 | 32.7371 | 60.1087 | 122.0133 | 22.1351 | 59.0256 | 65.8217 | 11.9411 | 57.6066 | 12.7227 | 2.3081 | 12.7227 | 10.494 | 1.9038 | 10.494 | 7.8619 | 1.4263 | 7.8619 | 4.9649 | 0.90072 | 4.9649 | 2.1003 | 0.38103 | 2.1003 | 2.114 | 0.38351 | 2.114 | 44.1967 | 8.018 | 36.7361 | 140.8005 | 43.4324 | 34.8258 | 142.2108 | 45.4766 | 34.7952 | 127.0817 | 54.7117 | 62.6608 | 127.7321 | 44.0117 | 60.8345 | 127.8821 | 33.8733 | 60.0179 | 128.2667 | 24.037 | 58.8907 | 80.2178 | 14.5528 | 57.4349 | 30.8225 | 5.5917 | 30.8225 | 27.962 | 5.0727 | 27.962 | 24.742 | 4.4886 | 24.742 | 21.3149 | 3.8669 | 21.3149 | 17.9584 | 3.2579 | 17.9584 | 5.9119 | 1.0725 | 5.9119 | 23.8068 | 4.3189 | 11.0072 | 148.8484 | 32.0652 | -8.9522 | 150.3854 | 31.4431 | -22.1709 | 127.0508 | 54.736 | 62.7487 | 127.7083 | 53.5402 | 60.9491 | 127.8664 | 52.4461 | 60.2206 | 128.2326 | 51.15 | 59.2658 | 128.8033 | 49.8303 | 57.9162 | 129.6492 | 48.8461 | 56.3225 | 130.725 | 48.1309 | 54.5381 | 131.8447 | 47.4353 | 52.7192 | 133.1183 | 46.699 | 50.4092 | 134.8718 | 45.3712 | 44.3397 | 140.4698 | 41.6853 | 16.4683 | 144.9532 | 35.5715 | -6.0184 | 147.117 | 32.0895 | -18.9483 | 147.1828 | 31.515 | -15.5877
HAZEL GROVE | BREDBURY | 391313 | 386877 | 154.2857 | 46.5057 | 65.011 | 154.6177 | 45.7424 | 63.5923 | 154.8284 | 44.9578 | 62.3687 | 155.2339 | 44.1234 | 60.911 | 157.3698 | 43.4259 | 57.4179 | 159.5682 | 42.3774 | 53.7172 | 159.9937 | 41.4986 | 51.5848 | 160.4418 | 40.7763 | 49.3287 | 160.9451 | 40.0399 | 47.0393 | 161.6235 | 39.1542 | 44.2703 | 164.6367 | 35.6027 | 34.8007 | 169.3489 | 32.9043 | 28.0177 | 170.7164 | 32.8054 | 27.4416 | 172.0037 | 33.3626 | 28.596 | 154.1023 | 46.6932 | 65.4044 | 154.2932 | 45.8929 | 64.3819 | 154.641 | 45.2229 | 63.0091 | 155.0889 | 44.4796 | 61.6794 | 155.6002 | 44.0106 | 60.106 | 156.1737 | 43.4112 | 58.3283 | 156.7406 | 42.7718 | 56.3693 | 157.2859 | 42.3161 | 54.2943 | 157.8668 | 41.8382 | 52.1032 | 158.471 | 41.2679 | 49.892 | 160.0281 | 39.5975 | 43.1598 | 161.396 | 38.2731 | 38.3401 | 162.4585 | 38.2655 | 35.4149 | 163.227 | 38.6352 | 33.5988 | 154.2872 | 46.6812 | 65.0316 | 154.6199 | 46.1591 | 63.7306 | 154.8315 | 45.41 | 62.5758 | 155.238 | 44.5401 | 61.1738 | 157.3723 | 43.9657 | 57.7483 | 159.5666 | 43.2652 | 54.143 | 159.9911 | 42.5301 | 52.1032 | 160.4372 | 41.9639 | 49.9363 | 160.9311 | 41.3597 | 47.7763 | 161.5725 | 40.6563 | 45.2997 | 164.3457 | 38.1301 | 36.8286 | 168.6462 | 36.2767 | 30.7461 | 169.7828 | 35.55 | 30.4035 | 170.7826 | 35.8003 | 31.5543 | 154.2686 | 46.5148 | 65.0573 | 154.6114 | 45.7543 | 63.7075 | 154.9058 | 44.9255 | 62.5939 | 155.4704 | 44.1128 | 61.2771 | 157.7508 | 43.4462 | 58.1363 | 159.9414 | 42.4145 | 54.7906 | 160.6464 | 41.5313 | 52.8583 | 161.4916 | 40.8171 | 50.8359 | 162.4464 | 40.1152 | 49.0824 | 163.6151 | 39.285 | 47.235 | 172.667 | 33.9827 | 31.2285 | 150.6802 | 27.3358 | 7.1397 | 128.7181 | 23.3515 | -10.6401 | 114.6798 | 20.8047 | -22.7781 | 154.2587 | 46.5126 | 65.0456 | 154.6691 | 45.8872 | 63.5181 | 155.0023 | 45.2171 | 62.435 | 155.5521 | 44.4995 | 61.2954 | 156.2021 | 43.9229 | 59.7756 | 161.412 | 42.9046 | 53.6733 | 166.0731 | 41.2647 | 48.1063 | 166.5587 | 40.6037 | 46.8297 | 167.262 | 39.8227 | 45.0485 | 168.4563 | 38.3031 | 39.6866 | 170.5969 | 30.949 | 13.0748 | 136.9412 | 24.8433 | -8.291 | 126.1265 | 22.8814 | -19.6141 | 120.6813 | 21.8935 | -15.4415
HARTSHEAD-HEYROD | STALYBRIDGE | 397322 | 399942 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -1.8332 | 6.7308 | 1.9358 | -18.2822 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 1.6262 | 6.7308 | 1.9358 | -14.3842 | 6.7308 | 1.9358 | -8.595
HUNCOAT | PADIHAM | 377997 | 431083 | 46.0421 | 46.0421 | 46.0421 | 46.4782 | 39.3247 | 45.2545 | 46.8377 | 31.4248 | 44.6171 | 47.3775 | 23.6799 | 43.8357 | 48.0569 | 16.162 | 42.749 | 48.5335 | 8.8273 | 41.3906 | 45.7279 | 8.2958 | 39.9665 | 42.6103 | 7.7302 | 38.5316 | 39.2296 | 7.1169 | 37.0823 | 35.7157 | 6.4794 | 35.1729 | 34.2964 | 6.2219 | 26.0653 | 58.5817 | 19.1805 | 20.7304 | 61.553 | 58.6323 | 19.0853 | 64.3657 | 62.7393 | 19.115 | 45.7868 | 45.7868 | 45.7868 | 46.0056 | 39.4794 | 46.0056 | 46.4447 | 31.2814 | 46.4447 | 46.9159 | 23.3156 | 46.2522 | 47.4665 | 15.5799 | 45.1129 | 44.3802 | 8.0513 | 43.8459 | 42.2855 | 7.6713 | 42.2855 | 40.1014 | 7.275 | 40.1014 | 37.8218 | 6.8615 | 37.8218 | 35.3904 | 6.4204 | 35.3904 | 35.2421 | 6.3935 | 31.4616 | 55.5046 | 14.013 | 27.0864 | 57.4303 | 39.2527 | 24.5402 | 58.9828 | 54.0316 | 23.1951 | 46.0529 | 46.0529 | 46.0529 | 46.4937 | 39.3676 | 45.3115 | 46.8573 | 31.0479 | 44.709 | 47.4006 | 22.8898 | 43.9643 | 48.074 | 15.0148 | 42.9212 | 40.2118 | 7.2951 | 40.2118 | 37.391 | 6.7833 | 37.391 | 34.6004 | 6.2771 | 34.6004 | 31.6078 | 5.7342 | 31.6078 | 28.5429 | 5.1781 | 28.5429 | 32.6461 | 5.9225 | 28.2029 | 56.921 | 20.1982 | 24.1033 | 59.1941 | 59.1941 | 23.0517 | 60.9606 | 60.9606 | 23.7245 | 46.0392 | 46.0392 | 46.0392 | 46.5069 | 39.3155 | 45.3929 | 46.9944 | 31.3603 | 44.7881 | 47.7574 | 23.6226 | 44.01 | 48.2679 | 16.0861 | 42.8967 | 48.2226 | 8.7484 | 41.4338 | 45.0208 | 8.1675 | 39.7692 | 41.7221 | 7.5691 | 38.017 | 38.403 | 6.9669 | 36.3499 | 35.0328 | 6.3555 | 34.5792 | 29.0324 | 5.2669 | 22.4431 | 69.765 | 14.1722 | -4.516 | 74.7092 | 49.1032 | -25.7193 | 77.0649 | 50.0422 | -40.6136 | 46.0518 | 46.0518 | 46.0518 | 46.6518 | 46.6518 | 45.3088 | 47.2677 | 46.81 | 44.6775 | 47.7259 | 46.2067 | 43.9599 | 48.2174 | 45.5447 | 42.8947 | 49.0385 | 44.7912 | 41.434 | 49.9991 | 44.0872 | 39.8488 | 51.13 | 43.833 | 38.2029 | 52.5493 | 43.701 | 35.9327 | 54.7309 | 43.1085 | 30.0161 | 63.716 | 61.731 | 1.206 | 70.0978 | 55.437 | -23.6056 | 73.0513 | 51.414 | -39.8506 | 73.1748 | 50.2999 | -35.3202
HYDE | STALYBRIDGE | 395522 | 395647 | 83.7911 | 15.201 | 77.0726 | 80.1382 | 14.5383 | 75.5828 | 76.4123 | 13.8624 | 74.2647 | 70.0664 | 12.7112 | 70.0664 | 63.7011 | 11.5564 | 63.7011 | 59.0895 | 10.7198 | 59.0895 | 55.9063 | 10.1423 | 55.9063 | 52.7917 | 9.5773 | 52.7917 | 49.4643 | 8.9736 | 49.4643 | 45.9211 | 8.3308 | 45.9211 | 40.2974 | 7.3106 | 40.2974 | 101.4177 | 18.3988 | 40.0927 | 110.9436 | 39.2532 | 38.7779 | 112.6784 | 44.4356 | 39.2665 | 84.2596 | 15.286 | 77.776 | 79.5948 | 14.4398 | 76.8496 | 76.2282 | 13.829 | 75.2164 | 71.2775 | 12.9309 | 71.2775 | 66.0026 | 11.9739 | 66.0026 | 62.3459 | 11.3105 | 62.3459 | 60.1054 | 10.9041 | 60.1054 | 58.1379 | 10.5471 | 58.1379 | 55.9964 | 10.1586 | 55.9964 | 53.7441 | 9.75 | 53.7441 | 52.7435 | 9.5685 | 52.2436 | 92.9395 | 16.8607 | 48.2365 | 105.6673 | 30.9692 | 46.2591 | 106.5249 | 35.2798 | 45.46 | 84.197 | 15.2747 | 77.1133 | 79.613 | 14.4431 | 75.6652 | 75.8864 | 13.767 | 74.3907 | 70.0224 | 12.7032 | 70.0224 | 63.925 | 11.597 | 63.925 | 59.1021 | 10.7221 | 59.1021 | 56.0856 | 10.1748 | 56.0856 | 53.2629 | 9.6627 | 53.2629 | 49.9645 | 9.0643 | 49.9645 | 46.3146 | 8.4022 | 46.3146 | 46.9273 | 8.5134 | 46.9273 | 107.9723 | 20.5305 | 42.566 | 109.7418 | 43.7101 | 41.5537 | 111.0647 | 47.7284 | 42.2777 | 83.796 | 15.2019 | 77.1486 | 80.1601 | 14.5423 | 75.749 | 75.9191 | 13.7729 | 74.5633 | 69.8894 | 12.6791 | 69.8894 | 63.5022 | 11.5203 | 63.5022 | 58.5119 | 10.615 | 58.5119 | 55.0386 | 9.9849 | 55.0386 | 51.6372 | 9.3678 | 51.6372 | 48.1938 | 8.7431 | 48.1938 | 44.5189 | 8.0764 | 44.5189 | 35.4223 | 6.4262 | 35.4223 | 80.8719 | 14.6715 | 21.5406 | 118.3648 | 33.0957 | 5.3067 | 119.8754 | 35.9782 | -5.0458 | 83.8374 | 15.2094 | 77.0698 | 82.4474 | 14.9573 | 75.3473 | 80.5071 | 14.6053 | 74.0422 | 75.863 | 13.7628 | 72.044 | 70.5483 | 12.7986 | 68.2388 | 66.8948 | 12.1358 | 66.2951 | 63.301 | 11.4838 | 63.301 | 63.5578 | 11.5304 | 61.9273 | 64.6133 | 11.7219 | 59.3141 | 65.1517 | 11.8195 | 53.7093 | 110.8717 | 45.115 | 27.986 | 114.574 | 40.0033 | 8.884 | 115.9388 | 37.3153 | -0.97931 | 115.6778 | 37.0382 | 2.7699
KEARSLEY LOCAL | KEARSLEY | 376355 | 404783 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.8026 | 1.9358 | 9.8026 | 6.3315 | 1.9358 | 6.3315 | 2.4182 | 0.99327 | 2.4182 | 0.012364 | 0.0050782 | 0.012364 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 1.5959 | 6.7308 | 1.9358 | -2.7778 | 6.7308 | 1.9358 | -5.7989 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.3581 | 1.9358 | 9.3581 | 7.6762 | 1.9358 | 7.6762 | 6.0972 | 1.9358 | 6.0972 | 4.3861 | 1.8016 | 4.3861 | 2.5847 | 1.0617 | 2.5847 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 3.591 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 7.594 | 1.9358 | 7.594 | 4.1738 | 1.7144 | 4.1738 | 2.291 | 0.94102 | 2.291 | 0.50095 | 0.20576 | 0.50095 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 4.9265 | 6.7308 | 1.9358 | 4.2882 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.6268 | 1.9358 | 9.6268 | 6.1126 | 1.9358 | 6.1126 | 2.0811 | 0.85479 | 2.0811 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -35.501 | 6.7308 | 1.9358 | -71.0195 | 6.7308 | 1.9358 | -94.8651 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.2112 | 1.9358 | 10.2112 | 6.9314 | 1.9358 | 6.9314 | 3.2464 | 1.3334 | 3.2464 | 0.79631 | 0.32708 | 0.79631 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -22.7778 | 6.7308 | 1.9358 | -64.7083 | 6.7308 | 1.9358 | -88.5344 | 6.7308 | 1.9358 | -83.6168
KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351915 | 491858 | -60.6599 | -11.0047 | -60.6599 | -64.6095 | -11.7212 | -64.6095 | -68.5713 | -12.4399 | -68.5713 | -74.9649 | -13.5998 | -74.9649 | -80.2173 | -14.5527 | -80.2173 | -87.9181 | -15.9497 | -87.9181 | -97.4521 | -17.6794 | -97.4521 | -103.7583 | -18.8234 | -103.7583 | -112.7545 | -20.4555 | -112.7545 | -120.3507 | -21.8335 | -120.3507 | -152.0304 | -27.5807 | -152.0304 | -177.4654 | -32.195 | -177.4654 | -184.7012 | -33.5077 | -184.7012 | -183.281 | -33.2501 | -183.281 | -59.4227 | -10.7802 | -59.4227 | -62.1465 | -11.2744 | -62.1465 | -65.104 | -11.8109 | -65.104 | -70.2534 | -12.7451 | -70.2534 | -74.192 | -13.4596 | -74.192 | -79.9703 | -14.5079 | -79.9703 | -85.3935 | -15.4917 | -85.3935 | -89.8654 | -16.303 | -89.8654 | -94.9846 | -17.2317 | -94.9846 | -100.7164 | -18.2716 | -100.7164 | -118.1412 | -21.4327 | -118.1412 | -134.4771 | -24.3963 | -134.4771 | -138.7654 | -25.1743 | -138.7654 | -138.845 | -25.1887 | -138.845 | -59.4809 | -10.7908 | -59.4809 | -62.4456 | -11.3286 | -62.4456 | -66.5631 | -12.0756 | -66.5631 | -74.2132 | -13.4635 | -74.2132 | -80.6292 | -14.6274 | -80.6292 | -89.6544 | -16.2647 | -89.6544 | -98.2405 | -17.8224 | -98.2405 | -105.8928 | -19.2106 | -105.8928 | -114.2477 | -20.7264 | -114.2477 | -122.98 | -22.3105 | -122.98 | -154.2007 | -27.9745 | -154.2007 | -182.2148 | -33.0567 | -182.2148 | -195.994 | -35.5564 | -195.994 | -204.0316 | -37.0146 | -204.0316 | -60.6376 | -11.0006 | -60.6376 | -72.3334 | -13.1224 | -72.3334 | -77.1815 | -14.002 | -77.1815 | -83.9842 | -15.2361 | -83.9842 | -89.8992 | -16.3092 | -89.8992 | -98.6568 | -17.8979 | -98.6568 | -109.1984 | -19.8103 | -109.1984 | -116.4479 | -21.1255 | -116.4479 | -126.1086 | -22.8781 | -126.1086 | -134.0661 | -24.3217 | -134.0661 | -177.4888 | -32.1993 | -177.4888 | -219.178 | -39.7624 | -219.178 | -240.899 | -43.7029 | -240.899 | -50.7205 | -20.8331 | -71.4835 | -60.6646 | -11.0055 | -60.6646 | -64.4671 | -11.6954 | -64.4671 | -69.6479 | -12.6352 | -69.6479 | -77.3459 | -14.0318 | -77.3459 | -84.1071 | -15.2584 | -84.1071 | -98.1796 | -17.8114 | -98.1796 | -108.8125 | -19.7403 | -108.8125 | -116.0803 | -21.0588 | -116.0803 | -124.2639 | -22.5435 | -124.2639 | -135.1757 | -24.523 | -135.1757 | -185.0755 | -33.5756 | -185.0755 | -224.6815 | -40.7608 | -224.6815 | -230.0181 | -41.7289 | -230.0181 | -245.3712 | -44.5142 | -245.3712
LANCASTER | HEYSHAM | 348644 | 463628 | 84.0644 | 20.0134 | 25.7034 | 84.6984 | 19.2632 | 22.8326 | 80.4506 | 14.595 | 20.8836 | 53.9023 | 9.7787 | 18.6327 | 25.3106 | 4.5917 | 14.3043 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.0041 | 10.6707 | 1.9358 | 4.6413 | 10.6707 | 1.9358 | 0.98507 | 10.6707 | 1.9358 | -5.7415 | 10.6707 | 1.9358 | -22.0639 | 10.6707 | 1.9358 | -68.5046 | 10.6707 | 1.9358 | -70.6653 | 10.6707 | 1.9358 | -66.4968 | 83.7623 | 20.5484 | 26.958 | 84.203 | 20.3147 | 25.1568 | 84.9055 | 19.8992 | 22.7725 | 85.795 | 19.3988 | 20.5594 | 86.7161 | 18.7059 | 17.9442 | 87.6503 | 18.0695 | 14.9918 | 88.6997 | 17.361 | 11.7157 | 89.8197 | 16.5157 | 8.3109 | 87.264 | 15.8311 | 4.7786 | 82.8408 | 15.0286 | 1.1558 | 71.1154 | 12.9015 | -8.961 | 62.6865 | 11.3723 | -17.6797 | 69.0085 | 12.5192 | -23.3515 | 79.3984 | 14.4041 | -26.9792 | 84.074 | 20.5369 | 25.7861 | 84.7125 | 20.0168 | 23.0874 | 84.996 | 19.2737 | 21.3164 | 85.5649 | 18.2912 | 19.2145 | 87.89 | 17.184 | 15.0548 | 88.7128 | 16.0939 | 12.2042 | 83.4528 | 15.1397 | 9.0743 | 77.7038 | 14.0967 | 5.5145 | 72.7015 | 13.1892 | 2.0067 | 67.1392 | 12.1801 | -4.2969 | 48.2166 | 8.7473 | -19.0373 | 37.5917 | 6.8197 | -63.8799 | 47.8079 | 8.6731 | -65.2413 | 46.851 | 8.4995 | -60.4662 | 84.0365 | 20.0209 | 25.7716 | 84.6624 | 19.2628 | 22.8919 | 80.8224 | 14.6625 | 20.9566 | 53.8791 | 9.7745 | 18.7305 | 24.7727 | 4.4942 | 14.4894 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 7.8014 | 10.6707 | 1.9358 | 2.9587 | 10.6707 | 1.9358 | -0.24425 | 10.6707 | 1.9358 | -5.7182 | 10.6707 | 1.9358 | -26.3177 | 10.6707 | 1.9358 | -98.9203 | 10.6707 | 1.9358 | -122.9435 | 10.6707 | 1.9358 | -136.7908 | 83.9632 | 20.0174 | 25.7945 | 84.574 | 19.3265 | 22.8478 | 80.1412 | 14.5389 | 21.0468 | 52.8608 | 9.5898 | 19.0914 | 24.1587 | 4.3828 | 16.5373 | 10.6707 | 1.9358 | 10.3407 | 10.6707 | 1.9358 | 4.5593 | 10.6707 | 1.9358 | 0.63242 | 10.6707 | 1.9358 | -2.4277 | 10.6707 | 1.9358 | -10.8038 | 10.6707 | 1.9358 | -90.9867 | 10.6707 | 1.9358 | -119.0708 | 10.6707 | 1.9358 | -134.4145 | 10.6707 | 1.9358 | -125.3994
LEYLAND | PENWORTHAM WEST / STANAH | 354121 | 423373 | 132.6131 | 42.5379 | 51.7628 | 133.2761 | 40.1268 | 48.9057 | 133.5448 | 38.0139 | 46.8231 | 134.0194 | 35.7903 | 44.6751 | 134.6584 | 33.7517 | 41.9907 | 135.4712 | 31.5958 | 38.9903 | 136.4058 | 30.764 | 35.6702 | 137.4235 | 29.8518 | 32.2759 | 138.517 | 28.9564 | 28.8544 | 139.7158 | 27.9646 | 24.9993 | 132.1899 | 23.9814 | 9.0255 | 125.4366 | 22.7562 | 0.36459 | 138.4431 | 25.1158 | -3.0248 | 138.5524 | 25.1356 | -5.5228 | 132.1262 | 42.8182 | 53.0572 | 132.3846 | 40.9382 | 51.3442 | 132.864 | 39.0954 | 49.0681 | 133.4337 | 37.2489 | 47.0624 | 134.0731 | 35.6929 | 44.7193 | 134.7888 | 34.0773 | 42.1236 | 135.5944 | 33.5118 | 39.2189 | 136.4544 | 32.8888 | 36.2346 | 137.3729 | 32.2451 | 33.1489 | 138.3288 | 31.5779 | 30.0464 | 142.2466 | 29.4923 | 19.4176 | 146.449 | 28.6902 | 11.4727 | 150.5011 | 30.1067 | 6.3485 | 153.917 | 30.6514 | 2.8318 | 132.6221 | 42.8039 | 51.8106 | 133.2911 | 40.7345 | 49.0475 | 133.5668 | 38.6606 | 47.0587 | 134.0493 | 36.6055 | 44.9927 | 134.6943 | 34.8182 | 42.4294 | 135.5069 | 32.9484 | 39.558 | 136.438 | 32.2471 | 36.3676 | 137.4497 | 31.5092 | 33.1006 | 138.5232 | 30.7371 | 29.8569 | 139.6571 | 29.9296 | 26.3775 | 147.2369 | 27.1912 | 12.1049 | 145.9628 | 26.48 | 5.5934 | 156.5891 | 28.7739 | 3.3425 | 157.9055 | 28.6466 | 2.7611 | 132.588 | 42.5422 | 51.8321 | 133.2537 | 40.1214 | 49.0535 | 133.5984 | 38.0486 | 47.0947 | 134.2175 | 35.7942 | 45.0839 | 135.0813 | 33.7166 | 42.7009 | 136.3074 | 31.5195 | 40.014 | 137.8673 | 30.6359 | 36.9584 | 139.7017 | 29.7373 | 33.8551 | 141.7857 | 28.8567 | 31.0376 | 144.1295 | 27.9278 | 28.2087 | 126.7811 | 23.0001 | 8.9367 | 99.9934 | 18.1404 | -22.4756 | 94.2813 | 17.1041 | -43.1604 | 82.0945 | 14.8932 | -57.5021 | 132.6299 | 42.5316 | 51.6068 | 133.4239 | 41.2723 | 48.4246 | 133.865 | 40.1738 | 46.4118 | 134.5435 | 38.8543 | 44.5369 | 135.4718 | 37.6667 | 42.3261 | 136.8426 | 36.2991 | 39.8992 | 138.6872 | 35.3941 | 37.0429 | 140.8547 | 34.4898 | 34.2034 | 143.3523 | 33.5175 | 31.0542 | 148.4312 | 31.725 | 22.0408 | 138.1494 | 25.0625 | -13.319 | 104.9994 | 19.0486 | -38.3461 | 93.8731 | 17.0301 | -51.9839 | 87.8493 | 15.9373 | -49.5902
LONGSIGHT | BREDBURY | 385592 | 396016 | 142.0886 | 51.4029 | 59.2788 | 142.8295 | 45.6619 | 54.0683 | 142.7721 | 39.3633 | 47.5211 | 142.9542 | 33.3967 | 41.7318 | 143.2777 | 27.976 | 37.8765 | 130.6539 | 23.7027 | 33.7527 | 122.8032 | 22.2785 | 29.582 | 118.5972 | 21.5154 | 26.7079 | 114.2935 | 20.7347 | 23.8287 | 107.3637 | 19.4775 | 19.01 | 95.2281 | 17.2759 | 10.8398 | 113.55 | 20.5998 | 6.797 | 152.9703 | 30.4457 | 5.2413 | 153.2771 | 34.1794 | 5.5462 | 141.2398 | 51.7262 | 61.9144 | 141.2743 | 36.3366 | 59.6773 | 141.5506 | 29.9016 | 54.259 | 130.3695 | 23.6511 | 49.303 | 98.443 | 17.8591 | 45.2865 | 75.6445 | 13.7231 | 41.1192 | 68.8169 | 12.4845 | 36.8407 | 65.4487 | 11.8734 | 33.828 | 62.0498 | 11.2568 | 30.7763 | 57.3548 | 10.4051 | 27.6959 | 54.7002 | 9.9235 | 22.2658 | 71.4881 | 12.9691 | 17.9942 | 110.2299 | 19.9975 | 15.4973 | 124.6004 | 22.6045 | 14.1245 | 142.0904 | 51.7214 | 59.3247 | 142.8322 | 46.1543 | 54.1776 | 142.7758 | 39.6431 | 47.6856 | 142.9588 | 33.3188 | 41.9379 | 143.2822 | 27.4635 | 38.1405 | 128.2631 | 23.269 | 34.0764 | 121.0661 | 21.9633 | 29.9651 | 117.3207 | 21.2838 | 27.1542 | 113.4611 | 20.5837 | 24.3614 | 108.2809 | 19.6439 | 19.7026 | 103.6863 | 18.8104 | 12.116 | 131.1877 | 23.7995 | 8.6071 | 152.3453 | 34.0527 | 7.3002 | 152.418 | 38.5078 | 7.7822 | 142.0209 | 51.4165 | 59.3814 | 142.6987 | 45.6781 | 54.2833 | 142.6028 | 39.3604 | 47.8524 | 142.7596 | 33.4055 | 42.1561 | 143.0693 | 27.9896 | 38.4437 | 130.7409 | 23.7185 | 34.462 | 122.9248 | 22.3005 | 30.3212 | 118.4472 | 21.4882 | 27.4659 | 114.233 | 20.7237 | 24.8085 | 107.4138 | 19.4866 | 20.4787 | 90.7873 | 16.4703 | 10.2508 | 92.1532 | 16.7181 | -8.2562 | 135.0911 | 24.5077 | -20.928 | 146.8152 | 26.6346 | -28.6436 | 141.9911 | 51.4474 | 59.4479 | 142.6584 | 48.9361 | 54.3518 | 142.5491 | 45.6829 | 47.9783 | 142.6763 | 42.6713 | 42.4076 | 142.9658 | 40.0957 | 38.7805 | 143.4305 | 38.5221 | 34.9589 | 143.958 | 36.9139 | 31.0276 | 144.5166 | 36.1573 | 28.4106 | 145.1456 | 35.3242 | 25.5973 | 149.7317 | 33.2896 | 16.4111 | 153.8117 | 33.2773 | -4.268 | 155.5369 | 28.884 | -19.5695 | 148.794 | 26.9936 | -27.7405 | 146.9241 | 26.6544 | -24.1146
LOWER DARWEN | ROCHDALE | 369695 | 424981 | 77.1773 | 14.0012 | 54.6795 | 58.7936 | 10.6661 | 51.9447 | 42.3404 | 7.6812 | 42.3404 | 25.8708 | 4.6934 | 25.8708 | 11.2194 | 2.0354 | 11.2194 | -4.3768 | -0.79402 | -4.3768 | -6.9208 | -1.2555 | -6.9208 | -9.2396 | -1.6762 | -9.2396 | -12.0173 | -2.1801 | -12.0173 | -15.4708 | -2.8066 | -15.4708 | -22.3739 | -4.059 | -22.3739 | 25.5871 | 4.6419 | 21.3933 | 106.6452 | 23.5544 | 20.1461 | 112.3792 | 27.9995 | 20.6526 | 79.0573 | 14.3423 | 56.7244 | 62.5962 | 11.3559 | 55.7535 | 46.6465 | 8.4624 | 46.6465 | 30.6837 | 5.5665 | 30.6837 | 16.6755 | 3.0252 | 16.6755 | 2.1506 | 0.39016 | 2.1506 | 0.30779 | 0.055839 | 0.30779 | -1.2933 | -0.23463 | -1.2933 | -3.0323 | -0.5501 | -3.0323 | -5.0921 | -0.92379 | -5.0921 | -4.5356 | -0.82283 | -4.5356 | 33.1317 | 6.0106 | 31.5501 | 100.1202 | 18.1634 | 29.385 | 114.726 | 20.8131 | 28.5396 | 78.9584 | 14.3243 | 54.7226 | 62.6023 | 11.3571 | 52.0487 | 46.6609 | 8.465 | 46.6609 | 30.7418 | 5.5771 | 30.7418 | 16.5744 | 3.0069 | 16.5744 | 2.6062 | 0.47281 | 2.6062 | 0.38099 | 0.069117 | 0.38099 | -1.7589 | -0.3191 | -1.7589 | -4.0265 | -0.73048 | -4.0265 | -6.6448 | -1.2055 | -6.6448 | -6.9453 | -1.26 | -6.9453 | 49.9201 | 9.0563 | 24.1531 | 126.868 | 28.851 | 23.2638 | 133.857 | 33.9158 | 24.2227 | 77.1675 | 13.9994 | 54.7586 | 58.7625 | 10.6605 | 52.0805 | 42.1239 | 7.6419 | 42.1239 | 25.4882 | 4.624 | 25.4882 | 10.8138 | 1.9618 | 10.8138 | -4.6732 | -0.84779 | -4.6732 | -7.5006 | -1.3607 | -7.5006 | -10.3537 | -1.8783 | -10.3537 | -13.378 | -2.427 | -13.378 | -17.0846 | -3.0994 | -17.0846 | -30.1814 | -5.4754 | -30.1814 | -1.3288 | -0.24107 | -1.3288 | 81.4648 | 15.1222 | -19.3946 | 81.1445 | 17.2165 | -31.5846 | 77.2773 | 14.0193 | 54.8043 | 73.4897 | 13.3322 | 52.0942 | 70.2033 | 12.736 | 51.1998 | 65.5545 | 11.8926 | 50.5859 | 62.2547 | 11.294 | 49.4622 | 55.9868 | 10.1569 | 48.2045 | 51.3966 | 9.3242 | 46.7561 | 49.6059 | 8.9993 | 45.279 | 47.0955 | 8.5439 | 42.5675 | 42.1405 | 7.645 | 34.0729 | 113.1005 | 25.3662 | 4.4317 | 97.1928 | 20.4016 | -18.1747 | 89.8057 | 19.0969 | -30.641 | 87.8727 | 18.7541 | -25.8942
LYTHAM | PENWORTHAM WEST / STANAH | 335361 | 429316 | 56.4183 | 56.4183 | 33.7342 | 56.6383 | 56.6383 | 32.917 | 56.8159 | 55.6652 | 32.1238 | 57.1143 | 54.5079 | 31.1738 | 57.4612 | 53.3574 | 30.0428 | 57.8647 | 52.1469 | 28.8342 | 58.2035 | 51.7099 | 27.561 | 58.522 | 51.2604 | 26.2672 | 58.849 | 50.7861 | 24.9656 | 59.2009 | 50.2949 | 23.5266 | 60.6057 | 48.3157 | 18.6202 | 61.6293 | 46.6083 | 16.0717 | 62.2449 | 46.4344 | 15.3622 | 62.6395 | 46.3467 | 15.5612 | 56.3395 | 56.3395 | 33.8989 | 56.5078 | 56.5078 | 33.2191 | 56.7477 | 56.7477 | 32.299 | 57.0479 | 56.9649 | 31.4136 | 57.3823 | 56.6354 | 30.3951 | 57.7493 | 56.2718 | 29.2729 | 58.1035 | 55.9495 | 28.0601 | 58.4189 | 55.6336 | 26.8095 | 58.7483 | 55.3133 | 25.5184 | 59.0881 | 54.9677 | 24.2087 | 59.8877 | 54.0179 | 20.396 | 60.54 | 53.2254 | 17.652 | 60.9924 | 52.6346 | 16.0102 | 61.2938 | 52.8273 | 14.8817 | 56.4184 | 56.4184 | 33.7558 | 56.6384 | 56.0914 | 33.0121 | 56.8162 | 54.1737 | 32.2932 | 57.1148 | 52.1577 | 31.3905 | 57.4604 | 50.1455 | 30.3189 | 57.8632 | 48.0866 | 29.1688 | 58.2013 | 47.6268 | 27.952 | 58.5193 | 47.2072 | 26.7132 | 58.8428 | 46.7784 | 25.4865 | 59.1794 | 46.3282 | 24.194 | 60.4969 | 44.5955 | 19.7817 | 61.4062 | 43.7946 | 17.582 | 61.9642 | 43.4104 | 16.9966 | 62.2943 | 43.7553 | 17.2394 | 56.4073 | 56.4073 | 33.7636 | 56.632 | 56.632 | 32.9741 | 56.8571 | 56.0887 | 32.231 | 57.2327 | 54.7799 | 31.3167 | 57.6576 | 53.5064 | 30.2664 | 58.0157 | 52.1579 | 29.1236 | 58.4298 | 51.5955 | 27.8773 | 58.8843 | 51.0693 | 26.6301 | 59.3723 | 50.5351 | 25.5126 | 59.9077 | 49.9591 | 24.4075 | 61.8375 | 47.1792 | 18.3333 | 63.454 | 44.5184 | 7.3044 | 64.1163 | 42.3828 | -0.69049 | 64.3762 | 41.1823 | -6.3168 | 56.413 | 56.413 | 33.7225 | 56.6925 | 56.6925 | 32.8167 | 56.9435 | 55.7988 | 32.0744 | 57.2798 | 54.577 | 31.2462 | 57.589 | 53.3972 | 30.2833 | 57.9449 | 52.081 | 29.2952 | 58.3296 | 51.5521 | 28.2224 | 58.7407 | 51.0323 | 27.1875 | 59.2058 | 50.4954 | 26.0616 | 59.8842 | 49.6302 | 23.2624 | 61.807 | 46.133 | 10.3207 | 62.8526 | 42.9937 | 0.43009 | 63.053 | 41.5573 | -4.9668 | 62.6966 | 40.7791 | -3.2335
MACCLESFIELD | MACCLESFIELD | 392047 | 374564 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -2.7611 | 10.6707 | 1.9358 | -16.9513 | 10.6707 | 1.9358 | -26.5048 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -1.4251 | 10.6707 | 1.9358 | -10.6239 | 10.6707 | 1.9358 | -7.6161
MOSS NOOK | SOUTH MANCHESTER | 384073 | 385068 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.2192 | 1.9358 | 9.2192 | 6.3248 | 1.9358 | 6.3248 | 3.8491 | 1.581 | 3.8491 | 1.6428 | 0.67478 | 1.6428 | -1.4613 | -0.60024 | -1.4613 | -3.9816 | -1.6354 | -3.9816 | -14.8478 | -6.0986 | -14.8478 | -21.2227 | -8.7171 | -21.2227 | -11.2396 | -4.6166 | -11.2396 | -10.7449 | -4.4134 | -10.7449 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.7682 | 1.9358 | 8.7682 | 7.1178 | 1.9358 | 7.1178 | 5.7567 | 1.9358 | 5.7567 | 4.3498 | 1.7867 | 4.3498 | 2.8568 | 1.1734 | 2.8568 | -2.3671 | -0.97229 | -2.3671 | -5.7354 | -2.3558 | -5.7354 | 2.8458 | 1.1689 | 2.8458 | 10.6707 | 1.9358 | 4.0079 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.6957 | 1.9358 | 9.6957 | 7.0375 | 1.9358 | 7.0375 | 4.9555 | 1.9358 | 4.9555 | 3.1398 | 1.2896 | 3.1398 | 1.2401 | 0.50937 | 1.2401 | -0.74992 | -0.30802 | -0.74992 | -8.264 | -3.3944 | -8.264 | -12.2998 | -5.052 | -12.2998 | 0.85697 | 0.35199 | -0.88413 | 1.8366 | 0.75436 | -0.59367 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.0561 | 1.9358 | 9.0561 | 6.0703 | 1.9358 | 6.0703 | 3.4163 | 1.4032 | 3.4163 | 1.0189 | 0.41852 | 1.0189 | -2.1709 | -0.89167 | -2.1709 | -4.6907 | -1.9267 | -4.6907 | -18.0749 | -7.4241 | -18.0749 | -34.7494 | -14.2731 | -34.7494 | -34.816 | -14.3004 | -34.816 | -42.0058 | -17.2536 | -42.0058 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.4382 | 1.9358 | 8.4382 | 5.8184 | 1.9358 | 5.8184 | 3.5217 | 1.4465 | 3.5217 | 0.50024 | 0.20547 | 0.50024 | -3.0875 | -1.2682 | -3.0875 | -11.5642 | -4.7499 | -11.5642 | -29.3642 | -12.0611 | -29.3642 | -33.8552 | -13.9058 | -36.0614 | -40.0561 | -16.4528 | -40.0561
NELSON | PADIHAM | 385989 | 438643 | 56.9687 | 10.335 | 29.9606 | 46.6728 | 8.4672 | 27.8423 | 38.3568 | 6.9585 | 27.1021 | 30.0837 | 5.4577 | 26.4677 | 22.3676 | 4.0578 | 22.3676 | 14.9602 | 2.714 | 14.9602 | 11.7338 | 2.1287 | 11.7338 | 8.3365 | 1.5124 | 8.3365 | 4.8391 | 0.87788 | 4.8391 | 1.1831 | 0.21464 | 1.1831 | -14.0005 | -2.5399 | -14.0005 | -20.7076 | -3.7567 | -20.7076 | -17.8201 | -3.2328 | -17.8201 | -22.0496 | -4.0002 | -22.0496 | 58.5423 | 10.6205 | 31.5295 | 49.8752 | 9.0482 | 30.7389 | 41.887 | 7.599 | 29.6862 | 34.1137 | 6.1888 | 28.7925 | 27.6893 | 5.0233 | 27.6893 | 21.3123 | 3.8664 | 21.3123 | 19.0858 | 3.4625 | 19.0858 | 16.781 | 3.0443 | 16.781 | 14.4961 | 2.6298 | 14.4961 | 12.1561 | 2.2053 | 12.1561 | 5.5887 | 1.0139 | 5.5887 | 2.9997 | 0.54419 | 2.9997 | 6.873 | 1.2469 | 6.873 | 5.2776 | 0.95745 | 5.2776 | 58.4789 | 10.609 | 30.0084 | 49.5739 | 8.9935 | 27.9476 | 41.1487 | 7.465 | 27.2662 | 32.6677 | 5.9264 | 26.6888 | 25.282 | 4.5866 | 25.282 | 18.025 | 3.27 | 18.025 | 14.8718 | 2.698 | 14.8718 | 11.5024 | 2.0867 | 11.5024 | 8.1157 | 1.4723 | 8.1157 | 4.6677 | 0.8468 | 4.6677 | -7.858 | -1.4256 | -7.858 | -12.8707 | -2.335 | -12.8707 | -6.9359 | -1.2583 | -6.9359 | -13.3263 | -2.4176 | -13.3263 | 56.9748 | 10.3361 | 30.0402 | 46.476 | 8.4315 | 27.9759 | 37.8519 | 6.8669 | 27.2852 | 29.4949 | 5.3508 | 26.7023 | 21.664 | 3.9302 | 21.664 | 14.0418 | 2.5474 | 14.0418 | 10.4505 | 1.8959 | 10.4505 | 6.7728 | 1.2287 | 6.7728 | 3.0505 | 0.55341 | 3.0505 | -0.67481 | -0.12242 | -0.67481 | -21.5359 | -3.907 | -21.5359 | -45.2297 | -8.2054 | -45.2297 | -57.6515 | -10.4589 | -57.6515 | -71.5188 | -12.9746 | -71.5188 | 57.1052 | 10.3598 | 30.1294 | 54.198 | 9.8324 | 28.0967 | 51.6367 | 9.3677 | 27.4751 | 48.1257 | 8.7308 | 27.0287 | 44.397 | 8.0543 | 26.2713 | 40.3481 | 7.3198 | 25.3101 | 36.4648 | 6.6153 | 24.2132 | 32.6357 | 5.9206 | 23.1206 | 28.1379 | 5.1047 | 21.5183 | 20.5765 | 3.7329 | 16.7729 | -15.3744 | -2.7892 | -15.3744 | -46.134 | -8.3694 | -46.134 | -63.603 | -11.5386 | -63.603 | -69.0972 | -12.5353 | -69.0972
NEW MILLS | STALYBRIDGE | 401141 | 383916 | 40.0178 | 40.0178 | 40.0178 | 40.2341 | 40.2341 | 40.2341 | 40.4897 | 40.4897 | 40.4897 | 40.798 | 40.798 | 39.9189 | 41.1539 | 41.1539 | 39.0023 | 41.5575 | 41.5575 | 37.9727 | 42.0102 | 42.0102 | 36.8148 | 42.4695 | 42.4695 | 35.6213 | 43.0574 | 43.0574 | 34.3245 | 43.5093 | 43.5093 | 32.9209 | 45.4646 | 45.4646 | 28.0887 | 47.2303 | 47.2303 | 25.7585 | 48.427 | 48.427 | 25.4955 | 49.4315 | 49.4315 | 26.2096 | 40.0266 | 40.0266 | 40.0266 | 40.204 | 40.204 | 40.204 | 40.4102 | 40.4102 | 40.4102 | 40.5779 | 40.5779 | 40.4691 | 40.7793 | 40.7793 | 39.6891 | 41.0106 | 41.0106 | 38.8063 | 41.2735 | 41.2735 | 37.7925 | 41.5542 | 41.5542 | 36.728 | 41.8522 | 41.8522 | 35.616 | 42.1549 | 42.1549 | 34.4808 | 43.2922 | 43.2922 | 31.5178 | 44.3928 | 44.3928 | 29.4529 | 45.0772 | 45.0772 | 28.3049 | 45.6073 | 45.6073 | 27.6223 | 40.0187 | 40.0187 | 40.0187 | 40.2357 | 40.2357 | 40.2357 | 40.4918 | 40.4918 | 40.4918 | 40.8009 | 40.8009 | 40.2086 | 41.1566 | 41.1566 | 39.3194 | 41.5588 | 41.5588 | 38.3208 | 42.0111 | 42.0111 | 37.1942 | 42.4695 | 42.4695 | 36.0311 | 43.0541 | 43.0541 | 34.7803 | 43.4829 | 43.4829 | 33.4773 | 45.2668 | 45.2668 | 28.9376 | 46.6813 | 46.6813 | 26.8825 | 47.6858 | 47.6858 | 26.6897 | 48.4172 | 48.4172 | 27.4898 | 40.0251 | 40.0251 | 40.0251 | 40.289 | 40.289 | 40.289 | 40.6433 | 40.6433 | 40.6433 | 41.0526 | 41.0526 | 40.09 | 41.5772 | 41.5772 | 39.2668 | 42.3838 | 42.3838 | 38.1515 | 42.9442 | 42.9442 | 37.0648 | 43.5486 | 43.5486 | 35.9477 | 44.2241 | 44.2241 | 34.9908 | 44.9857 | 44.9857 | 34.025 | 51.0252 | 51.0252 | 26.1669 | 53.5464 | 51.0282 | 17.1244 | 54.8627 | 52.7838 | 11.6334 | 54.8382 | 51.4361 | 7.4013 | 40.0875 | 40.0875 | 40.0875 | 40.3932 | 40.3932 | 40.3932 | 40.7366 | 40.7366 | 40.601 | 41.1896 | 41.1896 | 39.9758 | 41.9303 | 41.9303 | 39.0568 | 42.5111 | 42.5111 | 38.2629 | 43.046 | 43.046 | 37.3294 | 47.1993 | 47.1993 | 32.8616 | 47.7033 | 47.7033 | 32.2269 | 48.343 | 48.343 | 30.6559 | 51.1505 | 51.1505 | 20.8541 | 53.2234 | 53.2234 | 13.4864 | 53.867 | 52.097 | 10.1877 | 53.7726 | 51.5044 | 11.4793
ORRELL | WASHWAY FARM / KIRKBY | 352784 | 404565 | 142.2823 | 54.4945 | 68.3624 | 145.2503 | 53.3294 | 66.8808 | 145.4125 | 52.2269 | 65.9775 | 145.6991 | 51.1477 | 64.8867 | 146.0759 | 50.1029 | 63.4606 | 146.5221 | 48.9319 | 61.769 | 147.0227 | 48.2525 | 59.9258 | 147.5621 | 47.6162 | 58.0525 | 148.1294 | 46.9619 | 56.208 | 148.8275 | 46.2752 | 54.1561 | 160.1689 | 42.5728 | 38.756 | 164.2524 | 42.9468 | 34.0431 | 166.7184 | 48.1864 | 32.5336 | 168.4669 | 51.3132 | 32.8872 | 142.0549 | 54.6764 | 69.2254 | 144.7796 | 53.562 | 68.495 | 145.0433 | 52.3675 | 67.3929 | 145.3356 | 51.2138 | 66.3504 | 145.6754 | 50.0914 | 65.1165 | 146.0586 | 49.0613 | 63.6562 | 146.4867 | 48.5808 | 62.0352 | 146.9094 | 48.1349 | 60.3671 | 147.3509 | 47.6918 | 58.6589 | 147.8048 | 47.2489 | 56.9559 | 149.7622 | 45.8136 | 51.6744 | 151.6254 | 46.1454 | 48.0158 | 153.2814 | 49.7119 | 45.9016 | 154.5781 | 51.7438 | 44.4946 | 142.2828 | 54.674 | 68.3735 | 145.2582 | 53.5855 | 66.9234 | 145.4234 | 52.2416 | 66.0536 | 145.7115 | 50.9185 | 64.9959 | 146.0887 | 49.656 | 63.6148 | 146.5342 | 48.4588 | 62.003 | 147.033 | 47.7792 | 60.1975 | 147.5698 | 47.1204 | 58.36 | 148.1283 | 46.4435 | 56.5793 | 148.7969 | 45.7587 | 54.689 | 159.7374 | 43.0062 | 39.9111 | 162.8067 | 42.8462 | 36.1169 | 164.8457 | 47.5894 | 35.0351 | 165.7627 | 49.9877 | 35.9167 | 142.2679 | 54.4989 | 68.4244 | 145.2557 | 53.3229 | 67.0099 | 145.4815 | 51.9934 | 66.1988 | 145.8499 | 50.7904 | 65.2265 | 146.3364 | 49.6311 | 64.0001 | 147.0111 | 48.3725 | 62.573 | 147.8676 | 47.5438 | 60.945 | 148.8529 | 46.7049 | 59.2726 | 149.9227 | 45.99 | 57.8271 | 151.128 | 45.3379 | 56.3445 | 165.3758 | 40.3725 | 38.5488 | 174.2863 | 38.1537 | 17.6701 | 177.5502 | 41.976 | 4.4331 | 178.2807 | 44.3985 | -3.5184 | 142.2669 | 54.5322 | 68.3718 | 145.3071 | 53.9968 | 66.8203 | 145.5341 | 53.3635 | 65.9977 | 145.8848 | 53.0282 | 65.123 | 146.3947 | 52.5445 | 63.9907 | 147.1391 | 51.7766 | 62.7106 | 148.0711 | 51.0351 | 61.2606 | 149.1495 | 50.4148 | 59.8162 | 150.4627 | 49.7768 | 58.1124 | 161.6745 | 47.2183 | 44.1671 | 166.6059 | 47.4161 | 25.4642 | 171.0421 | 43.3176 | 10.1405 | 172.9161 | 46.1555 | 1.6415 | 172.3944 | 45.6345 | 4.9294
PADIHAM | PADIHAM | 378571 | 433224 | 155.8601 | 45.1408 | 55.341 | 156.6452 | 43.9786 | 52.3091 | 156.865 | 43.0681 | 50.6482 | 157.2009 | 42.095 | 49.3159 | 158.7373 | 41.0639 | 46.2052 | 159.2618 | 40.0622 | 44.0072 | 159.8504 | 39.3354 | 41.6044 | 160.4818 | 38.557 | 39.1053 | 164.0003 | 37.338 | 33.5836 | 164.7135 | 36.4947 | 30.3601 | 174.3942 | 32.6046 | 12.3977 | 162.6292 | 29.5035 | -6.871 | 164.8063 | 29.8985 | -8.9834 | 155.5429 | 28.218 | -8.4543 | 155.6055 | 45.4643 | 56.8923 | 156.1171 | 44.6935 | 55.3004 | 156.5523 | 43.9836 | 53.6916 | 157.0294 | 43.3694 | 52.1845 | 157.5598 | 42.7157 | 50.4095 | 158.1476 | 41.9826 | 48.4154 | 158.8024 | 41.4676 | 46.2058 | 159.5041 | 40.9201 | 43.8899 | 160.2555 | 40.3994 | 41.4855 | 161.0526 | 39.8562 | 39.027 | 162.9646 | 38.1898 | 31.2188 | 164.8902 | 36.8757 | 24.6582 | 166.6812 | 37.4267 | 20.1296 | 168.1281 | 37.9225 | 17.0739 | 155.8627 | 45.4495 | 55.3768 | 156.6495 | 44.6288 | 52.423 | 156.8706 | 43.8676 | 50.8481 | 157.2094 | 43.0487 | 49.6825 | 158.7478 | 42.2012 | 46.6738 | 159.2726 | 41.2806 | 44.5774 | 159.8613 | 40.5626 | 42.267 | 160.4929 | 39.8595 | 39.7361 | 164.0048 | 39.1836 | 34.3525 | 164.6867 | 38.5151 | 31.4328 | 173.9863 | 35.8768 | 14.6709 | 186.5989 | 33.852 | -3.3969 | 190.1079 | 34.4886 | -4.9545 | 178.4647 | 32.3763 | -3.9629 | 155.8384 | 45.1411 | 55.3674 | 156.6188 | 43.924 | 52.2799 | 156.8722 | 43.0105 | 50.5259 | 157.2805 | 42.0411 | 49.2702 | 158.9314 | 41.0203 | 46.192 | 159.6668 | 39.9861 | 43.966 | 160.573 | 39.1984 | 41.4409 | 161.6439 | 38.3771 | 38.8287 | 165.5814 | 37.1663 | 33.7316 | 167.0693 | 36.2454 | 31.1793 | 169.6958 | 30.7855 | 4.6367 | 142.5794 | 25.8662 | -17.1796 | 131.7257 | 23.8971 | -30.9347 | 114.9003 | 20.8447 | -40.9003 | 155.9979 | 45.1573 | 55.3507 | 156.6479 | 44.3379 | 52.1584 | 156.8975 | 43.5513 | 50.4038 | 157.2885 | 42.7165 | 49.0979 | 158.9233 | 41.8155 | 46.0792 | 159.6901 | 40.863 | 44.0345 | 163.7957 | 39.9456 | 38.6239 | 165.04 | 39.0379 | 36.2373 | 167.8637 | 38.0034 | 32.3615 | 169.287 | 36.7791 | 27.4607 | 173.7013 | 31.5122 | -10.3517 | 141.8856 | 25.7403 | -26.3582 | 125.2683 | 22.7257 | -35.957 | 115.8116 | 21.0101 | -34.1909
PEEL | PENWORTHAM WEST / STANAH | 335644 | 432080 | 22.4601 | 22.4601 | 22.3765 | 22.8448 | 22.8448 | 21.2187 | 23.0642 | 23.0642 | 20.8579 | 23.267 | 23.267 | 20.259 | 23.5439 | 23.5439 | 19.4634 | 23.8794 | 23.8794 | 18.5349 | 24.2234 | 24.2234 | 17.5141 | 24.647 | 24.647 | 16.4023 | 25.0116 | 25.0116 | 15.4014 | 25.4091 | 25.4091 | 14.2623 | 27.0805 | 27.0805 | 9.6381 | 28.5534 | 28.5534 | 6.6049 | 29.1977 | 29.1977 | 5.5366 | 29.6111 | 29.6111 | 5.54 | 22.2517 | 22.2517 | 22.2517 | 22.4333 | 22.4333 | 22.4333 | 22.6591 | 22.6591 | 22.143 | 22.9246 | 22.9246 | 21.3396 | 23.22 | 23.22 | 20.4704 | 23.5372 | 23.5372 | 19.4388 | 23.8825 | 23.8825 | 18.3328 | 24.2417 | 24.2417 | 17.1981 | 24.6111 | 24.6111 | 16.0149 | 24.9814 | 24.9814 | 14.3984 | 25.894 | 25.894 | 12.1065 | 26.6466 | 26.6466 | 10.2601 | 27.1499 | 27.1499 | 8.8487 | 27.4308 | 27.4308 | 8.0887 | 22.4602 | 22.4602 | 22.4136 | 22.8451 | 22.8451 | 21.2839 | 23.0667 | 23.0667 | 20.9085 | 23.2699 | 23.2699 | 20.34 | 23.5463 | 23.5463 | 19.5918 | 23.88 | 23.88 | 18.6918 | 24.2221 | 24.2221 | 17.7053 | 24.6436 | 24.6436 | 16.6653 | 25.0024 | 25.0024 | 15.7291 | 25.3804 | 25.3804 | 14.6972 | 26.9296 | 26.9296 | 10.6651 | 28.2326 | 28.2326 | 8.0737 | 28.7602 | 28.7602 | 7.2111 | 29.0468 | 29.0468 | 7.2753 | 22.4403 | 22.4403 | 22.4403 | 22.8042 | 22.8042 | 21.3628 | 23.049 | 23.049 | 20.9884 | 23.2927 | 23.2927 | 20.4003 | 23.6102 | 23.6102 | 19.6084 | 24.0868 | 24.0868 | 18.5312 | 24.562 | 24.562 | 17.3418 | 25.0911 | 25.0911 | 16.1211 | 25.6643 | 25.6643 | 14.9909 | 26.2733 | 26.2733 | 13.8353 | 29.3638 | 29.3638 | 7.3263 | 31.1483 | 31.1483 | -1.2498 | 31.7956 | 31.7956 | -6.7791 | 31.9907 | 31.9907 | -10.7289 | 22.4788 | 22.4788 | 22.4317 | 22.9255 | 22.9255 | 21.2764 | 23.0973 | 23.0973 | 20.8683 | 23.3266 | 23.3266 | 20.291 | 23.6971 | 23.6971 | 19.4362 | 24.0843 | 24.0843 | 18.4505 | 24.5526 | 24.5526 | 17.3626 | 26.5044 | 26.5044 | 14.8449 | 26.9813 | 26.9813 | 13.8588 | 27.928 | 27.928 | 11.4377 | 29.6435 | 29.6435 | 2.1526 | 30.6695 | 30.6695 | -4.6583 | 30.8701 | 30.8701 | -8.0951 | 30.5308 | 30.5308 | -6.9331
PENRITH & SHAP | HARKER / HUTTON | 349996 | 530398 | 129.2274 | 56.6311 | 50.7241 | 129.7001 | 54.5768 | 48.729 | 129.849 | 52.7604 | 47.4219 | 130.1679 | 50.6893 | 45.8746 | 130.587 | 48.7275 | 44.1756 | 131.1225 | 45.7827 | 42.2834 | 131.7439 | 43.9367 | 40.1552 | 132.4144 | 42.1922 | 37.9842 | 133.1345 | 40.3598 | 35.6077 | 133.9571 | 38.558 | 32.2313 | 144.5795 | 34.1363 | 12.4599 | 138.5827 | 31.5428 | -1.6935 | 133.6511 | 30.9014 | -6.3782 | 126.8705 | 29.1085 | -6.3613 | 128.9667 | 56.8431 | 51.5656 | 129.2733 | 55.557 | 50.2976 | 129.752 | 54.3119 | 48.6371 | 130.3488 | 52.8983 | 47.0977 | 131.0246 | 51.6074 | 45.3672 | 131.7859 | 50.1298 | 43.41 | 132.6557 | 49.3267 | 41.1737 | 133.6074 | 48.6345 | 38.8387 | 134.6416 | 47.9041 | 36.4066 | 135.7681 | 47.1426 | 33.8494 | 138.2397 | 45.142 | 26.444 | 141.1245 | 43.8076 | 17.6388 | 144.0087 | 43.3609 | 10.2834 | 146.4135 | 42.1366 | 5.1166 | 129.2326 | 56.825 | 50.7793 | 129.7094 | 54.9127 | 48.8848 | 129.8634 | 53.0197 | 47.6856 | 130.1881 | 50.805 | 46.2467 | 130.6126 | 48.7307 | 44.6478 | 131.1501 | 46.3116 | 42.8545 | 131.7714 | 44.9517 | 40.8249 | 132.4405 | 43.9132 | 38.7519 | 133.1514 | 42.7538 | 36.5005 | 133.9408 | 41.5559 | 33.3489 | 143.9565 | 38.0428 | 14.9798 | 152.5834 | 35.7252 | 2.8091 | 147.3659 | 35.0022 | -0.93291 | 138.2327 | 32.5894 | -0.035544 | 129.1986 | 56.6293 | 50.7714 | 129.6547 | 54.5192 | 48.6897 | 129.8137 | 52.6291 | 47.3052 | 130.1896 | 50.4701 | 45.6267 | 130.7176 | 48.4137 | 43.6255 | 131.4877 | 45.3311 | 41.2891 | 132.4909 | 43.3078 | 38.4693 | 133.6606 | 41.3894 | 35.6312 | 134.9778 | 39.4013 | 32.9977 | 136.4601 | 37.5113 | 30.3106 | 140.4753 | 31.7949 | 8.4299 | 125.0109 | 27.525 | -15.6252 | 116.1194 | 25.6922 | -26.0326 | 107.3937 | 23.3099 | -31.4124 | 129.1614 | 56.634 | 50.7647 | 129.6141 | 55.6164 | 48.6075 | 129.7684 | 54.5313 | 47.2706 | 130.1211 | 53.0392 | 45.6818 | 130.6428 | 51.5452 | 43.5291 | 131.4686 | 49.116 | 41.1955 | 133.9026 | 47.1447 | 37.2725 | 135.7017 | 45.2977 | 34.2221 | 137.1682 | 43.4436 | 31.7336 | 139.7683 | 41.1933 | 26.1807 | 143.8196 | 33.8575 | -7.922 | 127.3996 | 28.667 | -23.3069 | 116.042 | 25.225 | -29.6932 | 109.2605 | 23.192 | -26.0339
PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 356774 | 432942 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 6.0917 | 1.9358 | 6.0917 | 4.9469 | 1.9358 | 4.9469 | 3.8561 | 1.5839 | 3.8561 | 2.6703 | 1.0968 | 2.6703 | 1.3166 | 0.5408 | 1.3166 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 4.6793 | 1.922 | 4.6793 | 3.1623 | 1.2989 | 3.1623 | 1.6609 | 0.68219 | 1.6609 | 0.031689 | 0.013016 | 0.031689 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 7.1955 | 1.9358 | 7.1955 | 10.6707 | 1.9358 | 9.4657 | 10.6707 | 1.9358 | -1.3239 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 2.2669 | 10.6707 | 1.9358 | 4.0294
RED BANK | WHITEGATE | 384542 | 399276 | 157.4334 | 39.7222 | 50.4194 | 158.0405 | 38.5543 | 45.1424 | 158.0544 | 37.7543 | 42.2031 | 158.2865 | 36.8934 | 39.9445 | 158.6395 | 36.0334 | 38.705 | 159.1157 | 35.185 | 37.1426 | 159.6091 | 34.6003 | 35.5588 | 160.1127 | 34.0124 | 33.9839 | 160.6248 | 33.362 | 32.4129 | 161.1675 | 32.724 | 30.5255 | 163.1266 | 29.9226 | 23.0433 | 155.7374 | 28.2532 | 18.5853 | 161.0805 | 29.2226 | 16.8768 | 163.4004 | 29.6434 | 16.9165 | 156.8803 | 40.1409 | 53.4625 | 157.0493 | 39.2992 | 51.2762 | 157.4315 | 38.514 | 48.8193 | 157.9648 | 37.7688 | 46.7603 | 158.5715 | 37.0608 | 45.1901 | 159.2378 | 36.3394 | 43.4623 | 159.9652 | 35.9125 | 41.519 | 160.7401 | 35.4034 | 39.4191 | 161.5679 | 34.8092 | 37.2357 | 162.4511 | 34.2141 | 34.9721 | 163.7966 | 33.1168 | 29.193 | 164.8922 | 32.3802 | 24.7273 | 165.6381 | 33.2976 | 22.0509 | 166.0315 | 34.0229 | 20.4857 | 157.4337 | 40.1271 | 50.4823 | 158.0411 | 39.1847 | 45.2878 | 158.0557 | 38.2667 | 42.4383 | 158.2886 | 37.3906 | 40.2596 | 158.6417 | 36.5728 | 39.1111 | 159.1173 | 35.749 | 37.6405 | 159.6103 | 35.2308 | 36.1494 | 160.1139 | 34.6249 | 34.6684 | 160.6224 | 33.9301 | 33.213 | 161.1476 | 33.237 | 31.6491 | 162.9596 | 31.6288 | 24.952 | 164.2277 | 31.0284 | 21.102 | 165.0296 | 32.558 | 19.6629 | 165.4731 | 32.5991 | 19.8538 | 157.3786 | 39.7289 | 50.5209 | 157.935 | 38.5501 | 45.3296 | 157.9181 | 37.7337 | 42.451 | 158.147 | 36.8839 | 40.2085 | 158.5201 | 36.0247 | 38.9595 | 159.0575 | 35.1724 | 37.3218 | 159.658 | 34.5541 | 35.5362 | 160.3073 | 33.9281 | 33.711 | 160.9941 | 33.2645 | 31.988 | 161.7311 | 32.6271 | 30.2478 | 161.6066 | 29.318 | 21.7667 | 141.1227 | 25.6019 | 3.8602 | 134.2701 | 24.3587 | -9.6258 | 125.2628 | 22.7247 | -19.1142 | 157.3156 | 39.7457 | 50.579 | 157.8332 | 38.9559 | 45.373 | 157.7729 | 38.3661 | 42.5446 | 157.9321 | 37.626 | 40.4118 | 158.234 | 36.8201 | 39.2536 | 158.6919 | 36.0315 | 37.773 | 159.2247 | 35.3491 | 36.1797 | 159.7956 | 34.6587 | 34.5866 | 160.411 | 34 | 32.9498 | 161.1711 | 32.9995 | 29.085 | 159.1308 | 28.8689 | 9.1301 | 135.0401 | 24.4984 | -7.2676 | 124.4469 | 22.5767 | -16.4297 | 120.4028 | 21.843 | -13.7769
RIBBLE | PENWORTHAM EAST / ROCHDALE | 351794 | 429241 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 4.5078 | 1.8515 | 4.5078 | 5.6149 | 1.9358 | 5.6149 | 0.29984 | 0.12316 | 0.29984 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.4249 | 1.9358 | 9.4249 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -8.6667 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.4937 | 1.9358 | 10.4937 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -3.9579 | 6.7308 | 1.9358 | 2.8385
ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 88.6786 | 40.5179 | 59.2051 | 88.8934 | 38.0414 | 58.0647 | 89.079 | 35.6528 | 57.3133 | 89.3574 | 33.5919 | 56.5493 | 89.7182 | 31.5754 | 55.5914 | 90.1583 | 29.5557 | 54.5355 | 90.6613 | 29.0996 | 53.3846 | 91.211 | 28.7463 | 52.1933 | 91.8093 | 28.4082 | 50.9308 | 92.3285 | 27.9178 | 49.3655 | 94.3799 | 26.4465 | 43.6343 | 96.3243 | 27.3293 | 40.4697 | 97.5074 | 31.5946 | 39.4682 | 98.445 | 32.7219 | 39.178 | 88.6128 | 40.6649 | 59.6409 | 88.7629 | 38.2688 | 58.8827 | 89.0114 | 35.923 | 58.0049 | 89.2823 | 33.9338 | 57.2275 | 89.5904 | 32.0011 | 56.2574 | 89.9398 | 30.0964 | 55.1446 | 90.3341 | 29.7239 | 53.9322 | 90.7623 | 29.4588 | 52.6437 | 91.2225 | 29.2274 | 51.2867 | 91.7073 | 28.8761 | 49.8774 | 93.3396 | 28.3002 | 46.5584 | 94.6538 | 29.1429 | 43.5614 | 95.5095 | 31.5509 | 41.6829 | 96.1647 | 32.0136 | 40.4102 | 88.6869 | 40.656 | 59.1401 | 88.9049 | 38.2092 | 58.0618 | 89.0927 | 35.8346 | 57.3142 | 89.3727 | 33.744 | 56.5902 | 89.7327 | 31.7237 | 55.6834 | 90.1664 | 29.7621 | 54.6805 | 90.6594 | 29.3375 | 53.5828 | 91.196 | 29.0125 | 52.4441 | 91.772 | 28.711 | 51.1249 | 92.2899 | 28.2896 | 49.6466 | 94.1593 | 27.3173 | 44.428 | 95.6769 | 28.5426 | 41.7806 | 96.6881 | 32.4619 | 41.0296 | 97.3339 | 33.7889 | 41.2546 | 88.683 | 40.5247 | 59.2481 | 88.9106 | 38.2871 | 58.1407 | 89.1476 | 35.8983 | 57.3742 | 89.5175 | 33.7987 | 56.6428 | 90.0184 | 31.7487 | 55.7624 | 90.666 | 29.7515 | 54.7802 | 91.4212 | 29.2319 | 53.6582 | 91.9917 | 28.8999 | 52.5011 | 92.6097 | 28.5652 | 51.4569 | 93.2955 | 28.0663 | 50.3978 | 96.3299 | 26.2124 | 43.6904 | 99.2549 | 25.3032 | 31.0588 | 101.084 | 27.7415 | 21.5726 | 101.999 | 27.2777 | 15.3685 | 88.6777 | 40.5655 | 59.2415 | 88.9446 | 40.3414 | 58.0903 | 89.2101 | 39.8771 | 57.3779 | 89.5822 | 39.534 | 56.74 | 90.0827 | 38.9992 | 55.9441 | 90.736 | 38.2545 | 55.0994 | 91.3748 | 37.5907 | 54.1278 | 91.9456 | 37.1481 | 53.15 | 92.6207 | 36.6763 | 51.9616 | 93.5799 | 35.749 | 48.9829 | 96.6627 | 31.6193 | 34.7826 | 99.008 | 28.6737 | 23.5666 | 100.1237 | 27.4782 | 17.3164 | 100.1676 | 27.308 | 18.9862
ROSSENDALE | PADIHAM | 380261 | 422010 | 127.3007 | 72.2384 | 73.9425 | 127.7812 | 70.2113 | 72.2068 | 128.076 | 68.5912 | 70.9111 | 128.5344 | 66.9968 | 69.3852 | 129.1415 | 65.4505 | 67.4844 | 129.8853 | 63.8917 | 65.3398 | 130.7367 | 63.3387 | 63.0164 | 131.6714 | 62.7917 | 60.6009 | 135.5768 | 61.7037 | 55.2596 | 136.5104 | 61.0767 | 52.5328 | 141.2448 | 58.6019 | 42.3178 | 144.5588 | 58.0937 | 37.222 | 146.7432 | 59.4824 | 36.2531 | 148.6795 | 59.4517 | 37.1067 | 127.0225 | 72.5247 | 74.6837 | 127.276 | 70.8849 | 73.5579 | 127.719 | 69.2391 | 71.905 | 128.2232 | 67.7476 | 70.3342 | 128.7896 | 66.3324 | 68.5261 | 129.4193 | 64.9539 | 66.5109 | 130.1207 | 64.5912 | 64.2927 | 130.874 | 64.2166 | 61.9636 | 131.6766 | 63.8298 | 59.5426 | 132.5188 | 63.4258 | 57.0656 | 134.7529 | 62.362 | 50.1256 | 136.7229 | 62.3167 | 45.1675 | 138.4033 | 63.6067 | 42.159 | 139.7135 | 63.6129 | 40.2578 | 127.3013 | 72.5182 | 73.99 | 127.7828 | 70.863 | 72.3183 | 128.0791 | 69.1549 | 71.0887 | 128.5396 | 67.5595 | 69.6269 | 129.1462 | 66.0405 | 67.8048 | 129.8875 | 64.5234 | 65.7441 | 130.7369 | 64.0538 | 63.5037 | 131.6706 | 63.5814 | 61.1694 | 135.5636 | 63.0852 | 55.852 | 136.4398 | 62.5406 | 53.2409 | 140.7853 | 60.7595 | 43.9786 | 143.4524 | 60.7462 | 39.7488 | 145.2581 | 62.4059 | 39.0623 | 146.573 | 62.3806 | 40.1394 | 127.2783 | 72.2467 | 74.0004 | 127.7732 | 70.209 | 72.3291 | 128.1642 | 68.6127 | 71.1374 | 128.7948 | 66.9801 | 69.7364 | 129.669 | 65.4115 | 68.0511 | 130.8077 | 63.8177 | 66.15 | 132.2075 | 63.1795 | 64.0276 | 133.8325 | 62.5381 | 61.841 | 138.3545 | 61.3954 | 57.2104 | 140.0358 | 60.6928 | 55.4322 | 150.4257 | 56.6433 | 38.7099 | 156.0914 | 53.2548 | 12.7214 | 158.94 | 51.6284 | -6.6087 | 160.2678 | 49.423 | -18.966 | 127.2897 | 72.2652 | 74.0035 | 127.8866 | 71.8046 | 72.1906 | 128.3348 | 71.5849 | 71.0659 | 128.9641 | 71.1786 | 69.9009 | 129.8286 | 70.6097 | 68.4523 | 130.9334 | 69.9488 | 66.8868 | 135.1865 | 68.7575 | 62.2503 | 136.5972 | 68.0498 | 60.6362 | 138.2331 | 67.3152 | 58.4592 | 139.9557 | 66.1475 | 52.2469 | 147.0629 | 60.7973 | 22.1253 | 151.4098 | 55.3703 | -1.0489 | 152.8017 | 51.3088 | -13.521 | 152.3166 | 50.034 | -8.6731
ROYTON | WHITEGATE | 392426 | 407533 | -19.1789 | -3.4794 | -19.1789 | -49.0911 | -8.9059 | -49.0911 | -78.2201 | -14.1904 | -78.2201 | -107.7772 | -19.5525 | -107.7772 | -137.1461 | -24.8805 | -137.1461 | -166.5169 | -30.2088 | -166.5169 | -168.2846 | -30.5295 | -168.2846 | -170.301 | -30.8953 | -170.301 | -172.5188 | -31.2977 | -172.5188 | -174.8311 | -31.7171 | -174.8311 | -175.3173 | -31.8054 | -175.3173 | -128.4742 | -23.3073 | -128.4742 | 47.5352 | 8.6236 | 47.5352 | 63.991 | 11.609 | 63.991 | -18.5134 | -3.3586 | -18.5134 | -49.9412 | -9.0601 | -49.9412 | -80.8759 | -14.6722 | -80.8759 | -111.9808 | -20.3151 | -111.9808 | -142.8558 | -25.9163 | -142.8558 | -173.8486 | -31.5389 | -173.8486 | -174.8734 | -31.7248 | -174.8734 | -176.1801 | -31.9619 | -176.1801 | -177.6442 | -32.2275 | -177.6442 | -179.0585 | -32.4841 | -179.0585 | -178.9794 | -32.4697 | -178.9794 | -151.1359 | -27.4185 | -151.1359 | -35.3409 | -6.4114 | -35.3409 | 45.6045 | 8.2734 | 45.6045 | -18.561 | -3.3673 | -18.561 | -51.3662 | -9.3186 | -51.3662 | -83.7423 | -15.1922 | -83.7423 | -116.2987 | -21.0984 | -116.2987 | -148.5581 | -26.9508 | -148.5581 | -180.8602 | -32.8109 | -180.8602 | -182.1365 | -33.0425 | -182.1365 | -183.6877 | -33.3239 | -183.6877 | -185.4537 | -33.6443 | -185.4537 | -187.2166 | -33.9641 | -187.2166 | -182.7238 | -33.149 | -182.7238 | -126.9546 | -23.0316 | -126.9546 | 72.4071 | 13.1358 | 72.4071 | 85.953 | 16.0372 | 80.4619 | -19.1802 | -3.4796 | -19.1802 | -49.1704 | -8.9203 | -49.1704 | -78.4143 | -14.2256 | -78.4143 | -107.936 | -19.5813 | -107.936 | -137.335 | -24.9148 | -137.335 | -166.7817 | -30.2569 | -166.7817 | -168.7452 | -30.6131 | -168.7452 | -170.9654 | -31.0158 | -170.9654 | -173.2148 | -31.4239 | -173.2148 | -175.5633 | -31.85 | -175.5633 | -179.4362 | -32.5526 | -179.4362 | -144.529 | -26.2199 | -144.529 | 19.1926 | 3.4818 | 19.1926 | 25.5402 | 4.6334 | 25.5402 | -19.0856 | -3.4624 | -19.0856 | -22.3265 | -4.0504 | -22.3265 | -25.296 | -4.5891 | -25.296 | -28.97 | -5.2556 | -28.97 | -32.7483 | -5.9411 | -32.7483 | -36.4944 | -6.6207 | -36.4944 | -38.5787 | -6.9988 | -38.5787 | -38.7626 | -7.0322 | -38.7626 | -38.7375 | -7.0276 | -38.7375 | -39.6476 | -7.1927 | -39.6476 | 58.585 | 10.6282 | 58.585 | 40.0628 | 7.268 | 40.0628 | 28.4619 | 5.1634 | 28.4619 | 27.1023 | 4.9168 | 27.1023
SALE | CARRINGTON | 378726 | 392892 | 103.5077 | 56.8078 | 36.4899 | 103.8272 | 55.6426 | 35.2778 | 103.939 | 54.6481 | 34.2811 | 104.2067 | 53.6391 | 33.0685 | 104.5681 | 52.674 | 31.5731 | 105.0151 | 51.5963 | 29.8357 | 105.5038 | 51.0944 | 27.97 | 106.0292 | 50.703 | 26.0363 | 106.5897 | 50.0424 | 24.0289 | 107.2087 | 49.5209 | 21.7066 | 110.0064 | 47.3022 | 13.5735 | 112.591 | 45.975 | 9.2556 | 114.1915 | 49.4429 | 8.018 | 115.4311 | 51.0572 | 8.406 | 103.2725 | 56.8233 | 36.8708 | 103.4025 | 55.6586 | 35.9981 | 103.6732 | 54.6129 | 34.8409 | 104.0419 | 53.7101 | 33.7024 | 104.4415 | 52.9194 | 32.3674 | 104.8882 | 52.0458 | 30.8587 | 105.3793 | 51.7018 | 29.217 | 105.8896 | 51.4757 | 27.4991 | 106.4039 | 51.0094 | 25.6995 | 106.94 | 50.6882 | 23.8475 | 108.5042 | 49.7558 | 18.0534 | 109.946 | 49.2453 | 13.716 | 111.0607 | 51.4144 | 11.0771 | 111.8661 | 53.4246 | 9.3791 | 103.5119 | 56.8132 | 36.5675 | 103.834 | 55.5921 | 35.4634 | 103.9462 | 54.4684 | 34.5743 | 104.2139 | 53.4698 | 33.4265 | 104.575 | 52.5931 | 31.9527 | 105.0194 | 51.6542 | 30.2806 | 105.5044 | 51.2422 | 28.4896 | 106.0254 | 50.9519 | 26.5756 | 106.5751 | 50.4645 | 24.6106 | 107.1615 | 50.1143 | 22.5055 | 109.7202 | 49.038 | 15.1631 | 111.7862 | 48.8624 | 11.5436 | 113.1677 | 52.2321 | 10.5969 | 114.0479 | 53.8971 | 11.1927 | 103.4887 | 56.8093 | 36.5106 | 103.8013 | 55.6396 | 35.3286 | 103.947 | 54.6172 | 34.3874 | 104.2952 | 53.6195 | 33.2134 | 104.7785 | 52.6789 | 31.8163 | 105.4219 | 51.6054 | 30.2194 | 106.1958 | 51.0871 | 28.3687 | 107.0773 | 50.6874 | 26.4584 | 108.0321 | 50.0767 | 24.768 | 109.0808 | 49.6114 | 23.0684 | 113.4526 | 46.8893 | 13.184 | 117.185 | 43.3586 | -5.8821 | 119.1221 | 44.4097 | -20.1159 | 119.9724 | 44.1768 | -29.8829 | 103.4739 | 56.8094 | 36.5007 | 103.8063 | 56.242 | 35.1951 | 103.956 | 55.7804 | 34.2898 | 104.275 | 55.2896 | 33.2847 | 104.7389 | 54.7944 | 31.9964 | 105.3559 | 54.1644 | 30.5892 | 106.1227 | 53.5903 | 28.9924 | 106.986 | 53.1578 | 27.3866 | 107.9824 | 52.4403 | 25.6121 | 109.3988 | 51.4327 | 20.9771 | 113.7423 | 48.3359 | -0.70306 | 116.4393 | 44.6582 | -17.8187 | 117.4061 | 44.4496 | -27.2984 | 117.1081 | 44.2054 | -24.5083
BARROW & SANDGATE | HARKER / HUTTON | 321492 | 468870 | 167.5236 | 30.641 | 93.5475 | 166.1714 | 30.171 | 88.358 | 164.1346 | 29.7766 | 84.1075 | 159.8793 | 29.0047 | 80.9383 | 155.8796 | 28.279 | 80.0379 | 132.666 | 24.0677 | 79.1959 | 111.0806 | 20.1518 | 78.2255 | 90.1414 | 16.3531 | 77.1703 | 68.9801 | 12.5141 | 68.9801 | 47.3321 | 8.5868 | 47.3321 | 30.4338 | 5.5212 | 30.4338 | 17.0465 | 3.0925 | 17.0465 | 13.646 | 2.4756 | 13.646 | 6.3202 | 1.1466 | 6.3202 | 168.2471 | 30.9536 | 95.9951 | 168.132 | 30.9346 | 93.6738 | 167.5689 | 30.7013 | 90.8146 | 166.5053 | 30.2636 | 88.4828 | 164.9475 | 29.9241 | 87.3862 | 161.6348 | 29.3231 | 86.1587 | 158.7971 | 28.8083 | 84.714 | 156.57 | 28.4043 | 83.1181 | 154.2195 | 27.9779 | 80.8509 | 151.4635 | 27.4779 | 78.3838 | 143.1426 | 25.9684 | 76.5047 | 137.1614 | 24.8833 | 75.5519 | 136.6359 | 24.7879 | 75.4136 | 137.5343 | 24.9509 | 76.04 | 168.2276 | 30.9448 | 93.6584 | 167.4332 | 30.6889 | 88.5582 | 166.0924 | 30.1664 | 84.3988 | 161.6052 | 29.3178 | 81.3148 | 157.394 | 28.5538 | 80.4962 | 130.9427 | 23.7551 | 79.743 | 106.0046 | 19.2309 | 78.867 | 81.6877 | 14.8194 | 77.9093 | 57.4318 | 10.419 | 57.4318 | 32.8891 | 5.9666 | 32.8891 | 18.3217 | 3.3238 | 18.3217 | 6.6998 | 1.2154 | 6.6998 | 1.6408 | 0.29767 | 1.6408 | 10.6707 | 1.9358 | 10.6707 | 167.5471 | 30.6509 | 93.6322 | 165.9262 | 30.1017 | 88.5309 | 163.2965 | 29.6246 | 84.3733 | 159.0301 | 28.8506 | 81.3054 | 155.0444 | 28.1275 | 80.5197 | 131.7847 | 23.9078 | 79.6819 | 110.1615 | 19.985 | 78.824 | 89.058 | 16.1565 | 77.9822 | 67.8852 | 12.3155 | 67.8852 | 46.247 | 8.3899 | 46.247 | 16.108 | 2.9222 | 16.108 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 167.6109 | 30.6792 | 93.7246 | 166.3843 | 30.2361 | 88.6368 | 164.0218 | 29.7562 | 84.5543 | 159.3955 | 28.9169 | 81.6434 | 154.5571 | 28.0391 | 80.4687 | 131.0219 | 23.7695 | 79.984 | 102.9628 | 18.6791 | 70.859 | 82.276 | 14.9262 | 70.7889 | 61.012 | 11.0686 | 61.012 | 36.7978 | 6.6757 | 36.7978 | 8.9999 | 1.6327 | 8.9999 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707
PENRITH & SHAP | HARKER / HUTTON | 356910 | 513357 | 129.2274 | 56.6311 | 50.7241 | 129.7001 | 54.5768 | 48.729 | 129.849 | 52.7604 | 47.4219 | 130.1679 | 50.6893 | 45.8746 | 130.587 | 48.7275 | 44.1756 | 131.1225 | 45.7827 | 42.2834 | 131.7439 | 43.9367 | 40.1552 | 132.4144 | 42.1922 | 37.9842 | 133.1345 | 40.3598 | 35.6077 | 133.9571 | 38.558 | 32.2313 | 144.5795 | 34.1363 | 12.4599 | 138.5827 | 31.5428 | -1.6935 | 133.6511 | 30.9014 | -6.3782 | 126.8705 | 29.1085 | -6.3613 | 128.9667 | 56.8431 | 51.5656 | 129.2733 | 55.557 | 50.2976 | 129.752 | 54.3119 | 48.6371 | 130.3488 | 52.8983 | 47.0977 | 131.0246 | 51.6074 | 45.3672 | 131.7859 | 50.1298 | 43.41 | 132.6557 | 49.3267 | 41.1737 | 133.6074 | 48.6345 | 38.8387 | 134.6416 | 47.9041 | 36.4066 | 135.7681 | 47.1426 | 33.8494 | 138.2397 | 45.142 | 26.444 | 141.1245 | 43.8076 | 17.6388 | 144.0087 | 43.3609 | 10.2834 | 146.4135 | 42.1366 | 5.1166 | 129.2326 | 56.825 | 50.7793 | 129.7094 | 54.9127 | 48.8848 | 129.8634 | 53.0197 | 47.6856 | 130.1881 | 50.805 | 46.2467 | 130.6126 | 48.7307 | 44.6478 | 131.1501 | 46.3116 | 42.8545 | 131.7714 | 44.9517 | 40.8249 | 132.4405 | 43.9132 | 38.7519 | 133.1514 | 42.7538 | 36.5005 | 133.9408 | 41.5559 | 33.3489 | 143.9565 | 38.0428 | 14.9798 | 152.5834 | 35.7252 | 2.8091 | 147.3659 | 35.0022 | -0.93291 | 138.2327 | 32.5894 | -0.035544 | 129.1986 | 56.6293 | 50.7714 | 129.6547 | 54.5192 | 48.6897 | 129.8137 | 52.6291 | 47.3052 | 130.1896 | 50.4701 | 45.6267 | 130.7176 | 48.4137 | 43.6255 | 131.4877 | 45.3311 | 41.2891 | 132.4909 | 43.3078 | 38.4693 | 133.6606 | 41.3894 | 35.6312 | 134.9778 | 39.4013 | 32.9977 | 136.4601 | 37.5113 | 30.3106 | 140.4753 | 31.7949 | 8.4299 | 125.0109 | 27.525 | -15.6252 | 116.1194 | 25.6922 | -26.0326 | 107.3937 | 23.3099 | -31.4124 | 129.1614 | 56.634 | 50.7647 | 129.6141 | 55.6164 | 48.6075 | 129.7684 | 54.5313 | 47.2706 | 130.1211 | 53.0392 | 45.6818 | 130.6428 | 51.5452 | 43.5291 | 131.4686 | 49.116 | 41.1955 | 133.9026 | 47.1447 | 37.2725 | 135.7017 | 45.2977 | 34.2221 | 137.1682 | 43.4436 | 31.7336 | 139.7683 | 41.1933 | 26.1807 | 143.8196 | 33.8575 | -7.922 | 127.3996 | 28.667 | -23.3069 | 116.042 | 25.225 | -29.6932 | 109.2605 | 23.192 | -26.0339
STAINBURN & SIDDICK | HARKER / HUTTON | 300332 | 530823 | -12.2475 | -12.2475 | -12.2475 | -11.7432 | -11.7432 | -11.7432 | -10.9283 | -10.9283 | -10.9283 | -9.9464 | -9.9464 | -9.9464 | -8.7703 | -8.7703 | -8.7703 | -7.4707 | -7.4707 | -7.4707 | -5.9574 | -5.9574 | -5.9574 | -4.4138 | -4.4138 | -4.4138 | -3.107 | -3.107 | -3.107 | -1.6239 | -1.6239 | -1.6239 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | -12.1723 | -12.1723 | -12.1723 | -11.6569 | -11.6569 | -11.6569 | -10.9371 | -10.9371 | -10.9371 | -10.3558 | -10.3558 | -10.3558 | -9.6194 | -9.6194 | -9.6194 | -8.7878 | -8.7878 | -8.7878 | -7.8377 | -7.8377 | -7.8377 | -6.8095 | -6.8095 | -6.8095 | -5.7144 | -5.7144 | -5.7144 | -4.5695 | -4.5695 | -4.5695 | -0.11108 | -0.11108 | -0.11108 | 3.0611 | 1.9358 | 3.0611 | 5.4282 | 1.9358 | 5.4282 | 6.7308 | 1.9358 | 6.7308 | -12.2325 | -12.2325 | -12.2325 | -11.7225 | -11.7225 | -11.7225 | -10.9029 | -10.9029 | -10.9029 | -9.9177 | -9.9177 | -9.9177 | -8.7437 | -8.7437 | -8.7437 | -7.4573 | -7.4573 | -7.4573 | -5.9637 | -5.9637 | -5.9637 | -4.4361 | -4.4361 | -4.4361 | -3.1692 | -3.1692 | -3.1692 | -1.7853 | -1.7853 | -1.7853 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | -12.2051 | -12.2051 | -12.2051 | -11.5231 | -11.5231 | -11.5231 | -10.3677 | -10.3677 | -10.3677 | -8.9282 | -8.9282 | -8.9282 | -7.0762 | -7.0762 | -7.0762 | -5.3404 | -5.3404 | -5.3404 | -3.5179 | -3.5179 | -3.5179 | -1.3684 | -1.3684 | -1.3684 | 1.0583 | 1.0583 | 1.0583 | 4.9899 | 1.9358 | 4.9899 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -5.5287 | 6.7308 | 1.9358 | -15.6933 | -12.1464 | -12.1464 | -12.1464 | -11.2625 | -11.2625 | -11.2625 | -9.9058 | -9.9058 | -9.9058 | -8.2655 | -8.2655 | -8.2655 | -6.2518 | -6.2518 | -6.2518 | -1.0265 | -1.0265 | -1.0265 | 2.0502 | 1.9358 | 2.0502 | 5.1205 | 1.9358 | 5.1205 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -0.19807 | 6.7308 | 1.9358 | -10.0504 | 6.7308 | 1.9358 | -4.1017
SKELMERSDALE | WASHWAY FARM / KIRKBY | 347172 | 407455 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 34.4311 | 20.3388 | 34.4311 | 37.5473 | 31.7071 | 37.5473 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 30.1966 | 14.8557 | 30.1966 | 32.1941 | 24.9879 | 32.1941 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 31.7751 | 28.0009 | 31.7751 | 33.6032 | 33.6032 | 33.6032 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | -0.80864 | -0.33214 | -0.80864 | 10.6707 | 1.9358 | 10.6707 | 42.1272 | 12.5382 | 19.3078 | 43.5947 | 23.7669 | 9.7722 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 34.0485 | 25.4951 | 34.0485 | 39.5184 | 20.0734 | 22.4931 | 41.6728 | 25.7544 | 12.9596 | 40.9166 | 24.6971 | 14.3456
SIDDICK & STAINBURN | HARKER / HUTTON | 302535 | 529330 | -12.2475 | -12.2475 | -12.2475 | -11.7432 | -11.7432 | -11.7432 | -10.9283 | -10.9283 | -10.9283 | -9.9464 | -9.9464 | -9.9464 | -8.7703 | -8.7703 | -8.7703 | -7.4707 | -7.4707 | -7.4707 | -5.9574 | -5.9574 | -5.9574 | -4.4138 | -4.4138 | -4.4138 | -3.107 | -3.107 | -3.107 | -1.6239 | -1.6239 | -1.6239 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | -12.1723 | -12.1723 | -12.1723 | -11.6569 | -11.6569 | -11.6569 | -10.9371 | -10.9371 | -10.9371 | -10.3558 | -10.3558 | -10.3558 | -9.6194 | -9.6194 | -9.6194 | -8.7878 | -8.7878 | -8.7878 | -7.8377 | -7.8377 | -7.8377 | -6.8095 | -6.8095 | -6.8095 | -5.7144 | -5.7144 | -5.7144 | -4.5695 | -4.5695 | -4.5695 | -0.11108 | -0.11108 | -0.11108 | 3.0611 | 1.9358 | 3.0611 | 5.4282 | 1.9358 | 5.4282 | 6.7308 | 1.9358 | 6.7308 | -12.2325 | -12.2325 | -12.2325 | -11.7225 | -11.7225 | -11.7225 | -10.9029 | -10.9029 | -10.9029 | -9.9177 | -9.9177 | -9.9177 | -8.7437 | -8.7437 | -8.7437 | -7.4573 | -7.4573 | -7.4573 | -5.9637 | -5.9637 | -5.9637 | -4.4361 | -4.4361 | -4.4361 | -3.1692 | -3.1692 | -3.1692 | -1.7853 | -1.7853 | -1.7853 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | -12.2051 | -12.2051 | -12.2051 | -11.5231 | -11.5231 | -11.5231 | -10.3677 | -10.3677 | -10.3677 | -8.9282 | -8.9282 | -8.9282 | -7.0762 | -7.0762 | -7.0762 | -5.3404 | -5.3404 | -5.3404 | -3.5179 | -3.5179 | -3.5179 | -1.3684 | -1.3684 | -1.3684 | 1.0583 | 1.0583 | 1.0583 | 4.9899 | 1.9358 | 4.9899 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -5.5287 | 6.7308 | 1.9358 | -15.6933 | -12.1464 | -12.1464 | -12.1464 | -11.2625 | -11.2625 | -11.2625 | -9.9058 | -9.9058 | -9.9058 | -8.2655 | -8.2655 | -8.2655 | -6.2518 | -6.2518 | -6.2518 | -1.0265 | -1.0265 | -1.0265 | 2.0502 | 1.9358 | 2.0502 | 5.1205 | 1.9358 | 5.1205 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -0.19807 | 6.7308 | 1.9358 | -10.0504 | 6.7308 | 1.9358 | -4.1017
STRETFORD | SOUTH MANCHESTER | 380069 | 395104 | 133.3868 | 34.9468 | 69.6009 | 133.9271 | 33.9437 | 65.9974 | 134.0774 | 33.539 | 64.6939 | 134.4107 | 33.1803 | 63.9936 | 135.6088 | 32.562 | 62.3297 | 136.0582 | 32.0192 | 61.2136 | 136.4694 | 31.514 | 60.0628 | 136.9083 | 31.1112 | 58.8583 | 137.3659 | 30.6446 | 57.4617 | 137.8494 | 30.1445 | 55.9143 | 146.0507 | 28.9122 | 43.9265 | 156.676 | 34.9534 | 31.7843 | 162.4003 | 51.5843 | 25.9638 | 166.4106 | 58.0886 | 23.0025 | 132.8881 | 35.5123 | 71.9176 | 133.0421 | 34.9678 | 70.4163 | 133.3878 | 34.6087 | 69.1192 | 133.7999 | 34.3291 | 68.1824 | 134.2665 | 33.9629 | 67.1468 | 134.7797 | 33.5784 | 66.0159 | 135.3426 | 33.2198 | 64.8056 | 135.9015 | 32.9538 | 63.5627 | 136.4535 | 32.6308 | 62.287 | 136.9692 | 32.3145 | 61.0014 | 139.352 | 32.117 | 56.7375 | 142.1935 | 37.0305 | 52.3281 | 145.3252 | 49.1725 | 48.5229 | 148.0417 | 54.5807 | 45.7102 | 133.3902 | 35.5084 | 69.6301 | 133.934 | 34.9867 | 66.0682 | 134.089 | 34.5821 | 64.8076 | 134.428 | 34.2076 | 64.142 | 135.6309 | 33.8162 | 62.5193 | 136.0897 | 33.4202 | 61.4454 | 136.5059 | 33.0098 | 60.2562 | 136.9493 | 32.687 | 58.9135 | 137.4064 | 32.2941 | 57.5682 | 137.873 | 31.8939 | 56.1456 | 145.4829 | 31.6906 | 45.0327 | 154.1162 | 39.5982 | 34.7401 | 158.8215 | 58.0135 | 29.8262 | 160.9264 | 65.7591 | 28.374 | 133.3531 | 34.9623 | 69.6672 | 133.8827 | 33.9685 | 66.1232 | 134.0779 | 33.5577 | 61.2975 | 134.5127 | 33.2205 | 57.0514 | 135.6382 | 32.6439 | 55.4067 | 136.1888 | 32.116 | 54.2031 | 136.8886 | 31.599 | 52.8257 | 137.7245 | 31.1958 | 51.3128 | 138.6398 | 30.6954 | 49.5708 | 139.6138 | 30.2046 | 47.754 | 153.0905 | 27.7731 | 23.4368 | 172.7383 | 31.6331 | 0.27329 | 178.3286 | 46.649 | -13.5626 | 179.675 | 52.2567 | -22.117 | 133.3801 | 34.9838 | 69.6341 | 133.9945 | 34.0604 | 65.9899 | 134.2584 | 33.6557 | 61.1293 | 134.7086 | 33.3336 | 56.8945 | 135.8277 | 32.7651 | 55.2272 | 136.515 | 32.2021 | 53.9845 | 137.4565 | 31.5917 | 52.4836 | 138.9734 | 31.431 | 50.2625 | 141.8438 | 31.0805 | 46.5528 | 149.6478 | 30.8295 | 36.1379 | 165.5887 | 48.8928 | 8.4183 | 172.7379 | 45.8086 | -7.8703 | 175.5577 | 51.9604 | -18.4031 | 174.3466 | 51.5711 | -16.3136
STUART ST | STALYBRIDGE | 387247 | 398875 | 14.6106 | 2.6506 | 14.6106 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 5.7601 | 10.6707 | 1.9358 | -11.4728 | 10.6707 | 1.9358 | -31.1057 | 10.6707 | 1.9358 | -50.8426 | 10.6707 | 1.9358 | -55.3731 | 10.6707 | 1.9358 | -59.8813 | 10.6707 | 1.9358 | -63.4662 | 3.6316 | 1.4916 | -70.6189 | 4.4733 | 1.8374 | -76.4632 | 10.6707 | 1.9358 | -79.0933 | 10.6707 | 1.9358 | -80.0846 | 18.5367 | 3.3628 | 18.5367 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -4.9093 | 10.6707 | 1.9358 | -24.6921 | 10.6707 | 1.9358 | -44.687 | 10.6707 | 1.9358 | -49.5473 | 10.6707 | 1.9358 | -54.4518 | 10.6707 | 1.9358 | -57.3934 | 10.6707 | 1.9358 | -62.8718 | 10.6707 | 1.9358 | -67.3122 | 10.6707 | 1.9358 | -70.1142 | 10.6707 | 1.9358 | -71.4534 | 18.488 | 3.354 | 18.488 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.1773 | 10.6707 | 1.9358 | -10.9853 | 10.6707 | 1.9358 | -30.5469 | 10.6707 | 1.9358 | -50.2113 | 10.6707 | 1.9358 | -54.6639 | 10.6707 | 1.9358 | -59.0725 | 10.6707 | 1.9358 | -62.4763 | 8.8794 | 1.9358 | -68.8925 | 10.6707 | 1.9358 | -73.6664 | 10.6707 | 1.9358 | -75.7596 | 10.6707 | 1.9358 | -76.1022 | 14.7014 | 2.6671 | 14.7014 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.1904 | 10.6707 | 1.9358 | -11.0076 | 10.6707 | 1.9358 | -30.673 | 10.6707 | 1.9358 | -50.5772 | 10.6707 | 1.9358 | -55.3309 | 10.6707 | 1.9358 | -59.9882 | 10.3747 | 1.9358 | -62.6356 | 1.5031 | 0.6174 | -72.0933 | 6.7308 | 1.9358 | -88.7418 | 2.3763 | 0.97605 | -100.9566 | 6.7308 | 1.9358 | -109.7527 | 14.7628 | 2.6782 | 14.7628 | 6.0693 | 1.1011 | 6.0693 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.2469 | 10.6707 | 1.9358 | -10.9165 | 10.6707 | 1.9358 | -30.5082 | 10.6707 | 1.9358 | -50.3224 | 10.6707 | 1.9358 | -54.9701 | 10.6707 | 1.9358 | -59.658 | 10.6707 | 1.9358 | -64.7232 | 10.6707 | 1.9358 | -83.9729 | 9.4514 | 1.9358 | -99.1598 | 1.4221 | 0.58413 | -107.9779 | 6.7308 | 1.9358 | -105.2798
THORNTON | PENWORTHAM WEST / STANAH | 334559 | 443368 | 25.1615 | 13.8671 | 25.1615 | 25.742 | 8.005 | 25.742 | 9.0455 | 1.641 | 9.0455 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.8768 | 10.6707 | 1.9358 | 3.1419 | 39.8329 | 7.2263 | 1.9071 | 41.8644 | 10.583 | 2.8962 | 25.3041 | 13.9964 | 25.3041 | 25.9906 | 7.529 | 25.9906 | 3.2586 | 0.59116 | 3.2586 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.0084 | 10.6707 | 1.9358 | 7.3043 | 36.5032 | 10.2032 | 5.3745 | 25.1625 | 13.9915 | 25.1625 | 25.7435 | 7.5592 | 25.7435 | 0.27337 | 0.049594 | 0.27337 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 9.9386 | 10.6707 | 1.9358 | 4.7619 | 10.6707 | 1.9358 | 3.7313 | 10.6707 | 1.9358 | 4.7218 | 25.1622 | 13.8706 | 25.1622 | 25.7475 | 7.9975 | 25.7475 | 8.7222 | 1.5824 | 8.7222 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 9.0797 | 10.6707 | 1.9358 | -0.66973 | 10.6707 | 1.9358 | -16.4992 | 10.6707 | 1.9358 | -26.7864 | 11.5011 | 2.0865 | -34.4618 | 25.3532 | 13.854 | 25.3532 | 26.1906 | 13.4318 | 26.1906 | 27.1767 | 12.2777 | 27.1767 | 28.1567 | 10.9862 | 26.7449 | 29.2263 | 9.71 | 25.7157 | 29.9097 | 8.2642 | 24.667 | 30.7337 | 6.8938 | 23.2708 | 31.5552 | 5.7246 | 21.6888 | 25.4922 | 4.6247 | 20.004 | 18.6241 | 3.3787 | 16.2214 | 33.666 | 6.1076 | -8.9752 | 6.2735 | 1.1381 | -21.4501 | 23.3388 | 4.234 | -28.2724 | 12.0909 | 2.1935 | -27.0578
ULVERSTON | HARKER / HUTTON | 327495 | 477808 | 103.5058 | 38.2823 | 78.304 | 103.8345 | 37.7674 | 76.5368 | 104.102 | 37.356 | 75.3941 | 104.4911 | 36.7723 | 74.2261 | 104.9892 | 36.2447 | 72.8754 | 105.5915 | 35.44 | 71.3344 | 106.3089 | 34.5595 | 69.6171 | 107.0947 | 33.7097 | 67.8495 | 107.9387 | 32.8389 | 66.0723 | 108.8858 | 31.8518 | 63.7125 | 113.4826 | 27.5839 | 53.9734 | 117.198 | 24.2905 | 48.2848 | 121.4893 | 24.0983 | 43.837 | 121.8193 | 24.9688 | 45.4132 | 103.426 | 38.5564 | 79.1695 | 103.7119 | 38.2867 | 78.1795 | 104.1451 | 37.8456 | 76.8938 | 104.6288 | 37.2305 | 75.847 | 105.1769 | 36.6896 | 74.6522 | 105.7989 | 35.9898 | 73.2779 | 106.5139 | 35.2994 | 71.713 | 107.2936 | 34.7328 | 70.0745 | 108.1419 | 34.1178 | 68.3664 | 109.0527 | 33.4499 | 66.5231 | 110.4774 | 31.1821 | 61.9305 | 111.5475 | 29.0724 | 57.7657 | 112.2396 | 29.4549 | 54.9811 | 112.5972 | 30.4909 | 53.4155 | 103.5059 | 38.5585 | 78.3381 | 103.8347 | 38.3 | 76.6502 | 104.1024 | 37.7798 | 75.5926 | 104.4918 | 36.8196 | 74.5041 | 104.9879 | 35.9062 | 73.2318 | 105.5868 | 34.6415 | 71.7658 | 106.3008 | 33.4173 | 70.1209 | 107.0844 | 32.3205 | 68.4232 | 107.9169 | 31.1986 | 66.7545 | 108.816 | 30.0396 | 64.6329 | 113.2222 | 25.6547 | 55.7293 | 116.72 | 21.9562 | 50.6287 | 119.0909 | 21.605 | 46.4545 | 118.2382 | 21.4503 | 47.9506 | 103.495 | 38.2895 | 78.334 | 103.8393 | 37.8437 | 76.5076 | 104.1791 | 37.4698 | 75.3148 | 104.7005 | 36.8333 | 74.1204 | 105.4124 | 36.1455 | 72.6655 | 106.3195 | 35.1188 | 70.9614 | 107.4665 | 34.0265 | 68.9595 | 108.7861 | 33.0274 | 66.9031 | 110.0395 | 31.9851 | 65.1281 | 111.3886 | 30.7661 | 63.3338 | 121.6818 | 24.8317 | 47.6701 | 103.3219 | 18.7442 | 30.3639 | 91.0868 | 16.5246 | 19.363 | 84.5642 | 15.3413 | 11.8038 | 103.4783 | 38.3056 | 78.3487 | 103.863 | 37.9203 | 76.4609 | 104.21 | 37.5228 | 75.3133 | 104.6951 | 36.8901 | 74.2301 | 105.3637 | 36.1869 | 72.8355 | 106.2525 | 35.1377 | 71.2555 | 107.3227 | 33.9405 | 69.5505 | 109.3292 | 32.7651 | 67.0537 | 111.8777 | 31.4704 | 63.9196 | 116.5742 | 29.4228 | 56.2155 | 122.1798 | 22.7933 | 34.9588 | 95.1723 | 17.2658 | 21.0127 | 96.9344 | 17.5854 | 14.0987 | 83.1931 | 15.0926 | 17.5387
VERNON PARK | BREDBURY | 391131 | 390929 | 84.1256 | 36.9585 | 55.7036 | 84.5028 | 34.0688 | 51.6124 | 84.5836 | 31.4898 | 48.8304 | 84.9258 | 28.8583 | 45.75 | 85.4133 | 26.5098 | 42.2275 | 86.0401 | 23.6683 | 38.5109 | 86.7532 | 22.3666 | 34.6163 | 90.154 | 21.3203 | 29.3201 | 90.902 | 20.5421 | 26.6739 | 91.732 | 19.743 | 23.6119 | 88.0752 | 15.9782 | 5.7329 | 84.4261 | 15.3162 | -0.34178 | 103.0026 | 18.6863 | -3.524 | 112.9101 | 20.4837 | -2.7637 | 83.8268 | 37.2755 | 56.3604 | 83.991 | 34.8878 | 52.8363 | 84.3469 | 33.1035 | 49.8147 | 84.8776 | 31.3606 | 46.7691 | 85.489 | 29.8411 | 43.4132 | 86.1648 | 28.2156 | 39.8399 | 86.827 | 27.3192 | 36.0595 | 87.5126 | 26.9847 | 33.4866 | 88.2446 | 26.5895 | 30.7801 | 89.0067 | 26.0296 | 27.9985 | 91.4488 | 24.8601 | 20.3495 | 93.8174 | 24.5312 | 14.6171 | 95.7973 | 27.0817 | 10.884 | 97.3198 | 29.271 | 8.3756 | 84.1291 | 37.2507 | 55.7862 | 84.5087 | 35.2616 | 51.8358 | 84.5922 | 33.308 | 49.1946 | 84.9375 | 31.3837 | 46.2124 | 85.4263 | 29.8538 | 42.8059 | 86.0513 | 28.1895 | 39.2036 | 86.7614 | 27.2136 | 35.4187 | 90.1588 | 26.7952 | 30.2295 | 90.8938 | 26.2999 | 27.7368 | 91.6772 | 25.6252 | 24.9868 | 102.3633 | 23.4937 | 8.2126 | 105.346 | 23.4092 | 3.2479 | 108.7887 | 27.2867 | 0.52785 | 109.8708 | 29.0349 | 1.7241 | 84.0877 | 36.9626 | 55.7327 | 84.4325 | 34.0584 | 51.6764 | 84.515 | 31.4256 | 48.9778 | 84.908 | 28.7731 | 45.9851 | 85.4942 | 26.3872 | 42.609 | 86.3124 | 23.5571 | 39.0032 | 87.3229 | 22.1676 | 35.0922 | 92.9234 | 20.8099 | 27.9817 | 94.0298 | 20.2058 | 25.7925 | 95.4145 | 19.5139 | 23.4631 | 79.3602 | 14.3972 | 1.2651 | 53.7005 | 9.7421 | -29.5752 | 51.1384 | 9.2773 | -52.8044 | 46.0837 | 8.3603 | -68.0384 | 84.0295 | 36.9731 | 55.8307 | 84.3738 | 34.9363 | 51.6721 | 84.4543 | 33.0416 | 49.0141 | 84.8005 | 31.0442 | 46.2618 | 85.3422 | 29.317 | 43.0788 | 90.6922 | 26.5748 | 35.2228 | 91.4256 | 25.4355 | 31.9662 | 94.9046 | 24.6165 | 27.4195 | 95.9547 | 23.9975 | 25.0095 | 100.2466 | 22.0273 | 14.9387 | 89.5083 | 16.2382 | -21.4748 | 56.2 | 10.1956 | -49.157 | 55.0967 | 9.9954 | -64.4146 | 52.0602 | 9.4446 | -58.9126
WEST DIDSBURY | SOUTH MANCHESTER | 382900 | 393269 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.0839 | 1.9358 | 10.0839 | 6.7149 | 1.9358 | 6.7149 | -8.1947 | -3.3659 | -8.1947 | -18.2652 | -7.5023 | -18.2652 | -20.0448 | -8.2333 | -20.0448 | -22.2492 | -9.1387 | -22.2492 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 7.1993 | 1.9358 | 7.1993 | 1.6142 | 0.663 | 1.6142 | 1.8758 | 0.77048 | 1.8758 | 2.0868 | 0.85714 | 2.0868 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.2212 | 1.9358 | 10.2212 | -1.4467 | -0.59421 | -1.4467 | -9.9871 | -4.1021 | -9.9871 | -11.091 | -4.5556 | -11.091 | -13.8028 | -5.6694 | -13.8028 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.7031 | 1.9358 | 8.7031 | 5.2271 | 1.9358 | 5.2271 | -13.8439 | -5.6863 | -13.8439 | -39.1363 | -16.0749 | -39.1363 | -56.3165 | -23.1316 | -56.3165 | -70.082 | -28.7857 | -70.082 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.6357 | 1.9358 | 9.6357 | 4.3253 | 1.7766 | 4.3253 | -19.1385 | -7.861 | -19.1385 | -44.503 | -18.2793 | -44.503 | -56.2391 | -23.0998 | -57.109 | -64.1833 | -26.3628 | -64.1833
WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 32.4229 | 32.4229 | 32.4229 | 32.742 | 32.742 | 32.742 | 32.8316 | 28.9495 | 32.8316 | 33.0629 | 16.599 | 33.0629 | 25.3687 | 4.6023 | 25.3687 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 44.8118 | 44.8118 | 41.2961 | 46.9532 | 46.9532 | 41.592 | 32.1013 | 32.1013 | 32.1013 | 32.1799 | 32.1799 | 32.1799 | 32.397 | 27.3426 | 32.397 | 32.6689 | 14.1393 | 32.6689 | 6.9119 | 1.2539 | 6.9119 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 40.5479 | 20.687 | 40.5479 | 41.7617 | 41.7617 | 41.7617 | 32.4274 | 32.4274 | 32.4274 | 32.7461 | 32.7461 | 32.7461 | 32.8394 | 27.2433 | 32.8394 | 33.0736 | 13.9115 | 33.0736 | 5.1264 | 0.93001 | 5.1264 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 42.8638 | 42.8638 | 42.8638 | 44.2636 | 44.2636 | 44.2636 | 32.401 | 32.401 | 32.401 | 32.7111 | 32.7111 | 32.7111 | 32.8077 | 28.9319 | 32.8077 | 33.0801 | 16.5986 | 33.0801 | 25.4803 | 4.6225 | 25.4803 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 51.6796 | 41.0544 | 15.3312 | 53.1926 | 40.0242 | 6.1325 | 32.4102 | 32.4102 | 32.4102 | 32.735 | 32.735 | 32.735 | 32.8513 | 32.8513 | 32.8513 | 33.1176 | 33.1176 | 33.1176 | 33.5192 | 33.5192 | 33.5192 | 34.1169 | 34.1169 | 34.1169 | 34.9182 | 34.9182 | 34.9182 | 35.8522 | 35.8522 | 35.8522 | 36.9306 | 36.9306 | 36.9306 | 38.2732 | 38.2732 | 38.2732 | 44.0214 | 44.0214 | 35.4436 | 48.5275 | 44.0588 | 18.5115 | 50.4018 | 41.2431 | 9.2212 | 50.3593 | 40.5909 | 12.576
WIGAN | WASHWAY FARM / KIRKBY | 358343 | 404626 | 79.2044 | 69.708 | 70.1301 | 82.1393 | 55.4252 | 68.6249 | 82.2778 | 41.3637 | 67.6119 | 82.5635 | 27.2197 | 65.5595 | 73.3431 | 13.3056 | 63.1183 | 0.79849 | 0.14486 | 0.79849 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 92.2904 | 19.6363 | 30.796 | 94.1895 | 55.7471 | 29.477 | 95.8207 | 63.7803 | 29.9502 | 78.9858 | 69.9069 | 70.9329 | 81.6849 | 53.9795 | 70.061 | 81.9999 | 38.1433 | 68.5976 | 82.3924 | 22.3999 | 66.8859 | 37.3166 | 6.7698 | 37.3166 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 43.37 | 7.868 | 41.6684 | 90.6696 | 33.7997 | 39.3621 | 91.7298 | 39.1573 | 38.1276 | 79.2055 | 69.8982 | 70.2185 | 82.147 | 53.9576 | 68.7916 | 82.2879 | 38.0615 | 67.826 | 82.5759 | 22.233 | 65.8247 | 35.9868 | 6.5286 | 35.9868 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 91.1474 | 16.7616 | 33.4442 | 92.7164 | 57.8057 | 32.5553 | 93.7727 | 67.2044 | 33.368 | 79.1841 | 69.7091 | 70.1962 | 82.1134 | 55.4226 | 68.7839 | 82.2875 | 41.3248 | 67.9105 | 82.6542 | 27.1986 | 66.0054 | 72.9678 | 13.2375 | 63.6948 | 0.50168 | 0.091014 | 0.50168 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 87.8313 | 15.934 | 11.9316 | 100.0097 | 49.1315 | -6.3079 | 101.3279 | 55.2428 | -18.2955 | 79.1536 | 71.4641 | 70.2016 | 82.1139 | 71.1028 | 68.6382 | 82.3127 | 70.6988 | 67.7493 | 82.6744 | 70.126 | 66.0005 | 83.2036 | 69.5623 | 63.8013 | 83.9457 | 68.5066 | 60.2656 | 84.788 | 67.5615 | 56.5303 | 85.7459 | 66.8227 | 53.592 | 86.7493 | 66.0877 | 50.2384 | 88.0115 | 64.9544 | 43.7477 | 92.9927 | 64.6064 | 17.1733 | 96.7263 | 59.3214 | -4.0142 | 98.3006 | 56.3595 | -16.0098 | 98.1868 | 55.7331 | -12.4082
WRIGHTINGTON | PENWORTHAM WEST / STANAH | 354460 | 413610 | 89.8949 | 38.9465 | 42.127 | 90.4566 | 30.272 | 38.2262 | 90.8473 | 22.004 | 35.3937 | 76.6995 | 13.9145 | 32.8117 | 33.5549 | 6.0874 | 29.6818 | 11.8205 | 2.1444 | 11.8205 | 6.4454 | 1.1693 | 6.4454 | 1.2972 | 0.23533 | 1.2972 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.8939 | 10.6707 | 1.9358 | -11.8244 | 10.6707 | 1.9358 | -23.4507 | 57.5218 | 10.4354 | -27.072 | 96.4132 | 17.4909 | -27.0535 | 89.6555 | 38.6543 | 43.73 | 90.034 | 31.4401 | 41.3301 | 90.6271 | 24.3536 | 38.533 | 91.2903 | 17.4217 | 36.3678 | 58.9499 | 10.6944 | 33.7725 | 46.0717 | 8.3581 | 30.8773 | 41.734 | 7.5712 | 27.6879 | 37.4608 | 6.796 | 24.3591 | 33.2856 | 6.0385 | 20.906 | 28.9782 | 5.2571 | 17.3936 | 17.6285 | 3.1981 | 5.1251 | 30.9557 | 5.6159 | -4.7527 | 83.2491 | 15.1027 | -10.9484 | 108.7756 | 20.0487 | -14.9995 | 89.8986 | 38.6424 | 42.185 | 90.4634 | 28.887 | 38.4384 | 90.8579 | 19.1368 | 35.764 | 52.8387 | 9.5858 | 33.3243 | 2.2821 | 0.414 | 2.2821 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6391 | 10.6707 | 1.9358 | -8.1978 | 10.6707 | 1.9358 | -17.827 | 29.4067 | 5.3348 | -20.5971 | 64.7923 | 11.7543 | -19.7855 | 89.8758 | 38.9523 | 42.2113 | 90.4661 | 30.2564 | 38.264 | 90.966 | 21.7058 | 35.3872 | 74.0856 | 13.4403 | 32.8256 | 30.1516 | 5.47 | 29.7677 | 8.078 | 1.4655 | 8.078 | 2.0066 | 0.36402 | 2.0066 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.4695 | 10.6707 | 1.9358 | -11.4835 | 10.6707 | 1.9358 | -42.0185 | 19.1041 | 3.4658 | -61.3606 | 46.5868 | 8.4516 | -77.7471 | 89.8688 | 38.9358 | 42.1025 | 90.532 | 32.5743 | 37.8626 | 91.1023 | 26.1481 | 34.9576 | 91.8997 | 19.6373 | 32.4676 | 73.0136 | 13.2458 | 29.5025 | 58.1749 | 10.5539 | 26.2931 | 51.6781 | 9.3752 | 22.6909 | 47.0862 | 8.5422 | 19.0901 | 43.1515 | 7.8284 | 15.5413 | 37.2972 | 6.7663 | 7.9981 | 91.566 | 16.6115 | -28.2375 | 59.4455 | 10.7844 | -54.2812 | 62.0315 | 11.2535 | -67.103 | 54.2182 | 9.8361 | -64.9126