## Instructions
Thermal Rating Tool
This Thermal Rating tool is an output of the Celsius project. It predicts more informed ratings for Low Voltage transformers by using data or information about the asset and its environment.
Introduction
The aim of the Celsius project is to increase the capacity of distribution substations by investigating the thermal behaviour of the substation assets, developing methods to estimate improved thermal ratings, and investigating retrofit asset cooling technologies. This will allow the uptake of low carbon technologies and avoid the costly alternative of network reinforcement.
This tool has been built using the learning from the Celsius project. It can be used to understand the potential costs, capacity release and considerations for the relevant substations interventions investigated during the Celsius project, including monitoring and more informed 'Celsius rating', as well as retrofit cooling technologies.
This version of the tool was developed at the end of the Celsius project. It is intended that the underlying learning and methodologies will continue to develop as the solutions are rolled out into business as usual DNO operations, and as a result, it may be appropriate to update this tool.
This Model
This model is made up of two parts:
The Celsius Intervention Tool - Allows the user to input substation information, and returns details about potentially relevant interventions. This includes estimated costs and capacity release. This tool is limited to the interventions that were trialled during the Celsius project, and can only be used to investigate transformers with nameplate nominal ratings of 300kVA or above. The diagram to the right describes the tool functionality.
The Celsius Rating Tool - Allows the user to estimate a more informed rating, or 'Celsius Rating' for distribution transformers from input data, including half hourly measurement data as well as site information. Two versions of the Celsius Rating Tool have been developed: Indoor transformer tool: uses site information and data to estimate a more informed rating for a transformer inside a building or Glass Reinforced Plastic enclosure. Outdoor transformer tool: uses site information and data, and weather data to estimate a more informed rating for an outdoor transformer. WARNING: The results produced by this tool are initial indications only. A Celsius rating should be calculated from ongoing monitoring data. This tool can only be used to investigate transformers with nameplate nominal ratings of 300kVA or above. The diagram to the right describes the tool functionality.
Model Version
Version Number | Developers | Approver | Date | Notes
1 | Michael Kelly Olivia Carpenter-Lomax | Sarah Carter | 2019-11-29
2 | Michael Kelly Olivia Carpenter-Lomax | Sarah Carter | 2020-01-31
3 | Michael Kelly Olivia Carpenter-Lomax | Sarah Carter | 2020-03-31 | Removed transformers smaller than 300kVA, and amended to include weather data for only outdoor sites. This follows detailed analysis within the project to validate quality of the results in all cases.
Site information
(building type, transformer nominal rating, etc.)
Celsius Intervention Tool
Learning from trials: Capacity release from Celsius technologies
Learning from trials: Costs of Celsius technologies
Celsius intervention recommendations
Tool settings
Outputs
User inputs
Celsius Intervention Tool
Celsius Rating Tool
KEY:
Measured current and voltage
Indoor sites: Measured transformer and substation ambient temperature
Celsius Rating Tool
Celsius Rating
Site information
(building type, transformer spec, nominal rating)
Maximum set point for hotspot, ambient temperature and weather data as appropriate
Outdoor sites: Measured transformer temperature and weather data

## Celsius Intervention Tool
Celsius BAU tool: Celsius Intervention Recommendations
This tool provides data on relevant substation interventions that may release additional capacity if needed. The substation information should be selected from the drop-down menus provided. Where options are not available in the drop-down lists, results cannot be provided as there is not sufficient trial data. The interventions, along with relevant cost, capacity release, and practical information will appear in the orange table. Please note that the tool takes a few seconds to update once input data has been entered.
Input site information | To be hidden in the final tool |  | PLEASE FILL IN THE SUBSTATION DETAILS BELOW |  |  |  |  | To be hidden in the final tool |  |  |  | The Info below will be hidden from the final tool
[24 empty] | Lookup Value: | , No
|  | Is the substation exposed to direct sunlight? | Building Type | Nominal Rating kVA |  | WARNING: Trial results for GRP sites are less conclusive than for other site types. It is recommended that further work is carried out in these areas.
|  | No | [21 empty] | Index Code: | #N/A
Potential Celsius Interventions | [12 empty] | Intervention Technology Data | [10 empty] | Lookup Codes |  |  |  | Lookup Chart
[30 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
|  |  | 3 |  | 9 | 10 | 11 | 7 | 8
| Raw Index | Index Code | Options | Predicted Capacity Release % kVA | Mean Capacity Release across successful Celsius trials | Predicted Total Cost Range | Additional Info | Predicted Capacity Release Min | Predicted Capacity Release Max | Predicted Capacity Release Min kVA | Predicted Capacity Release Max kVA |  | Index | Options | Building Type | Site layout | Only for direct sunlight? | Predicted Capacity Release Min | Predicted Capacity Release Max | Mean Capacity Release across successful Celsius trials | Predicted Total Cost Range | Additional Info | Index | Building Type | Only for direct sunlight? | Description | Index | Output Index | Intervention Index | Options | Building Type | Site layout | Only for direct sunlight? | Predicted Capacity Release Min | Predicted Capacity Release Max | Mean Capacity Release across successful Celsius trials | Predicted Total Cost Range | Additional Info
| 1 | #N/A | [10 empty] | 1 | Monitoring + Celsius Rating | Stone/Brick | Single Transformer Site | No | -5 | 50 | 25% Based on 52 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. Note: substations with two transformers will require additional monitoring, with costs of ~£650. | 1 | Fenced Enclosure | No | Fenced Enclosure, No | 30 | 1 | 1 | Monitoring + Celsius Rating | Stone/Brick | Single Transformer Site | No | -500% | 5000% | 25% Based on 52 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. Note: substations with two transformers will require additional monitoring, with costs of ~£650.
| 2 | #N/A | [10 empty] | 2 | Monitoring + Celsius Rating | Part of a Larger Building | Single Transformer Site | No | 0 | 40 | 17% Based on 7 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. Note: substations with two transformers will require additional monitoring, with costs of ~£650. | 2 | Fenced Enclosure | Yes | Fenced Enclosure, Yes | 80 | 2 | 6 | Monitoring + Celsius Rating + Passive Ventilation | Stone/Brick | Single Transformer Site | No | 500% | 1000% | Successful trials resulted in a 9% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 36% | £800 - £3,000 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements.
| 3 | #N/A | [10 empty] | 3 | Monitoring + Celsius Rating | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | 7% Based on 4 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. | 3 | Fenced Enclosure | Unknown | Fenced Enclosure, Unknown | 80 | 3 | 10 | Monitoring + Celsius Rating + Active Cooling | Stone/Brick | Single Transformer Site | No | 500% | 4000% | Successful trials resulted in a 21% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 46%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent.
| 4 | #N/A | [10 empty] | 4 | Monitoring + Celsius Rating | Fenced Enclosure | Single Transformer Site | No | 20 | 50 | 41% Based on 10 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. If possible, weather data should also be collected to improve the accuracy of the model. Note: substations with two transformers will require additional monitoring, with costs of ~£650. | 4 | GRP | No | GRP, No | 20 | 11 | 2 | Monitoring + Celsius Rating | Part of a Larger Building | Single Transformer Site | No | 0% | 4000% | 17% Based on 7 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. Note: substations with two transformers will require additional monitoring, with costs of ~£650.
| 5 | #N/A | [10 empty] | 5 | Monitoring + Celsius Rating | Metal Kiosk | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. | 5 | GRP | Yes | GRP, Yes | 70 | 12 | 7 | Monitoring + Celsius Rating + Passive Ventilation | Part of a Larger Building | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | Successful trials resulted in a 6% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 23% | £800 - £3,000 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. This is an issue for many substations that are part of a larger building as they are often not owned by the DNO. Costs will be highly variable based on the configuration of the site and the required works.
| 6 | #N/A | [10 empty] | 6 | Monitoring + Celsius Rating + Passive Ventilation | Stone/Brick | Single Transformer Site | No | 5 | 10 | Successful trials resulted in a 9% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 36% | £800 - £3,000 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. | 6 | GRP | Unknown | GRP, Unknown | 70 | 13 | 11 | Monitoring + Celsius Rating + Active Cooling | Part of a Larger Building | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | A single successful trial resulted in a 14% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 31%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent.
| 7 | #N/A | [10 empty] | 7 | Monitoring + Celsius Rating + Passive Ventilation | Part of a Larger Building | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | Successful trials resulted in a 6% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 23% | £800 - £3,000 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. This is an issue for many substations that are part of a larger building as they are often not owned by the DNO. Costs will be highly variable based on the configuration of the site and the required works. | 7 | Metal Kiosk | No | Metal Kiosk, No | 40 | 21 | 3 | Monitoring + Celsius Rating | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | 7% Based on 4 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation.
| 8 | #N/A | [10 empty] | 8 | Monitoring + Celsius Rating + Passive Ventilation | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £500 - £700 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. Painting the roof of the substation may provide additional benefit if the substation is exposed to direct sunlight, however evidence for this is limited. | 8 | Metal Kiosk | Yes | Metal Kiosk, Yes | 90 | 22 | 8 | Monitoring + Celsius Rating + Passive Ventilation | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £500 - £700 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. Painting the roof of the substation may provide additional benefit if the substation is exposed to direct sunlight, however evidence for this is limited.
| 9 | #N/A | [10 empty] | 9 | Monitoring + Celsius Rating + Passive Ventilation + Paint | GRP | Single Transformer Site | Yes | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £500 - £700 | Configuration of vents to improve passive ventilation, and painting the roof white to reflect solar radiation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: Requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. Painting the roof of the substation may provide additional benefit if the substation is exposed to direct sunlight, however evidence for this is limited. | 9 | Metal Kiosk | Unknown | Metal Kiosk, Unknown | 90 | 23 | 12 | Monitoring + Celsius Rating + Active Cooling | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | A single successful trial resulted in a 23% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 30%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent.
[13 empty] | 10 | Monitoring + Celsius Rating + Active Cooling | Stone/Brick | Single Transformer Site | No | 5 | 40 | Successful trials resulted in a 21% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 46%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent. | 10 | Part of Larger Building | No | Part of Larger Building, No | 10 | 31 | 4 | Monitoring + Celsius Rating | Fenced Enclosure | Single Transformer Site | No | 2000% | 5000% | 41% Based on 10 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. If possible, weather data should also be collected to improve the accuracy of the model. Note: substations with two transformers will require additional monitoring, with costs of ~£650.
[13 empty] | 11 | Monitoring + Celsius Rating + Active Cooling | Part of a Larger Building | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | A single successful trial resulted in a 14% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 31%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent. | 11 | Part of Larger Building | Yes | Part of Larger Building, Yes | 60 | 41 | 5 | Monitoring + Celsius Rating | Metal Kiosk | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation.
[13 empty] | 12 | Monitoring + Celsius Rating + Active Cooling | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | A single successful trial resulted in a 23% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 30%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent. | 12 | Part of Larger Building | Unknown | Part of Larger Building, Unknown | 60 | 51 | 1 | Monitoring + Celsius Rating | Stone/Brick | Single Transformer Site | No | -500% | 5000% | 25% Based on 52 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. Note: substations with two transformers will require additional monitoring, with costs of ~£650.
[24 empty] | Stone/Brick | No | Stone/Brick, No | 0 | 52 | 6 | Monitoring + Celsius Rating + Passive Ventilation | Stone/Brick | Single Transformer Site | No | 500% | 1000% | Successful trials resulted in a 9% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 36% | £800 - £3,000 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements.
[24 empty] | Stone/Brick | Yes | Stone/Brick, Yes | 50 | 53 | 10 | Monitoring + Celsius Rating + Active Cooling | Stone/Brick | Single Transformer Site | No | 500% | 4000% | Successful trials resulted in a 21% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 46%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent.
[24 empty] | Stone/Brick | Unknown | Stone/Brick, Unknown | 50 | 61 | 2 | Monitoring + Celsius Rating | Part of a Larger Building | Single Transformer Site | No | 0% | 4000% | 17% Based on 7 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. Note: substations with two transformers will require additional monitoring, with costs of ~£650.
[28 empty] | 62 | 7 | Monitoring + Celsius Rating + Passive Ventilation | Part of a Larger Building | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | Successful trials resulted in a 6% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 23% | £800 - £3,000 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. This is an issue for many substations that are part of a larger building as they are often not owned by the DNO. Costs will be highly variable based on the configuration of the site and the required works.
[28 empty] | 63 | 11 | Monitoring + Celsius Rating + Active Cooling | Part of a Larger Building | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | A single successful trial resulted in a 14% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 31%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent.
[28 empty] | 71 | 3 | Monitoring + Celsius Rating | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | 7% Based on 4 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation.
[28 empty] | 72 | 8 | Monitoring + Celsius Rating + Passive Ventilation | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £500 - £700 | Configuration of vents to improve passive ventilation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. Painting the roof of the substation may provide additional benefit if the substation is exposed to direct sunlight, however evidence for this is limited.
[28 empty] | 73 | 9 | Monitoring + Celsius Rating + Passive Ventilation + Paint | GRP | Single Transformer Site | Yes | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £500 - £700 | Configuration of vents to improve passive ventilation, and painting the roof white to reflect solar radiation. Benefit will depend on the configuration of the existing substation and the effectiveness of existing ventilation arrangements. Note: Requires access and authority to alter the fabric of the building to alter the passive ventilation arrangements. Painting the roof of the substation may provide additional benefit if the substation is exposed to direct sunlight, however evidence for this is limited.
[28 empty] | 74 | 12 | Monitoring + Celsius Rating + Active Cooling | GRP | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | A single successful trial resulted in a 23% release over Celsius rating before installation. This suggests a combined release for both Celsius Rating and cooling of 30%. | £3,500 - £4,000 | Installation of fans and configuration of vents to encourage forced ventilation. Benefit will be dependent on the configuration of the existing substation, but there is strong trial evidence that significant capacity release can be achieved. Note: May require alteration of ventilation, requiring access and permissions to alter building fabric. There is also the need for a suitable location for the fan unit, which may be placed inside or outside the substation at a vent.
[28 empty] | 81 | 4 | Monitoring + Celsius Rating | Fenced Enclosure | Single Transformer Site | No | 2000% | 5000% | 41% Based on 10 trial sites. | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation. If possible, weather data should also be collected to improve the accuracy of the model. Note: substations with two transformers will require additional monitoring, with costs of ~£650.
[28 empty] | 82 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[28 empty] | 83 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[28 empty] | 91 | 5 | Monitoring + Celsius Rating | Metal Kiosk | Single Transformer Site | No | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | UNKNOWN: Only limited trial data available | £800 - £1000 | Monitoring will include three phase power (voltage and current), transformer surface temperature at the top oil level, and substation ambient temperature. The Celsius rating is calculated from analysis of the relationship between transformer load and temperature. Monitoring is performed on an ongoing basis to provide risk mitigation.

## Admin (hidden)
Hotspot Temperature Calculation
Transformer Spec | Surface Temp | Ambient Temp | Intercept
ESI | 1.65 | -0.53 | -1.97 | Format of the Linest() function
T1 | 2.19 | -1.06 | -11.16
Setting Max Ambient Temperature
Site Building Type | Max Ambient
Stone/Brick | 34.25
Part of Larger Building | 31.69
GRP | 38.88
Lists for drop down menus
List of ratings | Yes/no | Site types
300 | Yes | Stone/Brick
315 | No | Part of Larger Building
500 | Unknown | GRP
750 |  | Fenced Enclosure
800
1000